## CoverSheet
EDB Information Disclosure Requirements
Information Templates
Schedule 10a
Company Name
Disclosure Date
Disclosure Year (year ended)
Template for Schedule 10a
Prepared 2 June 2026.

## TOC
Table of Contents
Schedule | Schedule name
10a | REPORT ON INTERRUPTIONS

## Instructions
Disclosure Template Instructions
This document forms Schedule 10a to the Electricity Distribution Information Disclosure (Non-material) Amendment Determination 2026 [2026] NZCC 21.
The Schedules take the form of templates for use by EDBs when making disclosures under subclause 2.5.1 of the Electricity Distribution Information Disclosure Determination 2012, as amended.
Company Name and Dates
To prepare the templates for disclosure, the supplier's company name should be entered in cell C8, the date of the last day of the current (disclosure) year should be entered in cell C12, and the date on which the information is disclosed should be entered in cell C10 of the CoverSheet worksheet.
The cell C12 entry (current year) is used to calculate disclosure years in the column headings that show above some of the tables and in labels adjacent to some entry cells. It is also used to calculate the ‘For year ended’ date in the template title blocks (the title blocks are the light green shaded areas at the top of each template). The cell C8 entry (company name) is used in the template title blocks. Dates should be entered in day/month/year order (Example -"1 April 2023").
Data Entry Cells and Calculated Cells
Data entered into this workbook may be entered only into the data entry cells. Data entry cells are the bordered, unshaded areas (white cells) in each template. Under no circumstances should data be entered into the workbook outside a data entry cell.
In some cases, where the information for disclosure is able to be ascertained from disclosures elsewhere in the workbook, such information is disclosed in a calculated cell.
Validation Settings on Data Entry Cells
To maintain a consistency of format and to help guard against errors in data entry, some data entry cells test keyboard entries for validity and accept only a limited range of values. For example, entries may be limited to a list of category names, to values between 0% and 100%, or either a numeric entry or the text entry “N/A”. Where this occurs, a validation message will appear when data is being entered. These checks are applied to keyboard entries only and not, for example, to entries made using Excel’s copy and paste facility.
Inserting Additional Rows and Columns
The schedule 10a template may require additional rows to be inserted in tables marked 'include additional rows if needed' or similar. Column A schedule references should not be entered in additional rows, and should be deleted from additional rows that are created by copying and pasting rows that have schedule references.
Additional rows in the schedule 10a template must not be inserted directly above the first row or below the last row of a table. This is to ensure that entries made in the new row are included in the totals.
Description of Calculation References
Calculation cell formulas contain links to other cells within the same template or elsewhere in the workbook. Key cell references are described in a column to the right of each template. These descriptions are provided to assist data entry. Cell references refer to the row of the template and not the schedule reference.

## S10a.Interruptions
Company Name
For Year Ended
SCHEDULE 10a: REPORT ON INTERRUPTIONS
This schedule requires raw interruption data for the disclosure year. SAIDI and SAIFI is to be recorded using the multi-count approach.Where multiple feeders are affected, the interruption record is to be split into multiple interruptions, ie, one interruption record per feeder. This information is part of audited disclosure information (as defined in section 1.4 of this ID determination), and so is subject to the assurance report required by section 2.8.
sch ref
7 | 10a(i): Raw interruption data
8 |  | Interruption identifier | Circuit location | Sub-network (where applicable) | Feeder(s) affected by interruption | Start date (dd/mm/yyyy) | Start time (hh:mm:ss) | End date (dd/mm/yyyy) | End time (hh:mm:ss) | SAIDI value | SAIFI value | Number of ICPs interrupted | ICP interruption minutes | Planned or unplanned interruption (Class B or C) | Cause | Any explanation to help clarify the context of the interruption, including what the cause is if recorded as 'Other cause'
9 |  | INCD-3071-E | Hoeka | Network | HOECB1 | 02/04/2025 | 08:34 | 02/04/2025 | 15:29 | 0.10916 | 0.000263 | 27 | 11205 | Planned interruptions on the network | Planned | Distribution Transformer Replacement
10 |  | INCD-3112-E | Gordonton | Network | GORCB11 | 04/04/2025 | 09:15 | 04/04/2025 | 12:05 | 0.038639 | 0.000263 | 27 | 3966 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-3111-E | Hoeka | Network | HOECB6 | 04/04/2025 | 09:23 | 04/04/2025 | 15:15 | 0.12003 | 0.000341 | 35 | 12320 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-3119-E | Finlayson | Network | FINCB1 | 09/04/2025 | 08:03 | 09/04/2025 | 13:47 | 0.53799 | 0.0017439 | 179 | 55221 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-9-M | Weavers | Network | WEACB4 | 09/04/2025 | 09:02 | 09/04/2025 | 14:01 | 0.032043 | 0.0001072 | 11 | 3289 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-1214-K | Weavers | Network | WEACB4 | 13/04/2025 | 04:09 | 13/04/2025 | 05:56 | 0.0031273 | 2.92e-05 | 3 | 321 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-1369-K | Transpower Hamilton | Network | HAMCB2802 | 17/04/2025 | 07:42 | 17/04/2025 | 08:23 | 0.0003994 | 9.7e-06 | 1 | 41 | Unplanned interruptions on the network | Adverse weather | Line clash high wind
|  | INCD-1377-K | Whatawhata | Private | WHACB4 | 17/04/2025 | 08:35 | 17/04/2025 | 08:45 | 0.0014614 | 0.0001461 | 15 | 150 | Unplanned interruptions on the network | Third_party | Temp Disconnect / safety isolation
|  | INCD-1383-K | Weavers | Network | WEACB2 | 17/04/2025 | 09:31 | 17/04/2025 | 16:15 | 0.39267 | 0.0011009 | 113 | 40305 | Unplanned interruptions on the network | Vegetation | Tree blown ovr on line (OUT of Zone)
|  | INCD-1397-K | Weavers | Network | WEACB2 | 17/04/2025 | 09:32 | 17/04/2025 | 10:44 | 0.12194 | 0.0016855 | 173 | 12516 | Unplanned interruptions on the network | Adverse weather | High wind lne break
|  | INCD-1437-K | Weavers | Network | NGACB6 | 17/04/2025 | 12:32 | 17/04/2025 | 13:10 | 0.0071997 | 0.0009255 | 95 | 739 | Unplanned interruptions on the network | Adverse weather | Line clash high wind
|  | INCD-1465-K | Horotiu | Network | NGACB5 | 17/04/2025 | 14:27 | 17/04/2025 | 16:54 | 0.0014321 | 9.7e-06 | 1 | 147 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (OUT of Zone)
|  | INCD-1490-K | Weavers | Network | WEACB6 | 17/04/2025 | 12:03 | 17/04/2025 | 16:05 | 0.042438 | 0.0001754 | 18 | 4356 | Unplanned interruptions on the network | Adverse weather | Line clash high wind
|  | INCD-1515-K | Weavers | Network | WEACB6 | 17/04/2025 | 11:14 | 17/04/2025 | 19:40 | 0.059157 | 0.0001169 | 12 | 6072 | Unplanned interruptions on the network | Adverse weather | Line clash high wind
|  | INCD-16-M | Raglan | Network | TEUCB2 | 18/04/2025 | 14:51 | 18/04/2025 | 23:45 | 0.0027114 | 0.0001559 | 16 | 278.31 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-16-M | Raglan | Network | RAGCB3 | 18/04/2025 | 14:51 | 18/04/2025 | 23:45 | 0.017907 | 0.0014614 | 150 | 1838 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-1577-K | Weavers | Network | WEACB6 | 19/04/2025 | 02:18 | 19/04/2025 | 02:35 | 0.018764 | 0.0012178 | 125 | 1926 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-34-L | Weavers | Network | WEACB4 | 22/04/2025 | 08:25 | 22/04/2025 | 11:16 | 0.001666 | 9.7e-06 | 1 | 171 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-1746-K | Weavers | Network | GLACB7 | 26/04/2025 | 16:02 | 26/04/2025 | 16:32 | 0.018472 | 0.0008671 | 89 | 1896 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-2086-K | Claudelands | Network | CLACB3 | 05/05/2025 | 17:54 | 05/05/2025 | 23:35 | 0.4391 | 0.001325 | 136 | 45071 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-2313-K | Te Kauwhata | Network | TEKCB6 | 11/05/2025 | 03:02 | 11/05/2025 | 05:19 | 0.0026694 | 1.95e-05 | 2 | 274 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-2315-K | Te Kauwhata | Network | FINCB1 | 11/05/2025 | 07:54 | 11/05/2025 | 08:59 | 0.079947 | 0.0040529 | 416 | 8206 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2315-K | Te Kauwhata | Network | FINCB2 | 11/05/2025 | 07:54 | 11/05/2025 | 08:59 | 0.095901 | 0.0053876 | 553 | 9843.6 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2315-K | Te Kauwhata | Network | TEKCB3 | 11/05/2025 | 07:54 | 11/05/2025 | 08:59 | 0.0002626 | 9.7e-06 | 1 | 26.95 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-66-L | Steele Park | Network | STECB3 | 13/05/2025 | 08:32 | 14/05/2025 | 15:58 | 0.80847 | 0.0004287 | 44 | 82984 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2535-K | Wallace Rd | Network | WALCB6 | 16/05/2025 | 08:42 | 16/05/2025 | 13:39 | 0.026042 | 8.77e-05 | 9 | 2673 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-1982-K | Latham | Network | LATCB5 | 20/05/2025 | 09:08 | 20/05/2025 | 16:13 | 0.14431 | 0.0038775 | 398 | 14812 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-2801-K | Te Uku | Network | TEUCB11 | 23/05/2025 | 13:53 | 24/05/2025 | 02:22 | 0.14954 | 0.0027669 | 284 | 15349 | Unplanned interruptions on the network | Defective Equipment | Line break at twist joint
|  | INCD-2896-K | Chartwell | Network | CHACB13 | 27/05/2025 | 00:08 | 27/05/2025 | 01:52 | 0.093285 | 0.0015198 | 156 | 9575 | Unplanned interruptions on the network | Defective Equipment | Poor contacts
|  | INCD-3062-K | Peacockes | Network | PEACB13 | 30/05/2025 | 00:01 | 30/05/2025 | 01:39 | 0.23124 | 0.0039652 | 407 | 23735 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-98-M | Weavers | Network | WEACB3 | 03/06/2025 | 09:32 | 03/06/2025 | 14:18 | 0.12091 | 0.0004579 | 47 | 12411 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-3480-K | Horotiu | Network | HORCB5 | 10/06/2025 | 16:54 | 10/06/2025 | 19:47 | 0.015169 | 8.77e-05 | 9 | 1557 | Unplanned interruptions on the network | Defective Equipment | Mechanism seized
|  | INCD-3559-K | Te Uku | Network | TEUCB11 | 11/06/2025 | 01:15 | 12/06/2025 | 13:36 | 0.18448 | 0.0030981 | 318 | 18936 | Unplanned interruptions on the network | Defective Equipment | Chips or missing bits
|  | INCD-88-M | Weavers | Network | WEACB4 | 12/06/2025 | 09:45 | 12/06/2025 | 15:34 | 0.041951 | 0.0001267 | 13 | 4306 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-3747-K | Finlayson Rd | Network | FINCB2 | 16/06/2025 | 22:00 | 16/06/2025 | 23:51 | 0.0032443 | 2.92e-05 | 3 | 333 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-3878-K | Peacockes Rd | Network | PEACB12 | 21/06/2025 | 06:50 | 21/06/2025 | 14:31 | 0.001067 | 9.7e-06 | 1 | 109.52 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-3878-K | Peacockes Rd | Network | PEACB17 | 21/06/2025 | 06:50 | 21/06/2025 | 14:31 | 0.94883 | 0.009421 | 967 | 97390.48 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-165-L | Avalon | Network | AVACB4 | 23/06/2025 | 09:02 | 23/06/2025 | 12:42 | 0.14189 | 0.0012081 | 124 | 14564 | Unplanned interruptions on the network | Defective Equipment | Cable termination fails
|  | INCD-3946-K | Transpower Hamilton | Network | HAMCB2902 | 26/06/2025 | 12:22 | 26/06/2025 | 18:00 | 0.4695 | 0.0016757 | 172 | 48191 | Unplanned interruptions on the network | Defective Equipment | Cable termination fails
|  | INCD-3999-K | Whatawhata | Network | TEUCB12 | 28/06/2025 | 00:00 | 28/06/2025 | 00:12 | 0.031118 | 0.0026597 | 273 | 3194.08 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-4006-K | Ngaruawahia | Network | NGACB6 | 28/06/2025 | 07:49 | 28/06/2025 | 08:27 | 0.011642 | 0.0003118 | 32 | 1195 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-4074-K | Transpower Hamilton | Network | HAMCB2902 | 28/06/2025 | 23:39 | 29/06/2025 | 14:24 | 0.11968 | 0.0021823 | 224 | 12284 | Unplanned interruptions on the network | Defective Equipment | Cable termination fails
|  | INCD-4023-K | Hampton Downs | Network | HPTCB4 | 29/06/2025 | 07:38 | 29/06/2025 | 10:27 | 0.0016465 | 9.7e-06 | 1 | 169 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-4084-K | Te Uku Wind Farm | Network | TEUCB11 | 02/07/2025 | 00:34 | 02/07/2025 | 00:46 | 0.093292 | 0.0074238 | 762 | 9575.78 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-4084-K | Te Uku Wind Farm | Network | WHACB4402 | 02/07/2025 | 00:34 | 02/07/2025 | 00:46 | 0.0012243 | 9.74e-05 | 10 | 125.67 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-4112-K | Latham | Network | LATCB1 | 03/07/2025 | 05:04 | 03/07/2025 | 07:56 | 0.17872 | 0.0015783 | 162 | 18344 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-149-M | Peacockes | Network | PEACB12 | 03/07/2025 | 09:00 | 03/07/2025 | 13:25 | 0.12019 | 0.0010132 | 104 | 12337 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-4204-K | Te Kauwhata | Network | TEKCB6 | 05/07/2025 | 17:46 | 05/07/2025 | 22:45 | 0.002913 | 9.7e-06 | 1 | 299 | Unplanned interruptions on the network | Wildlife | Bird betw line & pole
|  | INCD-4239-K | Latham | Network | LATCB1 | 07/07/2025 | 09:03 | 07/07/2025 | 17:49 | 0.42021 | 0.0007989 | 82 | 43132 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-4242-K | Chartwell | Network | CHACB9 | 07/07/2025 | 09:34 | 07/07/2025 | 11:21 | 0.034401 | 0.0003215 | 33 | 3531 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-4426-K | Pukete | Network | PUKCB4 | 11/07/2025 | 07:14 | 11/07/2025 | 12:09 | 0.02838 | 0.0011301 | 116 | 2913 | Unplanned interruptions on the network | Defective Equipment | Cable termination fails
|  | INCD-4463-K | Pukete | Network | TASCB4 | 11/07/2025 | 15:01 | 11/07/2025 | 15:03 | 0.0091092 | 0.003215 | 330 | 935 | Planned interruptions on the network | Planned | New Connections
|  | INCD-4521-K | Waikato University | Network | UNICB4 | 14/07/2025 | 08:11 | 14/07/2025 | 18:43 | 0.0061573 | 9.7e-06 | 1 | 632 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-4628-K | Weavers | Network | WEACB3 | 16/07/2025 | 09:33 | 16/07/2025 | 15:56 | 0.027338 | 9.74e-05 | 10 | 2806 | Unplanned interruptions on the network | Defective Equipment | Intnl insulation failure
|  | INCD-4670-K | Gordonton | Network | GORCB11 | 17/07/2025 | 10:30 | 17/07/2025 | 16:11 | 0.081282 | 0.0047349 | 486 | 8343 | Unplanned interruptions on the network | Defective Equipment | Split crossarm
|  | INCD-4710-K | Pukete | Network | PUKCB10 | 18/07/2025 | 10:16 | 18/07/2025 | 16:36 | 0.0074043 | 1.95e-05 | 2 | 760 | Unplanned interruptions on the network | Third_party | Cable isolated - safety reasons
|  | INCD-4759-K | Te Kauwhata | Network | TEKCB5 | 19/07/2025 | 15:51 | 19/07/2025 | 18:24 | 0.0059624 | 3.9e-05 | 4 | 612 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-5192-K | Weavers | Network | WEACB2 | 29/07/2025 | 13:58 | 29/07/2025 | 16:53 | 0.0017049 | 9.7e-06 | 1 | 175 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-5252-K | Wallace Rd | Network | WALCB5 | 31/07/2025 | 10:28 | 31/07/2025 | 15:58 | 0.18326 | 0.0005553 | 57 | 18810 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-5445-K | Hampton Downs | Network | HPTCB5 | 06/08/2025 | 14:07 | 06/08/2025 | 17:53 | 0.0044036 | 1.95e-05 | 2 | 452 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-213-M | Sandwich | Network | SANCB5 | 07/08/2025 | 20:10 | 07/08/2025 | 23:06 | 0.079372 | 0.0004676 | 48 | 8147 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-219-M | Peacockes | Network | PEACB12 | 08/08/2025 | 10:04 | 08/08/2025 | 16:30 | 0.1508 | 0.0003994 | 41 | 15479 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-258-M | Steele Park | Network | STECB7 | 10/08/2025 | 08:04 | 10/08/2025 | 16:27 | 0.0007015 | 3.9e-05 | 4 | 72 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-231-M | Weavers | Network | WEACB3 | 11/08/2025 | 09:08 | 11/08/2025 | 11:24 | 0.022885 | 0.0001949 | 20 | 2349 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-353-L | Hoeka | Network | HOECB2 | 12/08/2025 | 09:41 | 12/08/2025 | 13:21 | 0.049102 | 0.0002338 | 24 | 5040 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-232-M | Finlayson | Network | FINCB2 | 12/08/2025 | 09:45 | 12/08/2025 | 16:14 | 0.0075797 | 1.95e-05 | 2 | 778 | Planned interruptions on the network | Planned | Transformer Upgrade
|  | INCD-5691-K | Gordonton | Network | GORCB12 | 13/08/2025 | 05:11 | 13/08/2025 | 06:30 | 0.0007697 | 9.7e-06 | 1 | 79 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-5779-K | Weavers | Network | WEACB5 | 14/08/2025 | 16:11 | 14/08/2025 | 19:13 | 0.0053194 | 2.92e-05 | 3 | 546 | Unplanned interruptions on the network | Defective Equipment | Pins fulls out
|  | INCD-5851-K | Weavers | Network | WEACB3 | 17/08/2025 | 22:43 | 18/08/2025 | 01:07 | 0.0056117 | 3.9e-05 | 4 | 576 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-521-L | Peacockes Rd | Network | PEACB12 | 18/08/2025 | 00:22 | 18/08/2025 | 00:33 | 0.025399 | 0.0022213 | 228 | 2607 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-5897-K | Finlayson Rd | Network | FINCB4 | 18/08/2025 | 09:05 | 18/08/2025 | 11:18 | 0.005183 | 3.9e-05 | 4 | 532 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-6075-K | Chartwell | Network | CHACB9 | 22/08/2025 | 02:28 | 22/08/2025 | 04:23 | 0.058114 | 0.0005066 | 52 | 5965 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-6128-K | Glasgow St | Network | GLACB2 | 24/08/2025 | 08:36 | 24/08/2025 | 10:45 | 0.0025136 | 1.95e-05 | 2 | 258 | Unplanned interruptions on the network | Defective Equipment | Wear or shear of pins
|  | INCD-270-M | Gordonton | Network | GORCB13 | 28/08/2025 | 09:12 | 28/08/2025 | 14:46 | 0.035794 | 0.0001072 | 11 | 3674 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-115-N | Finlayson Rd | Network | FINCB2 | 31/08/2025 | 08:04 | 31/08/2025 | 08:14 | 0.019935 | 0.0021434 | 220 | 2046.19 | Unplanned interruptions on the network | Vegetation | Tree blown ovr on line (OUT of Zone)
|  | INCD-117-N | Finlayson Rd | Network | FINCB2 | 31/08/2025 | 08:04 | 31/08/2025 | 08:18 | 0.0097815 | 0.0007112 | 73 | 1004 | Unplanned interruptions on the network | Vegetation | Tree blown ovr on line (OUT of Zone)
|  | INCD-6410-K | Horotiu | Network | GORCB13 | 31/08/2025 | 18:22 | 31/08/2025 | 18:41 | 0.10957 | 0.006167 | 633 | 11247 | Unplanned interruptions on the network | Defective Equipment | Broken binder
|  | INCD-276-M | Whatawhata | Network | WHACB5 | 02/09/2025 | 09:08 | 02/09/2025 | 16:41 | 0.48503 | 0.0011106 | 114 | 49785 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-6584-K | Avalon Dr | Network | AVACB1 | 02/09/2025 | 20:38 | 02/09/2025 | 21:09 | 0.1249 | 0.0040334 | 414 | 12820 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-6655-K | Peacockes Rd | Network | PEACB17 | 03/09/2025 | 23:23 | 03/09/2025 | 23:29 | 0.012509 | 0.0020849 | 214 | 1284 | Unplanned interruptions on the network | Defective Equipment | Fuse blown on overload
|  | INCD-6821-K | Weavers | Network | WEACB3 | 08/09/2025 | 09:15 | 08/09/2025 | 14:27 | 0.015198 | 4.87e-05 | 5 | 1560 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-306-M | Finlayson | Network | FINCB2 | 08/09/2025 | 09:51 | 08/09/2025 | 15:43 | 0.017147 | 4.87e-05 | 5 | 1760 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-6883-K | Kent St | Network | KENCB4 | 09/09/2025 | 09:15 | 09/09/2025 | 09:33 | 0.12337 | 0.007492 | 769 | 12663 | Unplanned interruptions on the network | Defective Equipment | Cable joint fails
|  | INCD-6970-K | Raglan | Network | RAGCB6 | 10/09/2025 | 20:51 | 10/09/2025 | 21:28 | 0.0025233 | 6.82e-05 | 7 | 259 | Unplanned interruptions on the network | Third_party | Cable hit by digger
|  | INCD-316-M | Weavers | Network | WEACB2 | 11/09/2025 | 09:38 | 11/09/2025 | 11:50 | 0.22958 | 0.0018413 | 189 | 23565 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-7089-K | Finlayson Rd | Network | FINCB2 | 13/09/2025 | 08:32 | 13/09/2025 | 10:06 | 0.0018316 | 1.95e-05 | 2 | 188 | Unplanned interruptions on the network | Defective Equipment | Mechanism seized
|  | INCD-333-M | Transpower Hamilton | Network | HAMCB2742 | 16/09/2025 | 11:11 | 16/09/2025 | 15:39 | 0.16188 | 0.000604 | 62 | 16616 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-342-M | Pukete | Network | TASCB4 | 18/09/2025 | 09:50 | 18/09/2025 | 17:31 | 0.067126 | 0.0019193 | 197 | 6890 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-7661-K | Crawford Rd | Network | SANCB7 | 27/09/2025 | 09:26 | 28/09/2025 | 15:18 | 0.050622 | 2.92e-05 | 3 | 5196 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-307-M | Sandwich | Network | SANCB5 | 28/09/2025 | 09:18 | 28/09/2025 | 14:55 | 0.18305 | 0.0005553 | 57 | 18789 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-329-M | Silverdale | Network | SILCB5 | 29/09/2025 | 10:07 | 29/09/2025 | 12:00 | 0.10836 | 0.0009645 | 99 | 11122 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-7730-K | Sandwich Rd | Network | SANCB4 | 30/09/2025 | 05:04 | 30/09/2025 | 06:19 | 0.013152 | 0.0001754 | 18 | 1350 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-7754-K | Finlayson Rd | Network | FINCB2 | 30/09/2025 | 11:19 | 30/09/2025 | 15:11 | 0.0067808 | 2.92e-05 | 3 | 696 | Unplanned interruptions on the network | Defective Equipment | Jumpers come off
|  | INCD-7781-K | Horotiu | Network | HORCB6 | 01/10/2025 | 05:32 | 01/10/2025 | 06:06 | 0.0003312 | 9.7e-06 | 1 | 34 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-7928-K | Finlayson Rd | Network | FINCB2 | 04/10/2025 | 10:25 | 04/10/2025 | 22:27 | 0.03517 | 4.87e-05 | 5 | 3610 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-7966-K | Weavers | Network | WEACB3 | 05/10/2025 | 12:53 | 05/10/2025 | 14:26 | 0.0027182 | 2.92e-05 | 3 | 279 | Unplanned interruptions on the network | Defective Equipment | Intnl insulation failure
|  | INCD-680-L | Peacockes Rd | Network | PEACB11 | 07/10/2025 | 06:51 | 07/10/2025 | 09:54 | 0.0035658 | 1.95e-05 | 2 | 366 | Unplanned interruptions on the network | Wildlife | Bird betw line & pole
|  | INCD-8093-K | Raglan | Network | RAGCB2 | 08/10/2025 | 15:59 | 08/10/2025 | 16:03 | 0.031712 | 0.0077355 | 794 | 3255 | Unplanned interruptions on the network | Human error | Unintentionally Disabled
|  | INCD-330-M | Chartwell | Network | CHACB9 | 09/10/2025 | 09:24 | 09/10/2025 | 12:35 | 0.070711 | 0.0003702 | 38 | 7258 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-8139-K | Transpower Hamilton | Network | CLACB16 | 10/10/2025 | 17:39 | 10/10/2025 | 19:00 | 0.14135 | 0.001929 | 198 | 14508.15 | Unplanned interruptions on the network | Defective Equipment | Bus chamber flashovr
|  | INCD-8171-K | Avalon Dr | Network | AVACB3 | 13/10/2025 | 10:44 | 15/10/2025 | 18:01 | 0.80359 | 0.0036729 | 377 | 82483 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-8213-K | Finlayson | Network | FINCB4 | 14/10/2025 | 20:36 | 14/10/2025 | 21:23 | 0.0022895 | 4.87e-05 | 5 | 235 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-8224-K | Claudelands | Network | CLACB13 | 15/10/2025 | 09:04 | 15/10/2025 | 15:15 | 0.061446 | 0.0001656 | 17 | 6307 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-345-M | Hampton Downs | Network | HPTCB5 | 16/10/2025 | 10:03 | 16/10/2025 | 15:42 | 0.05448 | 0.0001656 | 17 | 5592 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-8310-K | Te Uku | Network | TEUCB12 | 19/10/2025 | 16:28 | 19/10/2025 | 23:03 | 0.16928 | 0.0004287 | 44 | 17375 | Unplanned interruptions on the network | Vegetation | Tree blown ovr on line (IN Zone)
|  | INCD-8396-K | Hoeka | Network | HOECB4 | 23/10/2025 | 22:45 | 24/10/2025 | 01:05 | 0.14686 | 0.0024259 | 249 | 15074 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-8400-K | Transpower Hamilton | Network | HAMCB2762 | 24/10/2025 | 09:02 | 24/10/2025 | 10:47 | 0.053194 | 0.0005066 | 52 | 5460 | Planned interruptions on the network | Planned | Distribution Transformer Replacement
|  | INCD-8464-K | Te Uku | Network | TEUCB11 | 28/10/2025 | 05:56 | 28/10/2025 | 09:13 | 0.0038385 | 1.95e-05 | 2 | 394 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-8468-K | Wallace Rd | Network | WALCB1 | 28/10/2025 | 08:34 | 28/10/2025 | 10:10 | 0.006547 | 6.82e-05 | 7 | 672 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (OUT of Zone)
|  | INCD-1170-L | Hoeka | Network | HOECB2 | 28/10/2025 | 16:46 | 28/10/2025 | 19:29 | 0.061436 | 0.0004092 | 42 | 6306 | Unplanned interruptions on the network | Defective Equipment | Broken binder
|  | INCD-8528-K | Pukete | Network | TASCB4 | 30/10/2025 | 07:44 | 30/10/2025 | 16:32 | 0.79649 | 0.003254 | 334 | 81754 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-8539-K | Ngaruawahia | Network | NGACB2 | 30/10/2025 | 09:04 | 30/10/2025 | 15:00 | 0.17026 | 0.0004774 | 49 | 17476 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-8589-K | Transpower Hamilton | Network | HAMCB2742 | 02/11/2025 | 09:52 | 02/11/2025 | 11:58 | 0.13994 | 0.0011106 | 114 | 14364 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-8634-K | Steele Park | Network | STECB3 | 03/11/2025 | 11:56 | 03/11/2025 | 12:12 | 0.013094 | 0.0016367 | 168 | 1344 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-131-N | Weavers | Network | WEACB3 | 04/11/2025 | 10:07 | 04/11/2025 | 14:54 | 0.055484 | 0.0001949 | 20 | 5695 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-378-M | Finlayson | Network | FINCB1 | 04/11/2025 | 10:13 | 04/11/2025 | 16:52 | 0.0077745 | 1.95e-05 | 2 | 798 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-8689-K | Te Uku | Network | TEUCB11 | 06/11/2025 | 03:37 | 06/11/2025 | 16:13 | 0.59256 | 0.017497 | 1796 | 60822 | Unplanned interruptions on the network | Defective Equipment | Wear or shear of pins
|  | INCD-8714-K | Latham Court | Private | LATCB5 | 07/11/2025 | 11:18 | 07/11/2025 | 11:35 | 0.01855 | 0.0010912 | 112 | 1904 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-8746-K | Horotiu | Network | KOHCB6 | 09/11/2025 | 09:49 | 09/11/2025 | 11:15 | 0.071685 | 0.0049784 | 511 | 7358 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-8781-K | Weavers | Network | NGACB5 | 11/11/2025 | 07:37 | 11/11/2025 | 07:45 | 0.084848 | 0.0097522 | 1001 | 8709 | Unplanned interruptions on the network | Wildlife | Bird betw line & pole
|  | INCD-421-M | Chartwell | Network | CHACB12 | 14/11/2025 | 08:25 | 14/11/2025 | 15:20 | 0.24259 | 0.0005846 | 60 | 24900 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-1444-L | Ngaruawahia | Network | NGACB6 | 17/11/2025 | 03:26 | 17/11/2025 | 10:47 | 0.012889 | 2.92e-05 | 3 | 1323 | Unplanned interruptions on the network | Defective Equipment | Intnl insulation failure
|  | INCD-9048-K | Chartwell | Network | CHACB5 | 19/11/2025 | 00:34 | 19/11/2025 | 14:08 | 0.51423 | 0.0008866 | 91 | 52782 | Unplanned interruptions on the network | Defective Equipment | LV Panel fire
|  | INCD-9102-K | Avalon Dr | Network | AVACB4 | 20/11/2025 | 08:26 | 20/11/2025 | 14:07 | 0.1634 | 0.0007015 | 72 | 16772 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-9132-K | Finlayson | Network | FINCB2 | 20/11/2025 | 14:46 | 20/11/2025 | 17:00 | 0.0039165 | 2.92e-05 | 3 | 402 | Unplanned interruptions on the network | Defective Equipment | Stay wire/ line clash
|  | INCD-409-M | Horotiu | Network | HORCB3 | 21/11/2025 | 09:00 | 21/11/2025 | 15:21 | 0.11637 | 0.0003118 | 32 | 11945 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-1502-L | Weavers | Network | WEACB6 | 26/11/2025 | 21:04 | 26/11/2025 | 22:58 | 0.0011106 | 9.7e-06 | 1 | 114 | Unplanned interruptions on the network | Human error | Incorr fuse rating
|  | INCD-447-M | Peacockes | Network | PEACB16 | 27/11/2025 | 09:03 | 27/11/2025 | 15:35 | 0.012626 | 0.0021044 | 216 | 1296 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-137-N | Te Uku | Network | TEUCB11 | 27/11/2025 | 09:12 | 27/11/2025 | 16:07 | 0.033592 | 0.0002338 | 24 | 3448 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-450-M | Peacockes | Network | PEACB18 | 28/11/2025 | 09:06 | 28/11/2025 | 10:45 | 0.0048225 | 4.87e-05 | 5 | 495 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-9298-K | Transpower Hamilton | Network | HAMCB2802 | 28/11/2025 | 17:47 | 28/11/2025 | 23:38 | 0.11313 | 0.0004969 | 51 | 11612 | Unplanned interruptions on the network | Third_party | High vehicle contact
|  | INCD-445-M | Ngariuawahia | Network | NGACB2 | 01/12/2025 | 09:25 | 01/12/2025 | 13:58 | 0.18539 | 0.0007112 | 73 | 19029 | Planned interruptions on the network | Planned | 11kV Fuse Replacement
|  | INCD-252-N | Wallace Rd | Network | WALCB5 | 01/12/2025 | 14:17 | 01/12/2025 | 14:38 | 0.017595 | 0.0008379 | 86 | 1806 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-446-M | Peacockes | Network | PEACB12 | 02/12/2025 | 09:25 | 02/12/2025 | 11:24 | 0.026665 | 0.0002241 | 23 | 2737 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-9369-K | Horotiu | Network | HORCB6 | 03/12/2025 | 18:00 | 03/12/2025 | 20:43 | 0.014292 | 8.77e-05 | 9 | 1467 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-1607-L | Pukete | Network | PUKCB4 | 04/12/2025 | 06:42 | 04/12/2025 | 07:34 | 0.0030397 | 5.85e-05 | 6 | 312 | Planned interruptions on the network | Planned | Transformer Upgrade
|  | INCD-443-M | Gordonton | Network | GORCB11 | 05/12/2025 | 09:49 | 05/12/2025 | 15:18 | 0.34297 | 0.0010424 | 107 | 35203 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-9541-K | Ngaruawahia | Network | NGACB2 | 09/12/2025 | 09:31 | 09/12/2025 | 16:59 | 0.69515 | 0.0016562 | 170 | 71352 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-9706-K | Transpower Hamilton | Network | HAMCB2862 | 13/12/2025 | 10:30 | 13/12/2025 | 12:04 | 0.010989 | 0.0001169 | 12 | 1128 | Unplanned interruptions on the network | Defective Equipment | Cable termination fails
|  | INCD-471-M | Wallace | Network | WALCB5 | 15/12/2025 | 09:21 | 15/12/2025 | 13:04 | 0.095593 | 0.0004287 | 44 | 9812 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-9812-K | Wallace Rd | Network | WALCB2 | 17/12/2025 | 09:30 | 17/12/2025 | 11:12 | 0.082168 | 0.0017926 | 184 | 8434 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-506-M | Gordonton | Network | GORCB11 | 18/12/2025 | 09:10 | 18/12/2025 | 11:41 | 0.01324 | 8.77e-05 | 9 | 1359 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-10095-K | Te Uku | Network | TEUCB11 | 29/12/2025 | 14:20 | 30/12/2025 | 03:10 | 0.059946 | 7.79e-05 | 8 | 6153 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-10173-K | Gordonton | Network | GORCB11 | 30/12/2025 | 07:53 | 30/12/2025 | 12:35 | 0.01098 | 3.9e-05 | 4 | 1127 | Unplanned interruptions on the network | Adverse weather | Line clash high wind
|  | INCD-10332-K | Whatawhata | Network | WHACB4 | 06/01/2026 | 09:34 | 06/01/2026 | 11:47 | 0.066122 | 0.0005261 | 54 | 6787 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-532-M | SpringHill Rd | Network | HPTCB3 | 13/01/2026 | 10:30 | 20/01/2026 | 16:05 | 0.17693 | 0.0003605 | 37 | 18161 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-532-M | SpringHill Rd | Network | SPRCB1 | 13/01/2026 | 10:30 | 20/01/2026 | 16:05 | 0.0047804 | 9.7e-06 | 1 | 490.67 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-1706-L | Finlayson | Network | FINCB4 | 14/01/2026 | 15:20 | 14/01/2026 | 16:23 | 0.050193 | 0.0011886 | 122 | 5152 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (IN Zone)
|  | INCD-1709-L | Finlayson | Network | FINCB4 | 14/01/2026 | 15:20 | 15/01/2026 | 03:09 | 0.0019388 | 0.0001851 | 19 | 199 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (IN Zone)
|  | INCD-10649-K | Peacockes | Network | PEACB12 | 15/01/2026 | 03:23 | 15/01/2026 | 04:59 | 0.06547 | 0.000682 | 70 | 6720 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-527-M | Finlayson | Network | FINCB3 | 16/01/2026 | 09:38 | 16/01/2026 | 14:06 | 0.14711 | 0.0005846 | 60 | 15100 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-10770-K | Chartwell | Network | CHACB9 | 18/01/2026 | 07:40 | 18/01/2026 | 09:10 | 0.0035073 | 3.9e-05 | 4 | 360 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-10811-K | Te Kauwhata | Network | TEKCB2 | 19/01/2026 | 22:01 | 19/01/2026 | 22:58 | 0.047202 | 0.0008281 | 85 | 4845 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (OUT of Zone)
|  | INCD-10812-K | Te Kauwhata | Network | TEKCB2 | 19/01/2026 | 22:01 | 19/01/2026 | 22:17 | 0.0067656 | 0.0042282 | 434 | 694.44 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (OUT of Zone)
|  | INCD-10870-K | Silverdale | Network | SILCB2 | 20/01/2026 | 18:59 | 20/01/2026 | 20:10 | 0.04842 | 0.000682 | 70 | 4970 | Unplanned interruptions on the network | Defective Equipment | Cable short to fuse fram
|  | INCD-1733-L | Hoeka | Private | HOECB3 | 21/01/2026 | 13:27 | 21/01/2026 | 13:38 | 0.0016075 | 0.0001461 | 15 | 165 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-530-M | Weavers | Network | WEACB4 | 23/01/2026 | 08:33 | 23/01/2026 | 16:22 | 0.042974 | 9.74e-05 | 10 | 4411 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-1769-L | Raglan | Network | RAGCB4 | 29/01/2026 | 01:26 | 30/01/2026 | 01:46 | 0.19072 | 0.001286 | 132 | 19576 | Unplanned interruptions on the network | Defective Equipment | Bus chamber flashovr
|  | INCD-11473-K | Gordonton | Network | GORCB13 | 05/02/2026 | 08:02 | 05/02/2026 | 12:21 | 0.0025233 | 9.7e-06 | 1 | 259 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-575-M | Glasgow | Network | GLACB1 | 05/02/2026 | 09:41 | 05/02/2026 | 15:14 | 0.02799 | 8.77e-05 | 9 | 2873 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-12032-K | Weavers | Network | WEACB6 | 24/02/2026 | 08:00 | 24/02/2026 | 14:20 | 0.16306 | 0.0004482 | 46 | 16737 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-261-N | Chartwell | Network | CHACB12 | 25/02/2026 | 08:04 | 25/02/2026 | 11:19 | 0.38566 | 0.0019777 | 203 | 39585 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-12067-K | Latham Court | Network | LATCB7 | 25/02/2026 | 18:48 | 25/02/2026 | 19:45 | 0.0038873 | 6.82e-05 | 7 | 399 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-12148-K | Silverdale | Network | SILCB5 | 03/03/2026 | 04:13 | 03/03/2026 | 05:16 | 0.032092 | 0.0005943 | 61 | 3294 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-649-M | Glasgow | Network | GLACB1 | 04/03/2026 | 08:35 | 04/03/2026 | 10:20 | 0.0015393 | 0.0007697 | 79 | 158 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-1914-L | Te Kauwhata | Network | TEKCB6 | 04/03/2026 | 09:39 | 04/03/2026 | 10:36 | 0.0066639 | 0.0001169 | 12 | 684 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-12236-K | Chartwell | Network | GORCB13 | 06/03/2026 | 09:43 | 06/03/2026 | 12:12 | 0.0099374 | 9.74e-05 | 10 | 1020 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-12239-K | Weavers | Network | WEACB6 | 06/03/2026 | 14:47 | 06/03/2026 | 16:01 | 0.05941 | 0.0024551 | 252 | 6098 | Unplanned interruptions on the network | Wildlife | Bird betw line & pole
|  | INCD-12272-K | Transpower Hamilton | Network | BORCB3 | 09/03/2026 | 06:33 | 09/03/2026 | 07:44 | 0.7857 | 0.011623 | 1193 | 80647 | Unplanned interruptions on the network | Defective Equipment | Loose connection
|  | INCD-12272-K | Transpower Hamilton | Network | BORCB4 | 09/03/2026 | 06:33 | 09/03/2026 | 07:44 | 0.38345 | 0.013815 | 1418 | 39358 | Unplanned interruptions on the network | Defective Equipment | Loose connection
|  | INCD-12306-K | Latham Court | Network | LATCB6 | 10/03/2026 | 22:01 | 11/03/2026 | 04:45 | 0.10362 | 0.000263 | 27 | 10636 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-610-M | Transpower Hamilton | Network | SILCB5 | 12/03/2026 | 09:15 | 12/03/2026 | 13:31 | 0.13289 | 0.0005358 | 55 | 13640 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-12334-K | Te Uku | Network | TEUCB12 | 12/03/2026 | 11:16 | 12/03/2026 | 11:30 | 0.031575 | 0.0021434 | 220 | 3241 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-12382-K | Silverdale | Network | HOECB3 | 14/03/2026 | 23:59 | 15/03/2026 | 00:08 | 0.051324 | 0.0085442 | 877 | 5268.07 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-12383-K | Transpower Hamilton | Network | HOECB4 | 15/03/2026 | 00:04 | 15/03/2026 | 00:07 | 0.0077934 | 0.0024356 | 250 | 799.94 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-677-M | Glasgow | Network | GLACB5 | 19/03/2026 | 08:30 | 19/03/2026 | 13:22 | 0.2552 | 0.0009158 | 94 | 26194 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-2269-L | Whatawhata | Network | WHACB5 | 20/03/2026 | 16:21 | 20/03/2026 | 17:32 | 0.018394 | 0.0002923 | 30 | 1888 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-12624-K | Hoeka | Network | HOECB6 | 24/03/2026 | 08:57 | 24/03/2026 | 09:22 | 0.095106 | 0.0058455 | 600 | 9762 | Unplanned interruptions on the network | Defective Equipment | Flickers misaligned
|  | INCD-12695-K | Horotiu | Network | HORCB6 | 26/03/2026 | 21:50 | 27/03/2026 | 03:29 | 0.16905 | 0.0098692 | 1013 | 17352 | Unplanned interruptions on the network | Defective Equipment | Pins fulls out
|  | INCD-305-N | Peacockes | Network | PEACB13 | 28/03/2026 | 08:47 | 28/03/2026 | 16:08 | 0.53027 | 0.00189 | 194 | 54429 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-760-K | Claudelands | Network | CLACB3 | 01/04/2025 | 00:06 | 01/04/2025 | 00:26 | 0.011603 | 0.000604 | 62 | 1191 | Unplanned interruptions on the network | Third_party | Cable isolated - safety reasons
|  | INCD-958-K | Horotiu | Network | HORCB5 | 06/04/2025 | 21:18 | 06/04/2025 | 23:02 | 0.0030397 | 2.92e-05 | 3 | 312 | Unplanned interruptions on the network | Wildlife | Rodent on HV terminals
|  | INCD-0-M | Transpower Hamilton | Network | HAMCB2902 | 08/04/2025 | 09:47 | 08/04/2025 | 12:49 | 0.093976 | 0.0005164 | 53 | 9646 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-1036-K | Weavers | Network | WEACB5 | 08/04/2025 | 13:43 | 08/04/2025 | 15:06 | 0.0008086 | 9.7e-06 | 1 | 83 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-1051-K | Whatawhata | Network | WHACB3 | 08/04/2025 | 16:15 | 08/04/2025 | 22:28 | 0.010902 | 2.92e-05 | 3 | 1119 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-210-K | Ngaruawahia | Network | NGACB3 | 14/04/2025 | 08:08 | 14/04/2025 | 18:07 | 0.11968 | 0.0006235 | 64 | 12284 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-1437-K | Weavers | Network | NGACB2 | 17/04/2025 | 12:32 | 17/04/2025 | 13:10 | 0.23433 | 0.0061475 | 631 | 24052 | Unplanned interruptions on the network | Adverse weather | Line clash high wind
|  | INCD-16-M | Raglan | Network | RAGCB6 | 18/04/2025 | 14:51 | 18/04/2025 | 23:45 | 0 | 0.0098497 | 1011 | 0 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-16-M | Raglan | Network | TEUCB13 | 18/04/2025 | 14:51 | 18/04/2025 | 23:45 | 0.01262 | 0.0007794 | 80 | 1295.37 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-1591-K | Peacockes Rd | Network | PEACB12 | 19/04/2025 | 13:56 | 19/04/2025 | 14:38 | 0.12227 | 0.0085344 | 876 | 12550 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (OUT of Zone)
|  | INCD-35-L | Claudelands | Private | CLACB3 | 23/04/2025 | 14:45 | 23/04/2025 | 14:47 | 0.0031955 | 0.0015978 | 164 | 328 | Unplanned interruptions on the network | Third_party | Temp Disconnect / safety isolation
|  | INCD-1686-K | Finlayson Rd | Network | FINCB2 | 23/04/2025 | 23:49 | 23/04/2025 | 23:51 | 0.0014224 | 0.0043062 | 442 | 146 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-1710-K | Te Uku | Network | TEUCB11 | 24/04/2025 | 16:35 | 24/04/2025 | 18:12 | 0.0047251 | 4.87e-05 | 5 | 485 | Unplanned interruptions on the network | Lightning | Spontaneous failure
|  | INCD-1736-K | Horotiu | Network | KOHCB6 | 26/04/2025 | 07:57 | 26/04/2025 | 09:22 | 0.01325 | 0.0001559 | 16 | 1360 | Unplanned interruptions on the network | Defective Equipment | Contact problem
|  | INCD-2022-K | Wallace Rd | Network | WALCB6 | 02/05/2025 | 15:06 | 02/05/2025 | 17:52 | 0.0032345 | 1.95e-05 | 2 | 332 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-55-L | Latham | Network | LATCB5 | 06/05/2025 | 09:34 | 06/05/2025 | 18:07 | 1.2172 | 0.0025623 | 263 | 124936 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-2143-K | Whatawhata | Network | WHACB4 | 06/05/2025 | 18:16 | 08/05/2025 | 17:03 | 0.054694 | 1.95e-05 | 2 | 5614 | Unplanned interruptions on the network | Third_party | Tree felled into line (Third Party)
|  | INCD-2208-K | Weavers | Network | WEACB6 | 08/05/2025 | 09:08 | 08/05/2025 | 13:11 | 0.0094697 | 3.9e-05 | 4 | 972 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-39-M | Steele Park | Network | STECB8 | 08/05/2025 | 20:24 | 09/05/2025 | 03:24 | 0.036827 | 8.77e-05 | 9 | 3780 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2351-K | Wallace Rd | Network | PEACB12 | 09/05/2025 | 22:57 | 09/05/2025 | 22:58 | 0.0018934 | 0.0012081 | 124 | 194.34 | Unplanned interruptions on the network | Defective Equipment | Wear or shear of pins
|  | INCD-2315-K | Te Kauwhata | Network | FINCB3 | 11/05/2025 | 07:54 | 11/05/2025 | 08:59 | 0.029917 | 0.0012373 | 127 | 3070.82 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2315-K | Te Kauwhata | Network | WEACB3 | 11/05/2025 | 07:54 | 11/05/2025 | 08:59 | 0.0005495 | 5.85e-05 | 6 | 56.4 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-48-M | Chartwell | Network | CHACB12 | 14/05/2025 | 10:10 | 14/05/2025 | 17:59 | 0.81297 | 0.0018413 | 189 | 83446 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2590-K | Gordonton | Network | GORCB13 | 19/05/2025 | 09:12 | 19/05/2025 | 14:48 | 0.13562 | 0.000984 | 101 | 13920 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2700-K | Latham Court | Network | LATCB5 | 21/05/2025 | 09:51 | 21/05/2025 | 10:39 | 0.39418 | 0.0083396 | 856 | 40460 | Unplanned interruptions on the network | Defective Equipment | Wear or shear of pins
|  | INCD-2846-K | Cobham Dr | Network | BRYCB3 | 25/05/2025 | 06:47 | 25/05/2025 | 06:52 | 0.0001461 | 2.92e-05 | 3 | 15 | Planned interruptions on the network | Unknown | RMU Replacement
|  | INCD-2988-K | Peacockes | Network | PEACB13 | 29/05/2025 | 08:38 | 29/05/2025 | 16:05 | 0.55743 | 0.001247 | 128 | 57216 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-3017-K | Te Uku | Network | TEUCB11 | 29/05/2025 | 14:11 | 31/05/2025 | 12:19 | 0.1377 | 0.0020167 | 207 | 14134 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-3205-K | Bryce St | Network | BRYCB12 | 04/06/2025 | 08:14 | 04/06/2025 | 08:14 | 0.0036924 | 9.7e-06 | 1 | 379 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-3373-K | Avalon Dr | Network | AVACB7 | 08/06/2025 | 08:06 | 08/06/2025 | 17:15 | 0.0053486 | 9.7e-06 | 1 | 549 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-89-L | Claudelands | Network | CLACB13 | 10/06/2025 | 22:19 | 11/06/2025 | 02:29 | 0.27766 | 0.0011106 | 114 | 28500 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-3647-K | Simsey | Network | SIMCB2 | 14/06/2025 | 08:19 | 14/06/2025 | 08:37 | 0.0001754 | 9.7e-06 | 1 | 18 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-3709-K | Glasgow St | Network | GLACB2 | 16/06/2025 | 10:04 | 16/06/2025 | 13:48 | 0.017459 | 7.79e-05 | 8 | 1792 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-137-M | Hampton Downs | Network | HPTCB3 | 24/06/2025 | 08:03 | 24/06/2025 | 16:06 | 0.16271 | 0.0003605 | 37 | 16701 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-137-M | Hampton Downs | Network | HPTCB4 | 24/06/2025 | 08:03 | 24/06/2025 | 16:06 | 0.0044036 | 9.7e-06 | 1 | 452 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-137-M | Hampton Downs | Network | TEKCB2 | 24/06/2025 | 08:03 | 24/06/2025 | 16:06 | 1.3449 | 0.0029422 | 302 | 138046 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-135-M | Horotiu | Network | HORCB5 | 24/06/2025 | 08:45 | 24/06/2025 | 15:05 | 0.014809 | 3.9e-05 | 4 | 1520 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-129-M | Glasgow | Network | GLACB2 | 25/06/2025 | 10:09 | 25/06/2025 | 14:26 | 0.05258 | 0.0002338 | 24 | 5397 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-4024-K | Te Kauwhata | Network | TEKCB5 | 29/06/2025 | 09:22 | 29/06/2025 | 11:09 | 0.0031273 | 2.92e-05 | 3 | 321 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-146-M | Chartwell | Network | CHACB12 | 01/07/2025 | 09:39 | 01/07/2025 | 12:48 | 0.19702 | 0.0010424 | 107 | 20223 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-4067-K | Whatawhata | Network | WHACB2 | 01/07/2025 | 13:11 | 01/07/2025 | 16:58 | 1.0108 | 0.0046374 | 476 | 103752 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-4067-K | Whatawhata | Network | WHACB4 | 01/07/2025 | 13:11 | 01/07/2025 | 16:58 | 0.23603 | 0.0010424 | 107 | 24227 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-4083-K | Finlayson | Network | FINCB2 | 02/07/2025 | 00:10 | 02/07/2025 | 00:14 | 0.0097522 | 0.0021921 | 225 | 1001 | Unplanned interruptions on the network | Defective Equipment | Loose connection
|  | INCD-4084-K | Te Uku Wind Farm | Network | RAGCB6 | 02/07/2025 | 00:34 | 02/07/2025 | 00:46 | 0.125 | 0.0099471 | 1021 | 12830.54 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-4185-K | Te Uku | Network | TEUCB11 | 04/07/2025 | 16:30 | 04/07/2025 | 16:35 | 0.0003312 | 6.82e-05 | 7 | 34 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-159-M | Avalon | Network | AVACB3 | 07/07/2025 | 08:50 | 07/07/2025 | 12:05 | 0.18048 | 0.0009255 | 95 | 18525 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-245-M | Te Kauwhata | Network | TEKCB5 | 07/07/2025 | 08:51 | 07/07/2025 | 14:35 | 0.013406 | 3.9e-05 | 4 | 1376 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-4392-K | Whitiora School | Network | WHICB7 | 10/07/2025 | 06:47 | 10/07/2025 | 06:52 | 4.87e-05 | 9.7e-06 | 1 | 5 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-165-M | Hoeka | Network | HOECB6 | 11/07/2025 | 10:00 | 11/07/2025 | 15:54 | 0.15343 | 0.0006917 | 71 | 15748 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-157-M | MAF | Network | MAFCB6 | 12/07/2025 | 09:49 | 12/07/2025 | 15:47 | 0.0066736 | 2.92e-05 | 3 | 685 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-4667-K | Hoeka | Network | HOECB1 | 17/07/2025 | 09:30 | 17/07/2025 | 16:49 | 0.40798 | 0.0012958 | 133 | 41876 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-209-M | Glasgow | Network | GLACB6 | 22/07/2025 | 08:32 | 22/07/2025 | 14:08 | 0.082539 | 0.0002533 | 26 | 8472 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-444-L | Finlayson Rd | Network | FINCB1 | 25/07/2025 | 08:41 | 25/07/2025 | 12:17 | 0.0021044 | 9.7e-06 | 1 | 216 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-5090-K | Hoeka | Network | HOECB6 | 27/07/2025 | 17:34 | 28/07/2025 | 00:01 | 0.20157 | 0.0010912 | 112 | 20690 | Unplanned interruptions on the network | Wildlife | Bird lne clash/break
|  | INCD-5156-K | Ngaruawahia | Network | NGACB2 | 29/07/2025 | 07:33 | 29/07/2025 | 11:45 | 0.15404 | 0.0033222 | 341 | 15811 | Unplanned interruptions on the network | Defective Equipment | Burning crossarm
|  | INCD-5168-K | Whatawhata | Network | WHACB4 | 29/07/2025 | 06:37 | 29/07/2025 | 10:19 | 0.012977 | 5.85e-05 | 6 | 1332 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-5325-K | Hoeka | Network | HOECB6 | 03/08/2025 | 13:37 | 03/08/2025 | 18:01 | 0.57961 | 0.0058358 | 599 | 59493 | Unplanned interruptions on the network | Defective Equipment | Line break at twist joint
|  | INCD-518-L | Te Kauwhata | Network | TEKCB5 | 11/08/2025 | 09:34 | 11/08/2025 | 12:24 | 0.0066249 | 3.9e-05 | 4 | 680 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-5689-K | Transpower Hamilton | Network | HAMCB2722 | 13/08/2025 | 00:34 | 13/08/2025 | 01:40 | 0.037937 | 0.0005748 | 59 | 3894 | Unplanned interruptions on the network | Defective Equipment | Fuse blown on overload
|  | INCD-5705-K | Weavers | Network | WEACB2 | 13/08/2025 | 09:41 | 13/08/2025 | 15:24 | 0.16769 | 0.0005261 | 54 | 17212 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-5772-K | Te Kauwhata | Network | TEKCB5 | 14/08/2025 | 10:18 | 14/08/2025 | 13:52 | 0.0062547 | 2.92e-05 | 3 | 642 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-5827-K | Transpower Hamilton | Network | HAMCB2802 | 16/08/2025 | 10:49 | 16/08/2025 | 11:17 | 0.0072095 | 0.000263 | 27 | 740 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-5934-K | Whatawhata | Network | WHACB6 | 19/08/2025 | 06:21 | 19/08/2025 | 12:39 | 0.015111 | 0.0001072 | 11 | 1551 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-527-L | Te Kauwhata | Network | TEKCB3 | 20/08/2025 | 09:34 | 20/08/2025 | 15:07 | 0.025954 | 7.79e-05 | 8 | 2664 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-6018-K | Transpower Hamilton | Network | HAMCB2722 | 20/08/2025 | 20:53 | 20/08/2025 | 21:04 | 0.0080473 | 0.0011496 | 118 | 826 | Unplanned interruptions on the network | Defective Equipment | Fuse blown on overload
|  | INCD-257-M | Latham | Network | LATCB5 | 21/08/2025 | 09:40 | 21/08/2025 | 14:52 | 0.52022 | 0.0017244 | 177 | 53397 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-6066-K | Whatawhata | Network | WHACB5 | 21/08/2025 | 19:12 | 21/08/2025 | 22:54 | 0.074257 | 0.0003605 | 37 | 7622 | Unplanned interruptions on the network | Defective Equipment | Nut or bolt loose
|  | INCD-6071-K | Hampton Downs | Network | HPTCB5 | 21/08/2025 | 17:00 | 21/08/2025 | 20:46 | 0.019816 | 8.77e-05 | 9 | 2034 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-281-M | Ngaruawahia | Network | NGACB5 | 26/08/2025 | 08:42 | 26/08/2025 | 19:29 | 0.38477 | 0.0006235 | 64 | 39494 | Planned interruptions on the network | Planned | New Connections
|  | INCD-271-M | Sandwich | Network | SANCB2 | 28/08/2025 | 09:02 | 28/08/2025 | 17:12 | 0.47711 | 0.0016075 | 165 | 48972 | Planned interruptions on the network | Planned | Recloser & Sectionaliser replacement
|  | INCD-6338-K | Hoeka | Network | HOECB4 | 30/08/2025 | 06:27 | 30/08/2025 | 08:29 | 0.0035658 | 2.92e-05 | 3 | 366 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-6369-K | Weavers | Network | WEACB2 | 31/08/2025 | 13:59 | 31/08/2025 | 15:53 | 0.055289 | 0.0005651 | 58 | 5675 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (OUT of Zone)
|  | INCD-6410-K | Horotiu | Network | GORCB11 | 31/08/2025 | 18:22 | 31/08/2025 | 18:41 | 0.10097 | 0.0056409 | 579 | 10364 | Unplanned interruptions on the network | Defective Equipment | Broken binder
|  | INCD-6441-K | Gordonton | Network | GORCB12 | 31/08/2025 | 19:19 | 31/08/2025 | 23:48 | 0.020907 | 7.79e-05 | 8 | 2146 | Unplanned interruptions on the network | Adverse weather | Line clash high wind
|  | INCD-119-N | Te Uku | Network | TEUCB11 | 31/08/2025 | 20:09 | 01/09/2025 | 14:30 | 0.021453 | 1.95e-05 | 2 | 2202 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-6525-K | Chartwell | Network | CHACB9 | 02/09/2025 | 03:31 | 02/09/2025 | 05:38 | 0.0037119 | 2.92e-05 | 3 | 381 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-6566-K | Weavers | Network | WEACB3 | 02/09/2025 | 14:11 | 02/09/2025 | 14:26 | 0.0002923 | 1.95e-05 | 2 | 30 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-279-M | Chartwell | Network | CHACB9 | 03/09/2025 | 09:30 | 03/09/2025 | 15:59 | 0.13371 | 0.0006235 | 64 | 13724 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-287-M | Transpower Hamilton | Network | HAMCB2742 | 08/09/2025 | 09:01 | 08/09/2025 | 12:12 | 0.16412 | 0.0008573 | 88 | 16846 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-287-M | Transpower Hamilton | Network | HAMCB2902 | 08/09/2025 | 09:01 | 08/09/2025 | 12:12 | 0.16671 | 0.0009061 | 93 | 17112 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-6883-K | Kent St | Network | MASCB12 | 09/09/2025 | 09:15 | 09/09/2025 | 09:33 | 0.20375 | 0.011555 | 1186 | 20913.01 | Unplanned interruptions on the network | Defective Equipment | Cable joint fails
|  | INCD-6883-K | Kent St | Network | MASCB18 | 09/09/2025 | 09:15 | 09/09/2025 | 09:33 | 0.014602 | 0.0008281 | 85 | 1498.82 | Unplanned interruptions on the network | Defective Equipment | Cable joint fails
|  | INCD-289-M | Peacockes | Network | PEACB12 | 11/09/2025 | 09:51 | 11/09/2025 | 18:06 | 0.15914 | 0.0003215 | 33 | 16335 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-7020-K | Finlayson | Network | FINCB2 | 12/09/2025 | 09:02 | 12/09/2025 | 15:21 | 0.11453 | 0.0005261 | 54 | 11756 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-341-M | Pukete | Network | KOHCB4 | 17/09/2025 | 08:56 | 17/09/2025 | 14:22 | 0.0092554 | 0.0003312 | 34 | 950 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-342-M | Pukete | Network | KOHCB4 | 18/09/2025 | 09:50 | 18/09/2025 | 17:31 | 0.0033319 | 8.77e-05 | 9 | 342 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-7405-K | Transpower Hamilton | Network | HAMCB2902 | 19/09/2025 | 15:18 | 19/09/2025 | 19:23 | 0.20289 | 0.0008281 | 85 | 20825 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-228-M | Glasgow | Network | GLACB2 | 23/09/2025 | 09:13 | 23/09/2025 | 18:05 | 0.4974 | 0.0009743 | 100 | 51055 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-7664-K | Horotiu | Network | KOHCB6 | 27/09/2025 | 11:26 | 27/09/2025 | 14:31 | 0.010814 | 5.85e-05 | 6 | 1110 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-7783-K | Horotiu | Network | HORCB6 | 01/10/2025 | 06:26 | 01/10/2025 | 07:00 | 0.0006625 | 1.95e-05 | 2 | 68 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-7936-K | Te Kauwhata | Network | TEKCB6 | 04/10/2025 | 10:39 | 04/10/2025 | 21:24 | 0.0062839 | 9.7e-06 | 1 | 645 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-7945-K | Finlayson Rd | Network | FINCB2 | 04/10/2025 | 11:41 | 04/10/2025 | 15:00 | 0.007755 | 3.9e-05 | 4 | 796 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-8114-K | Hoeka | Network | HOECB1 | 09/10/2025 | 17:02 | 09/10/2025 | 21:23 | 0.0178 | 6.82e-05 | 7 | 1827 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-8128-K | Te Kauwhata | Network | TEKCB2 | 10/10/2025 | 09:07 | 10/10/2025 | 13:22 | 0.024843 | 9.74e-05 | 10 | 2550 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-8139-K | Transpower Hamilton | Network | HAMCB2902 | 10/10/2025 | 17:39 | 10/10/2025 | 19:00 | 0.77967 | 0.012626 | 1296 | 80027.85 | Unplanned interruptions on the network | Defective Equipment | Bus chamber flashovr
|  | INCD-8156-K | Gordonton | Network | GORCB13 | 12/10/2025 | 06:59 | 12/10/2025 | 07:27 | 0.0002728 | 9.7e-06 | 1 | 28 | Unplanned interruptions on the network | Wildlife | Bird betw line & pole
|  | INCD-8242-K | Civic Car Park | Network | CIVCB5 | 15/10/2025 | 22:01 | 16/10/2025 | 03:22 | 0.16262 | 0.0005066 | 52 | 16692 | Planned interruptions on the network | Planned | Distribution Transformer Replacement
|  | INCD-8292-K | Finlayson | Network | FINCB2 | 18/10/2025 | 12:41 | 18/10/2025 | 14:41 | 0.035619 | 0.0003118 | 32 | 3656 | Unplanned interruptions on the network | Defective Equipment | Faulty joint/connection
|  | INCD-8329-K | Te Uku | Network | TEUCB11 | 20/10/2025 | 16:59 | 20/10/2025 | 23:49 | 0.11423 | 0.0052512 | 539 | 11725 | Unplanned interruptions on the network | Third_party | Vehicle hits lines
|  | INCD-368-M | Finlayson | Network | FINCB2 | 21/10/2025 | 09:31 | 21/10/2025 | 12:25 | 0.05827 | 0.0005358 | 55 | 5981 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-8362-K | Te Uku | Network | NGACB2 | 22/10/2025 | 07:21 | 22/10/2025 | 09:35 | 0.044068 | 0.000341 | 35 | 4523.3 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-369-M | Borman | Network | BORCB3 | 22/10/2025 | 09:05 | 22/10/2025 | 13:25 | 0.23051 | 0.0008866 | 91 | 23660 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-362-M | Raglan | Network | RAGCB2 | 23/10/2025 | 09:39 | 23/10/2025 | 15:42 | 0.10226 | 0.0031955 | 328 | 10496 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-8389-K | Gordonton | Network | GORCB13 | 23/10/2025 | 15:29 | 24/10/2025 | 01:45 | 0.011857 | 1.95e-05 | 2 | 1217 | Unplanned interruptions on the network | Defective Equipment | Intnl insulation failure
|  | INCD-8456-K | Ngaruawahia | Network | NGACB6 | 28/10/2025 | 06:10 | 28/10/2025 | 07:51 | 0.0036827 | 3.9e-05 | 4 | 378 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-382-M | Civic Car Park | Network | CIVCB4 | 29/10/2025 | 22:08 | 29/10/2025 | 23:09 | 0.026743 | 0.0004384 | 45 | 2745 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-8575-K | Ngaruawahia | Network | NGACB2 | 01/11/2025 | 13:54 | 01/11/2025 | 15:49 | 0.0011204 | 9.7e-06 | 1 | 115 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-8687-K | Weavers | Network | WEACB6 | 05/11/2025 | 20:17 | 05/11/2025 | 22:34 | 0.0080083 | 5.85e-05 | 6 | 822 | Unplanned interruptions on the network | Defective Equipment | Loss or failure of oil
|  | INCD-8732-K | Ngaruawahia | Network | NGACB2 | 08/11/2025 | 09:48 | 08/11/2025 | 15:05 | 0.47064 | 0.004199 | 431 | 48308 | Unplanned interruptions on the network | Defective Equipment | Contact problem
|  | INCD-402-M | Latham | Network | LATCB2 | 11/11/2025 | 09:08 | 11/11/2025 | 15:40 | 0.85547 | 0.0021823 | 224 | 87808 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-8967-K | Ngaruawahia | Network | NGACB6 | 16/11/2025 | 19:53 | 17/11/2025 | 14:50 | 0.28804 | 0.0009255 | 95 | 29565 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-425-M | Glasgow | Network | GLACB2 | 17/11/2025 | 09:30 | 17/11/2025 | 13:11 | 0.1094 | 0.0005456 | 56 | 11229 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-9083-K | Bryce St | Network | BRYCB12 | 19/11/2025 | 14:41 | 19/11/2025 | 15:03 | 0.020576 | 0.0009353 | 96 | 2112 | Unplanned interruptions on the network | Defective Equipment | Fuse blown on overload
|  | INCD-9150-K | Gordonton | Network | GORCB12 | 21/11/2025 | 07:57 | 21/11/2025 | 09:34 | 0.0028351 | 2.92e-05 | 3 | 291 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-9171-K | Latham Court | Network | LATCB2 | 22/11/2025 | 01:33 | 22/11/2025 | 08:42 | 0.64132 | 0.0034001 | 349 | 65827 | Unplanned interruptions on the network | Defective Equipment | Broken insulator/bush
|  | INCD-9238-K | Latham | Network | LATCB2 | 25/11/2025 | 09:12 | 25/11/2025 | 09:37 | 0.027766 | 0.0011106 | 114 | 2850 | Unplanned interruptions on the network | Defective Equipment | Broken insulator/bush
|  | INCD-441-M | Finlayson | Network | FINCB2 | 02/12/2025 | 09:35 | 02/12/2025 | 15:40 | 0.13288 | 0.0003897 | 40 | 13639 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-9376-K | Glasgow St | Network | GLACB2 | 03/12/2025 | 18:18 | 03/12/2025 | 19:57 | 0.0077161 | 7.79e-05 | 8 | 792 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-9453-K | Weavers | Network | WEACB3 | 06/12/2025 | 05:31 | 06/12/2025 | 16:52 | 0.67285 | 0.010308 | 1058 | 69063 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-461-M | Gordonton | Network | GORCB11 | 11/12/2025 | 08:49 | 11/12/2025 | 16:49 | 1.1024 | 0.0024161 | 248 | 113153 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-507-M | Finlayson | Network | FINCB2 | 12/12/2025 | 10:18 | 12/12/2025 | 17:00 | 0.17901 | 0.0004676 | 48 | 18374 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-455-M | Cobham | Network | COBCB9 | 13/12/2025 | 08:33 | 13/12/2025 | 10:17 | 0.0020264 | 1.95e-05 | 2 | 208 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-488-M | Finlayson | Network | FINCB2 | 15/12/2025 | 09:42 | 15/12/2025 | 16:30 | 0.0159 | 3.9e-05 | 4 | 1632 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-9019-K | Avalon | Network | AVACB8 | 18/12/2025 | 09:07 | 18/12/2025 | 13:26 | 0.037021 | 0.0037022 | 380 | 3800 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-9889-K | Transpower Hamilton | Network | UNICB4 | 18/12/2025 | 16:55 | 18/12/2025 | 17:09 | 0.0001364 | 9.7e-06 | 1 | 14 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-10027-K | Gordonton | Network | GORCB13 | 23/12/2025 | 15:51 | 23/12/2025 | 18:15 | 0.075865 | 0.0005261 | 54 | 7787 | Unplanned interruptions on the network | Defective Equipment | Split crossarm
|  | INCD-10067-K | Weavers | Network | WEACB6 | 26/12/2025 | 13:03 | 26/12/2025 | 20:41 | 0.12202 | 0.0009645 | 99 | 12525 | Unplanned interruptions on the network | Defective Equipment | Contact problem
|  | INCD-10082-K | Te Kauwhata | Network | TEKCB5 | 28/12/2025 | 19:23 | 28/12/2025 | 20:13 | 0.070146 | 0.0014029 | 144 | 7200 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-10293-K | Weavers | Network | TEKCB5 | 29/12/2025 | 00:27 | 29/12/2025 | 00:45 | 0.0063962 | 0.0003507 | 36 | 656.53 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-10158-K | Raglan | Network | RAGCB4 | 29/12/2025 | 21:13 | 30/12/2025 | 00:12 | 0.21926 | 0.0015685 | 161 | 22506 | Unplanned interruptions on the network | Defective Equipment | Connect/jumper loose
|  | INCD-10204-K | Weavers | Network | WEACB6 | 29/12/2025 | 18:20 | 30/12/2025 | 22:41 | 0.033144 | 1.95e-05 | 2 | 3402 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-10301-K | MAF | Network | MAFCB3 | 02/01/2026 | 17:10 | 02/01/2026 | 18:32 | 0.0007989 | 9.7e-06 | 1 | 82 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-10403-K | Transpower Hamilton | Network | HAMCB2902 | 08/01/2026 | 09:10 | 08/01/2026 | 15:34 | 0.90309 | 0.0023577 | 242 | 92696 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-1693-L | Weavers | Network | WEACB4 | 11/01/2026 | 11:41 | 11/01/2026 | 16:58 | 0.012353 | 3.9e-05 | 4 | 1268 | Unplanned interruptions on the network | Defective Equipment | Faulty joint/connection
|  | INCD-532-M | SpringHill Rd | Network | HPTCB2 | 13/01/2026 | 10:30 | 20/01/2026 | 16:05 | 0.0095606 | 1.95e-05 | 2 | 981.33 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-1762-L | Claudelands | Network | CLACB16 | 15/01/2026 | 22:04 | 15/01/2026 | 22:42 | 0.026655 | 0.0007015 | 72 | 2736 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-571-M | Glasgow | Network | GLACB1 | 16/01/2026 | 08:34 | 16/01/2026 | 11:23 | 0.018111 | 0.0001072 | 11 | 1859 | Planned interruptions on the network | Planned | Distribution Transformer Replacement
|  | INCD-1766-L | Weavers | Network | WEACB6 | 16/01/2026 | 11:49 | 16/01/2026 | 16:20 | 0.0052804 | 1.95e-05 | 2 | 542 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-10744-K | Kent St | Network | KENCB12 | 17/01/2026 | 10:42 | 17/01/2026 | 11:42 | 0.089436 | 0.0014906 | 153 | 9180 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-10873-K | Gordonton | Network | GORCB11 | 20/01/2026 | 20:35 | 21/01/2026 | 03:14 | 0.70181 | 0.0018024 | 185 | 72036 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-1767-L | Cobham Dr | Network | COBCB3 | 21/01/2026 | 14:57 | 21/01/2026 | 15:03 | 0.008476 | 0.0014127 | 145 | 870 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-10952-K | Hoeka | Network | HOECB2 | 22/01/2026 | 00:44 | 22/01/2026 | 00:49 | 0.0042477 | 0.0007891 | 81 | 436 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (OUT of Zone)
|  | INCD-10954-K | Hoeka | Network | HOECB2 | 22/01/2026 | 03:20 | 22/01/2026 | 06:20 | 0.005261 | 2.92e-05 | 3 | 540 | Unplanned interruptions on the network | Defective Equipment | Jumper fails on thru flt
|  | INCD-10998-K | Hoeka | Network | HOECB6 | 22/01/2026 | 10:36 | 22/01/2026 | 16:00 | 0.17327 | 0.0011106 | 114 | 17785 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (OUT of Zone)
|  | INCD-11113-K | Hoeka | Network | HOECB1 | 22/01/2026 | 11:13 | 24/01/2026 | 15:46 | 0.0013737 | 9.7e-06 | 1 | 141 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-561-M | Horotiu | Network | HORCB3 | 23/01/2026 | 09:04 | 23/01/2026 | 13:52 | 0.15993 | 0.0005553 | 57 | 16416 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-11070-K | Finlayson Rd | Network | FINCB1 | 23/01/2026 | 13:40 | 23/01/2026 | 15:43 | 0.15413 | 0.0040139 | 412 | 15820 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (OUT of Zone)
|  | INCD-11114-K | Hoeka | Network | HOECB1 | 24/01/2026 | 15:46 | 24/01/2026 | 16:05 | 0.026646 | 0.0063131 | 648 | 2735 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-560-M | Wallace Rd | Network | WALCB6 | 27/01/2026 | 09:01 | 27/01/2026 | 16:16 | 0.11197 | 0.0003215 | 33 | 11493 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-569-M | Finlayson | Network | FINCB2 | 28/01/2026 | 09:37 | 28/01/2026 | 18:02 | 0.1408 | 0.0003118 | 32 | 14452 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-11293-K | Te Uku | Network | TEUCB11 | 29/01/2026 | 12:50 | 29/01/2026 | 13:34 | 0.001286 | 2.92e-05 | 3 | 132 | Unplanned interruptions on the network | Wildlife | Possum across structure
|  | INCD-583-M | Horotiu | Network | HORCB6 | 05/02/2026 | 09:43 | 05/02/2026 | 13:52 | 0.44359 | 0.00189 | 194 | 45531 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-10312-K | Finlayson | Network | FINCB1 | 10/02/2026 | 09:28 | 10/02/2026 | 14:35 | 0.044864 | 0.0001461 | 15 | 4605 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-11660-K | Transpower Hamilton | Network | HAMCB2722 | 11/02/2026 | 16:09 | 11/02/2026 | 19:51 | 0.14707 | 0.0006625 | 68 | 15096 | Unplanned interruptions on the network | Defective Equipment | Connect/jumper loose
|  | INCD-265-N | Hampton Downs | Network | FINCB2 | 15/02/2026 | 08:29 | 15/02/2026 | 17:24 | 0.47306 | 0.0017147 | 176 | 48556 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-11836-K | Chartwell | Network | CHACB9 | 17/02/2026 | 21:55 | 17/02/2026 | 23:24 | 0.033816 | 0.00038 | 39 | 3471 | Unplanned interruptions on the network | Defective Equipment | Split crossarm
|  | INCD-260-N | Raglan | Network | RAGCB6 | 18/02/2026 | 08:43 | 18/02/2026 | 15:57 | 1.0199 | 0.0024941 | 256 | 104682 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-601-M | Wallace | Network | WALCB6 | 18/02/2026 | 09:19 | 18/02/2026 | 15:28 | 0.23498 | 0.0006917 | 71 | 24119 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-631-M | Weavers | Network | WEACB6 | 24/02/2026 | 08:18 | 24/02/2026 | 11:15 | 0.017244 | 9.74e-05 | 10 | 1770 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-12046-K | Ngaruawahia | Network | NGACB2 | 24/02/2026 | 16:26 | 24/02/2026 | 20:42 | 0.0099763 | 3.9e-05 | 4 | 1024 | Unplanned interruptions on the network | Defective Equipment | Contact problem
|  | INCD-517-M | Whatawhata | Network | WHACB3 | 25/02/2026 | 09:21 | 25/02/2026 | 15:18 | 0.26881 | 0.0008086 | 83 | 27591 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-637-M | Weaver | Network | WEACB6 | 26/02/2026 | 09:16 | 26/02/2026 | 09:16 | 0.0088462 | 1.95e-05 | 2 | 908 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-12173-K | Te Kauwhata | Network | TEKCB6 | 03/03/2026 | 21:28 | 03/03/2026 | 22:42 | 0.0086513 | 0.0001169 | 12 | 888 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-12183-K | Steele Park | Network | STECB3 | 04/03/2026 | 08:16 | 04/03/2026 | 09:07 | 0.10385 | 0.0020362 | 209 | 10659 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-12229-K | Finalyson | Network | FINCB1 | 05/03/2026 | 13:28 | 06/03/2026 | 02:35 | 0.31116 | 0.0004969 | 51 | 31938 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-12234-K | Glasgow | Network | GLACB1 | 06/03/2026 | 06:27 | 06/03/2026 | 09:07 | 0.0015588 | 9.7e-06 | 1 | 160 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-610-M | Transpower Hamilton | Network | HAMCB2862 | 12/03/2026 | 09:15 | 12/03/2026 | 13:31 | 0.41846 | 0.0016757 | 172 | 42952 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2123-L | Whatawhata | Private | WHACB5 | 13/03/2026 | 16:56 | 13/03/2026 | 17:32 | 0.0035073 | 9.74e-05 | 10 | 360 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-12379-K | Silverdale | Network | SILCB5 | 14/03/2026 | 15:57 | 14/03/2026 | 17:18 | 0.32406 | 0.004501 | 462 | 33263 | Unplanned interruptions on the network | Unknown | Fire Risk Mitigation Patrol - Sucessfully reclosed
|  | INCD-12456-K | Wallace Rd | Network | WHACB4 | 17/03/2026 | 09:30 | 17/03/2026 | 12:15 | 0.10108 | 0.0006138 | 63 | 10375 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-12479-K | Tasman | Network | TASCB5 | 18/03/2026 | 22:39 | 19/03/2026 | 01:43 | 0.0085929 | 8.77e-05 | 9 | 882 | Unplanned interruptions on the network | Defective Equipment | Fuse blow from overload
|  | INCD-657-M | Te Uku | Network | TEUCB11 | 20/03/2026 | 09:49 | 20/03/2026 | 13:17 | 0.0081058 | 3.9e-05 | 4 | 832 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2260-L | Avalon | Network | AVACB1 | 20/03/2026 | 14:02 | 20/03/2026 | 14:30 | 0.02155 | 0.0007697 | 79 | 2212 | Planned interruptions on the network | Planned | New Connections
|  | INCD-12596-K | Weavers | Network | WEACB6 | 22/03/2026 | 08:57 | 22/03/2026 | 10:53 | 0.068295 | 0.0040139 | 412 | 7010 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-689-M | Weavers | Network | WEACB3 | 23/03/2026 | 07:26 | 23/03/2026 | 15:18 | 0.048235 | 0.0001754 | 18 | 4951 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-669-M | Whatawhata | Network | WHACB3 | 24/03/2026 | 09:41 | 24/03/2026 | 15:21 | 0.019875 | 5.85e-05 | 6 | 2040 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-12699-K | Hoeka | Network | HOECB6 | 27/03/2026 | 00:45 | 27/03/2026 | 01:17 | 0.041289 | 0.0012763 | 131 | 4238 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (IN Zone)
|  | INCD-687-M | Hampton Downs | Network | HPTCB5 | 27/03/2026 | 08:36 | 27/03/2026 | 12:23 | 0.42261 | 0.00189 | 194 | 43378 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-12804-K | Cobham | Network | COBCB9 | 31/03/2026 | 04:19 | 31/03/2026 | 05:12 | 0.0005164 | 9.7e-06 | 1 | 53 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-691-M | Glasgow | Network | GLACB2 | 31/03/2026 | 09:31 | 31/03/2026 | 16:29 | 0.0079889 | 1.95e-05 | 2 | 820 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-774-K | Wallace Rd | Network | WALCB6 | 01/04/2025 | 10:06 | 01/04/2025 | 12:15 | 0.017595 | 0.0001364 | 14 | 1806 | Unplanned interruptions on the network | Defective Equipment | Rotten crossarm
|  | INCD-28-M | Sandwich | Network | SANCB6 | 08/04/2025 | 09:31 | 08/04/2025 | 17:29 | 0.96006 | 0.002231 | 229 | 98543 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-20-L | Sandwich Rd | Network | SANCB6 | 09/04/2025 | 16:51 | 09/04/2025 | 17:50 | 0.020693 | 0.0003507 | 36 | 2124 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-1115-K | Weavers | Network | WEACB2 | 09/04/2025 | 18:02 | 09/04/2025 | 21:05 | 0.016046 | 8.77e-05 | 9 | 1647 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-12-M | Wallace | Network | WALCB2 | 11/04/2025 | 09:45 | 11/04/2025 | 14:10 | 0.24269 | 0.0009158 | 94 | 24910 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-1394-K | Weavers | Network | WEACB2 | 17/04/2025 | 09:45 | 17/04/2025 | 10:10 | 0.059351 | 0.0028448 | 292 | 6092 | Unplanned interruptions on the network | Adverse weather | High wind lne break
|  | INCD-33-L | Weavers | Network | WEACB3 | 17/04/2025 | 14:06 | 17/04/2025 | 21:30 | 0.0043257 | 9.7e-06 | 1 | 444 | Unplanned interruptions on the network | Defective Equipment | Intnl insulation failure
|  | INCD-16-M | Raglan | Network | NGACB2 | 18/04/2025 | 14:51 | 18/04/2025 | 23:45 | 0.011043 | 0.000682 | 70 | 1133.45 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-16-M | Raglan | Network | RAGCB2 | 18/04/2025 | 14:51 | 18/04/2025 | 23:45 | 0.18306 | 0.015276 | 1568 | 18790 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-24-M | Horotiu | Network | KOHCB6 | 24/04/2025 | 09:12 | 24/04/2025 | 13:33 | 0.012714 | 4.87e-05 | 5 | 1305 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-1744-K | Weavers | Network | NGACB2 | 26/04/2025 | 16:02 | 26/04/2025 | 16:44 | 0.25441 | 0.0061475 | 631 | 26113 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-1796-K | Te Kauwhata | Network | TEKCB5 | 28/04/2025 | 07:43 | 28/04/2025 | 10:36 | 0.0067418 | 3.9e-05 | 4 | 692 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-1874-K | Transpower Hamilton | Network | HAMCB2802 | 30/04/2025 | 08:41 | 30/04/2025 | 19:03 | 0.26619 | 0.0004384 | 45 | 27323 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2091-K | Horotiu | Network | KOHCB6 | 05/05/2025 | 20:22 | 06/05/2025 | 01:49 | 0.13102 | 0.0009255 | 95 | 13448 | Unplanned interruptions on the network | Defective Equipment | Mechanism seized
|  | INCD-2242-K | Te Kauwhata | Network | HPTCB5 | 08/05/2025 | 17:01 | 08/05/2025 | 19:01 | 0.0058455 | 4.87e-05 | 5 | 600 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2284-K | Ngaruawahia | Network | NGACB2 | 09/05/2025 | 22:27 | 09/05/2025 | 23:43 | 0.16837 | 0.0061475 | 631 | 17282 | Unplanned interruptions on the network | Vegetation | Tree blown ovr on line (OUT of Zone)
|  | INCD-2352-K | Peacockes Rd | Network | PEACB12 | 09/05/2025 | 22:57 | 09/05/2025 | 23:19 | 0.013464 | 0.0006138 | 63 | 1382 | Unplanned interruptions on the network | Defective Equipment | Wear or shear of pins
|  | INCD-2347-K | Peacockes | Network | PEACB12 | 12/05/2025 | 09:20 | 12/05/2025 | 11:34 | 0.0039165 | 2.92e-05 | 3 | 402 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2300-K | Te Kauwhata | Network | HPTCB5 | 10/05/2025 | 10:48 | 10/05/2025 | 12:29 | 0.001968 | 1.95e-05 | 2 | 202 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2486-K | Weavers | Network | WEACB6 | 15/05/2025 | 08:51 | 15/05/2025 | 18:44 | 1.4798 | 0.0028546 | 293 | 151895 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2695-K | Gordonton | Network | GORCB13 | 21/05/2025 | 09:10 | 21/05/2025 | 14:25 | 0.012276 | 3.9e-05 | 4 | 1260 | Planned interruptions on the network | Planned | Distribution Transformer Replacement
|  | INCD-2825-K | Te Uku | Network | TEUCB11 | 24/05/2025 | 02:48 | 24/05/2025 | 03:57 | 0.01551 | 0.0002241 | 23 | 1592 | Unplanned interruptions on the network | Defective Equipment | Line break at twist joint
|  | INCD-2988-K | Peacockes | Network | PEACB14 | 29/05/2025 | 08:38 | 29/05/2025 | 16:05 | 0.21774 | 0.0004871 | 50 | 22350 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-3021-K | Sandwich Rd | Private | SANCB2 | 29/05/2025 | 14:51 | 29/05/2025 | 16:02 | 0.042887 | 0.000604 | 62 | 4402 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-3037-K | Te Uku | Network | TEUCB11 | 29/05/2025 | 18:53 | 30/05/2025 | 10:34 | 0.21301 | 0.0010717 | 110 | 21864 | Unplanned interruptions on the network | Adverse weather | High wind lne break
|  | INCD-3132-K | Gordonton | Network | GORCB11 | 31/05/2025 | 13:59 | 31/05/2025 | 15:13 | 0.0021628 | 2.92e-05 | 3 | 222 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-3568-K | Pukete | Network | TASCB4 | 12/06/2025 | 09:04 | 12/06/2025 | 11:54 | 0.068003 | 0.0008184 | 84 | 6980 | Planned interruptions on the network | Planned | Distribution Transformer Replacement
|  | INCD-3598-K | Claudelands | Network | CLACB13 | 12/06/2025 | 18:09 | 12/06/2025 | 18:58 | 0.046647 | 0.0022213 | 228 | 4788 | Unplanned interruptions on the network | Defective Equipment | Fuse blown on overload
|  | INCD-3755-K | Bryce St | Network | BRYCB12 | 17/06/2025 | 09:13 | 17/06/2025 | 09:13 | 0.0049784 | 9.7e-06 | 1 | 511 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-145-M | Whatawhata | Network | WHACB2 | 23/06/2025 | 08:00 | 23/06/2025 | 08:24 | 0.002572 | 0.0001072 | 11 | 264 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-137-M | Hampton Downs | Network | HPTCB5 | 24/06/2025 | 08:03 | 24/06/2025 | 16:06 | 0.80888 | 0.0017829 | 183 | 83026 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-3943-K | Glasgow | Network | GLACB1 | 26/06/2025 | 08:40 | 26/06/2025 | 12:28 | 0.0044426 | 1.95e-05 | 2 | 456 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-96-M | Peacockes | Network | PEACB12 | 27/06/2025 | 08:32 | 27/06/2025 | 13:35 | 0.053136 | 0.0001754 | 18 | 5454 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-4021-K | Whatawhata | Network | WHACB4 | 29/06/2025 | 08:00 | 29/06/2025 | 12:16 | 0.26707 | 0.0010424 | 107 | 27413 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-4-N | Finlayson | Network | FINCB1 | 30/06/2025 | 10:41 | 30/06/2025 | 12:32 | 0.0010717 | 1.95e-05 | 2 | 110 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-4084-K | Te Uku Wind Farm | Network | RAGCB2 | 02/07/2025 | 00:34 | 02/07/2025 | 00:46 | 0.096353 | 0.0076674 | 787 | 9889.95 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-4084-K | Te Uku Wind Farm | Network | TEUCB12 | 02/07/2025 | 00:34 | 02/07/2025 | 00:46 | 0.033424 | 0.0026597 | 273 | 3430.69 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-4088-K | Latham Court | Network | LATCB1 | 02/07/2025 | 09:05 | 02/07/2025 | 10:42 | 0.13673 | 0.0015783 | 162 | 14034 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-4219-K | Whatawhata | Network | WALCB6 | 06/07/2025 | 13:34 | 06/07/2025 | 20:34 | 0.024551 | 5.85e-05 | 6 | 2520 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-158-M | Glasgow | Network | GLACB2 | 10/07/2025 | 10:08 | 10/07/2025 | 16:42 | 0.036827 | 9.74e-05 | 10 | 3780 | Planned interruptions on the network | Planned | Distribution Transformer Replacement
|  | INCD-248-M | Latham | Network | LATCB1 | 16/07/2025 | 09:02 | 16/07/2025 | 09:49 | 0.036632 | 0.0007794 | 80 | 3760 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-4529-K | Te Kauwhata | Network | TEKCB5 | 14/07/2025 | 08:04 | 14/07/2025 | 11:58 | 0.009119 | 3.9e-05 | 4 | 936 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-4756-K | Weavers | Network | WEACB3 | 19/07/2025 | 14:49 | 19/07/2025 | 16:25 | 0.018667 | 0.0001949 | 20 | 1916 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-4929-K | Weavers | Network | WEACB6 | 24/07/2025 | 07:17 | 24/07/2025 | 16:50 | 0.097916 | 0.0056896 | 584 | 10050.4 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-462-L | Horotiu | Network | HORCB5 | 30/07/2025 | 15:30 | 31/07/2025 | 13:58 | 0.013133 | 9.7e-06 | 1 | 1348 | Unplanned interruptions on the network | Defective Equipment | Faulty joint/connection
|  | INCD-223-M | Silverdale | Network | SILCB4 | 01/08/2025 | 09:16 | 01/08/2025 | 15:53 | 0.019339 | 4.87e-05 | 5 | 1985 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-5341-K | Te Kauwhata | Network | TEKCB5 | 04/08/2025 | 09:08 | 04/08/2025 | 11:37 | 0.0014516 | 9.7e-06 | 1 | 149 | Unplanned interruptions on the network | Defective Equipment | Conduct worn on insulr
|  | INCD-5412-K | Whatawhata | Network | WHACB5 | 06/08/2025 | 04:57 | 06/08/2025 | 06:46 | 0.032803 | 0.000302 | 31 | 3367 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-5499-K | Latham Court | Network | LATCB5 | 08/08/2025 | 08:12 | 08/08/2025 | 11:05 | 0.45855 | 0.014507 | 1489 | 47067 | Unplanned interruptions on the network | Defective Equipment | faulty line connection
|  | INCD-516-L | Latham Court | Network | LATCB5 | 08/08/2025 | 13:40 | 08/08/2025 | 17:17 | 0.07188 | 0.0003312 | 34 | 7378 | Unplanned interruptions on the network | Defective Equipment | Contact problem
|  | INCD-242-M | Te Kauwhata | Network | TEKCB6 | 11/08/2025 | 09:15 | 11/08/2025 | 11:25 | 0.0088657 | 6.82e-05 | 7 | 910 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-5664-K | Te Kauwhata | Network | TEKCB5 | 12/08/2025 | 09:58 | 12/08/2025 | 12:48 | 0.0049687 | 2.92e-05 | 3 | 510 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-517-L | Transpower Hamilton | Network | HAMCB2722 | 13/08/2025 | 01:41 | 13/08/2025 | 01:51 | 0.0057481 | 0.0005748 | 59 | 590 | Unplanned interruptions on the network | Defective Equipment | Fuse blown on overload
|  | INCD-5754-K | Te Kauwhata | Network | TEKCB3 | 14/08/2025 | 09:49 | 14/08/2025 | 12:21 | 0.011847 | 7.79e-05 | 8 | 1216 | Planned interruptions on the network | Planned | 11kV Fuse Replacement
|  | INCD-523-L | Peacockes Rd | Network | PEACB12 | 18/08/2025 | 00:22 | 18/08/2025 | 00:41 | 0.054385 | 0.0028351 | 291 | 5582.26 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-250-M | Finalyson | Network | FINCB1 | 19/08/2025 | 09:11 | 19/08/2025 | 13:45 | 0.010678 | 3.9e-05 | 4 | 1096 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-5969-K | Horotiu | Network | GORCB11 | 19/08/2025 | 20:17 | 19/08/2025 | 20:52 | 0.14818 | 0.0056409 | 579 | 15210.02 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-6166-K | Transpower Hamilton | Network | HAMCB2762 | 25/08/2025 | 09:13 | 25/08/2025 | 10:32 | 0.052337 | 0.0006625 | 68 | 5372 | Planned interruptions on the network | Planned | New Connections
|  | INCD-261-M | Tasman | Network | TASCB3 | 30/08/2025 | 08:03 | 30/08/2025 | 10:17 | 0.0013055 | 9.7e-06 | 1 | 134 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-6494-K | Horotiu | Network | KOHCB6 | 01/09/2025 | 12:05 | 01/09/2025 | 15:53 | 0.091424 | 0.0004774 | 49 | 9384 | Unplanned interruptions on the network | Defective Equipment | Broken binder
|  | INCD-6628-K | Sandwich Rd | Network | SANCB5 | 03/09/2025 | 15:03 | 03/09/2025 | 23:00 | 0.5504 | 0.0018511 | 190 | 56495 | Unplanned interruptions on the network | Third_party | Hit by car
|  | INCD-287-M | Transpower Hamilton | Network | HAMCB2762 | 08/09/2025 | 09:01 | 08/09/2025 | 12:12 | 0.23823 | 0.0013542 | 139 | 24453 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-6883-K | Kent St | Network | KENCB6 | 09/09/2025 | 09:15 | 09/09/2025 | 09:33 | 0.012756 | 0.0007989 | 82 | 1309.3 | Unplanned interruptions on the network | Defective Equipment | Cable joint fails
|  | INCD-6883-K | Kent St | Network | KENCB7 | 09/09/2025 | 09:15 | 09/09/2025 | 09:33 | 0.025045 | 0.0015685 | 161 | 2570.7 | Unplanned interruptions on the network | Defective Equipment | Cable joint fails
|  | INCD-6883-K | Kent St | Network | NORCB1 | 09/09/2025 | 09:15 | 09/09/2025 | 09:33 | 0.13331 | 0.0075602 | 776 | 13683.39 | Unplanned interruptions on the network | Defective Equipment | Cable joint fails
|  | INCD-6883-K | Kent St | Network | NORCB3 | 09/09/2025 | 09:15 | 09/09/2025 | 09:33 | 0.018038 | 0.001023 | 105 | 1851.49 | Unplanned interruptions on the network | Defective Equipment | Cable joint fails
|  | INCD-6897-K | Finlayson Rd | Network | FINCB1 | 09/09/2025 | 12:55 | 09/09/2025 | 23:13 | 0.094015 | 0.0003702 | 38 | 9650 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-7108-K | Whatawhata | Network | WHACB6 | 13/09/2025 | 15:23 | 14/09/2025 | 02:05 | 0.27118 | 0.000604 | 62 | 27835 | Unplanned interruptions on the network | Vegetation | Tree blown ovr on line (IN Zone)
|  | INCD-7152-K | Hoeka | Network | HOECB6 | 15/09/2025 | 08:24 | 15/09/2025 | 16:38 | 0.5407 | 0.0058455 | 600 | 55499 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-7194-K | Whatawhata | Network | WHACB4 | 16/09/2025 | 03:26 | 16/09/2025 | 04:43 | 0.06885 | 0.0018316 | 188 | 7067 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (IN Zone)
|  | INCD-7236-K | Claudelands | Network | CLACB3 | 16/09/2025 | 15:04 | 16/09/2025 | 15:19 | 0.017244 | 0.0011496 | 118 | 1770 | Unplanned interruptions on the network | Third_party | Cable isolated - safety reasons
|  | INCD-7257-K | Ngaruawahia | Network | NGACB5 | 17/09/2025 | 08:45 | 17/09/2025 | 19:40 | 0.02005 | 2.92e-05 | 3 | 2058 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-294-M | Chartwell | Network | CHACB9 | 17/09/2025 | 09:09 | 17/09/2025 | 12:13 | 0.010756 | 5.85e-05 | 6 | 1104 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-309-M | Wallace | Network | WALCB4 | 19/09/2025 | 05:27 | 19/09/2025 | 19:59 | 0.012276 | 0.0003897 | 40 | 1260 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-7675-K | Te Kauwhata | Network | TEKCB5 | 28/09/2025 | 08:55 | 28/09/2025 | 10:55 | 0.0011691 | 9.7e-06 | 1 | 120 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-3063-E | Weavers | Network | WEACB6 | 29/09/2025 | 08:39 | 29/09/2025 | 10:49 | 0.010132 | 7.79e-05 | 8 | 1040 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-7729-K | Finlayson Rd | Network | FINCB2 | 29/09/2025 | 20:06 | 30/09/2025 | 11:58 | 0.18962 | 0.012373 | 1270 | 19463 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-7790-K | Horotiu | Network | HORCB6 | 01/10/2025 | 10:10 | 01/10/2025 | 17:29 | 2.2566 | 0.0054266 | 557 | 231627 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-7807-K | Gordonton | Network | GORCB12 | 02/10/2025 | 07:15 | 02/10/2025 | 12:44 | 0.12221 | 0.0007209 | 74 | 12544 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-8001-K | Horotiu | Network | HORCB6 | 02/10/2025 | 18:59 | 02/10/2025 | 19:37 | 0.0003702 | 9.7e-06 | 1 | 38 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-7919-K | Kent St | Private | KENCB2 | 04/10/2025 | 07:14 | 04/10/2025 | 08:42 | 0.034294 | 0.0003897 | 40 | 3520 | Unplanned interruptions on the network | Third_party | Temp Disconnect / safety isolation
|  | INCD-8041-K | Weavers | Network | WEACB2 | 07/10/2025 | 09:49 | 07/10/2025 | 19:27 | 0.050641 | 8.77e-05 | 9 | 5198 | Unplanned interruptions on the network | Defective Equipment | Faulty joint/connection
|  | INCD-343-M | Transpower Hamilton | Network | HAMCB2762 | 08/10/2025 | 09:09 | 08/10/2025 | 15:59 | 0.27162 | 0.0006625 | 68 | 27880 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-305-M | Horotiu | Network | HORCB3 | 08/10/2025 | 09:14 | 08/10/2025 | 16:06 | 0.12215 | 0.0003118 | 32 | 12538 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-8095-K | Transpower Hamilton | Network | CLACB16 | 09/10/2025 | 07:12 | 09/10/2025 | 11:29 | 0.17981 | 0.0007015 | 72 | 18456.05 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-8147-K | Te Uku | Network | TEUCB13 | 11/10/2025 | 09:59 | 11/10/2025 | 17:18 | 0.004277 | 9.7e-06 | 1 | 439 | Unplanned interruptions on the network | Defective Equipment | Intnl insulation failure
|  | INCD-8174-K | Hoeka | Network | HOECB6 | 13/10/2025 | 13:43 | 13/10/2025 | 17:54 | 0.89714 | 0.0065275 | 670 | 92085 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-8231-K | Raglan | Network | RAGCB2 | 15/10/2025 | 09:51 | 15/10/2025 | 17:58 | 0.2788 | 0.0020654 | 212 | 28617 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-8232-K | Peacockes | Private | PEACB12 | 15/10/2025 | 11:38 | 15/10/2025 | 11:55 | 0.0003312 | 1.95e-05 | 2 | 34 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-8264-K | Weavers | Network | WEACB6 | 17/10/2025 | 06:34 | 17/10/2025 | 11:22 | 0.067311 | 0.0002338 | 24 | 6909 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-348-M | Finlayson | Network | FINCB2 | 17/10/2025 | 09:45 | 17/10/2025 | 12:30 | 0.0048225 | 2.92e-05 | 3 | 495 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-8300-K | Transpower Hamilton | Network | HAMCB2802 | 19/10/2025 | 03:24 | 19/10/2025 | 04:48 | 0.0016367 | 1.95e-05 | 2 | 168 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-8359-K | Weavers | Network | WEACB6 | 21/10/2025 | 18:55 | 21/10/2025 | 19:52 | 0.0011106 | 1.95e-05 | 2 | 114 | Unplanned interruptions on the network | Adverse weather | Line clash high wind
|  | INCD-375-M | Wallace | Network | WALCB6 | 22/10/2025 | 09:25 | 22/10/2025 | 14:34 | 0.28114 | 0.0009353 | 96 | 28857 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-8369-K | Te Kauwhata | Network | TEKCB5 | 22/10/2025 | 11:33 | 22/10/2025 | 12:52 | 0.095223 | 0.0015685 | 161 | 9774 | Unplanned interruptions on the network | Defective Equipment | Cable termination fails
|  | INCD-8459-K | Horotiu | Network | HORCB3 | 28/10/2025 | 07:04 | 28/10/2025 | 16:24 | 0.031478 | 0.0001851 | 19 | 3231 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-383-M | Borman | Network | BORCB3 | 28/10/2025 | 09:13 | 28/10/2025 | 12:18 | 0.11896 | 0.000643 | 66 | 12210 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-8476-K | Te Uku | Network | TEUCB11 | 28/10/2025 | 07:50 | 28/10/2025 | 14:04 | 0.014575 | 3.9e-05 | 4 | 1496 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-386-M | Finlayson | Network | FINCB2 | 29/10/2025 | 09:13 | 29/10/2025 | 15:00 | 0.030192 | 8.77e-05 | 9 | 3099 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-385-M | Chartwell | Network | CHACB9 | 31/10/2025 | 09:04 | 31/10/2025 | 15:08 | 0.13651 | 0.00038 | 39 | 14012 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-389-M | Glasgow | Network | GLACB6 | 02/11/2025 | 08:09 | 02/11/2025 | 13:42 | 0.049648 | 0.0010132 | 104 | 5096 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-1338-L | Horotiu | Network | HORCB5 | 05/11/2025 | 05:35 | 05/11/2025 | 12:26 | 0.13365 | 0.0003507 | 36 | 13718 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-8675-K | Peacockes | Private | PEACB12 | 05/11/2025 | 08:51 | 05/11/2025 | 10:24 | 0.012685 | 0.0001364 | 14 | 1302 | Unplanned interruptions on the network | Third_party | Part power
|  | INCD-1403-L | Te Kauwhata | Network | TEKCB5 | 09/11/2025 | 09:22 | 09/11/2025 | 12:30 | 0.0054948 | 2.92e-05 | 3 | 564 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-8781-K | Weavers | Network | NGACB2 | 11/11/2025 | 07:37 | 11/11/2025 | 07:45 | 0.045053 | 0.0064983 | 667 | 4624.36 | Unplanned interruptions on the network | Wildlife | Bird betw line & pole
|  | INCD-140-N | Weavers | Network | WEACB3 | 13/11/2025 | 09:37 | 13/11/2025 | 13:39 | 0.1484 | 0.0006917 | 71 | 15232 | Planned interruptions on the network | Planned | New Connections
|  | INCD-8888-K | Gordonton | Network | GORCB11 | 13/11/2025 | 20:37 | 13/11/2025 | 23:23 | 0.0048518 | 2.92e-05 | 3 | 498 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-401-M | Chartwell | Network | CHACB9 | 14/11/2025 | 09:05 | 14/11/2025 | 15:52 | 0.20968 | 0.0005553 | 57 | 21522 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-8959-K | Gordonton | Network | GORCB11 | 16/11/2025 | 11:39 | 16/11/2025 | 18:11 | 0.025058 | 0.0002046 | 21 | 2572 | Unplanned interruptions on the network | Defective Equipment | Mechanism seized
|  | INCD-9087-K | Glasgow St | Network | GLACB2 | 19/11/2025 | 14:14 | 19/11/2025 | 16:41 | 0.0028643 | 1.95e-05 | 2 | 294 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-9178-K | Gordonton | Network | GORCB11 | 22/11/2025 | 09:14 | 22/11/2025 | 09:38 | 0.0021044 | 8.77e-05 | 9 | 216 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-404-M | Latham | Network | LATCB1 | 22/11/2025 | 18:03 | 22/11/2025 | 20:03 | 0.0023382 | 1.95e-05 | 2 | 240 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-9217-K | Pukete | Network | PUKCB2 | 24/11/2025 | 09:07 | 24/11/2025 | 10:57 | 0.0064301 | 5.85e-05 | 6 | 660 | Unplanned interruptions on the network | Defective Equipment | Cond not fully in sleeve
|  | INCD-9274-K | Peacockes Rd | Private | PEACB17 | 27/11/2025 | 22:03 | 27/11/2025 | 22:16 | 0.0026597 | 0.0002046 | 21 | 273 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-419-M | Glasgow | Network | GLACB2 | 28/11/2025 | 10:08 | 28/11/2025 | 13:16 | 0.010989 | 5.85e-05 | 6 | 1128 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-466-M | Gordonton | Network | GORCB13 | 08/12/2025 | 09:41 | 08/12/2025 | 15:32 | 0.017098 | 4.87e-05 | 5 | 1755 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-8769-K | Peacockes | Network | PEACB17 | 10/12/2025 | 09:00 | 10/12/2025 | 15:17 | 0.1105 | 0.0041698 | 428 | 11342 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-9707-K | Hoeka | Private | HOECB6 | 13/12/2025 | 11:29 | 13/12/2025 | 11:53 | 0.0021044 | 8.77e-05 | 9 | 216 | Unplanned interruptions on the network | Third_party | Temp Disconnect / safety isolation
|  | INCD-9787-K | Weavers | Network | WEACB6 | 16/12/2025 | 18:31 | 16/12/2025 | 19:52 | 0.1634 | 0.0025428 | 261 | 16772 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-1663-L | Hoeka | Network | HOECB6 | 18/12/2025 | 11:31 | 18/12/2025 | 17:39 | 0.039438 | 0.0001072 | 11 | 4048 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-9922-K | Whatawhata | Private | WHACB5 | 19/12/2025 | 09:42 | 19/12/2025 | 09:53 | 0.0008573 | 7.79e-05 | 8 | 88 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-9949-K | Weavers | Network | WEACB6 | 19/12/2025 | 23:29 | 20/12/2025 | 13:54 | 1.7815 | 0.004579 | 470 | 182857 | Unplanned interruptions on the network | Defective Equipment | Insulator split
|  | INCD-9979-K | Finlayson | Network | FINCB4 | 22/12/2025 | 08:00 | 22/12/2025 | 11:50 | 0.0022408 | 9.7e-06 | 1 | 230 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-10103-K | Te Uku | Network | TEUCB11 | 29/12/2025 | 15:32 | 30/12/2025 | 01:31 | 0.45237 | 0.0093333 | 958 | 46433 | Unplanned interruptions on the network | Adverse weather | Line clash high wind
|  | INCD-10169-K | Te Uku | Network | TEUCB11 | 30/12/2025 | 06:25 | 31/12/2025 | 15:41 | 0.21542 | 0.0052512 | 539 | 22111 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-10299-K | Avalon Dr | Network | AVACB6 | 01/01/2026 | 11:04 | 01/01/2026 | 11:54 | 0.018511 | 0.0003702 | 38 | 1900 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-10297-K | Avalon Dr | Network | AVACB6 | 01/01/2026 | 11:04 | 01/01/2026 | 11:54 | 0.026792 | 0.0005358 | 55 | 2750 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-10302-K | MAF | Network | MAFCB3 | 02/01/2026 | 17:27 | 02/01/2026 | 17:32 | 4.87e-05 | 9.7e-06 | 1 | 5 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-519-M | Finlayson | Network | FINCB2 | 08/01/2026 | 09:17 | 08/01/2026 | 13:18 | 0.0023479 | 9.7e-06 | 1 | 241 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-10690-K | Latham Court | Network | LATCB1 | 15/01/2026 | 22:36 | 16/01/2026 | 05:32 | 0.56335 | 0.0013542 | 139 | 57824 | Unplanned interruptions on the network | Defective Equipment | Loss or failure of oil
|  | INCD-10812-K | Te Kauwhata | Network | TEKCB3 | 19/01/2026 | 22:01 | 19/01/2026 | 22:17 | 0.025316 | 0.015822 | 1624 | 2598.56 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (OUT of Zone)
|  | INCD-10946-K | Finlayson Rd | Network | FINCB2 | 21/01/2026 | 22:30 | 22/01/2026 | 01:01 | 0.13799 | 0.0043452 | 446 | 14164 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (OUT of Zone)
|  | INCD-1768-L | Te Kauwhata | Network | TEKCB2 | 24/01/2026 | 08:23 | 24/01/2026 | 09:57 | 0.078427 | 0.0008281 | 85 | 8050 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-541-M | Finlayson | Network | FINCB4 | 28/01/2026 | 08:31 | 28/01/2026 | 12:32 | 0.014088 | 5.85e-05 | 6 | 1446 | Planned interruptions on the network | Planned | New Connections
|  | INCD-11366-K | Glasgow St | Network | GLACB7 | 01/02/2026 | 08:00 | 01/02/2026 | 14:51 | 0.35195 | 0.0008573 | 88 | 36125 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-11389-K | Finlayson Rd | Network | FINCB2 | 02/02/2026 | 09:16 | 03/02/2026 | 13:19 | 0.016397 | 9.7e-06 | 1 | 1683 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-579-M | Whatawhata | Network | WHACB6 | 02/02/2026 | 09:18 | 02/02/2026 | 12:09 | 0.038317 | 0.0002241 | 23 | 3933 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-11423-K | Weavers | Network | WEACB6 | 03/02/2026 | 09:32 | 03/02/2026 | 16:56 | 0.55332 | 0.0013347 | 137 | 56794 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-11460-K | Whatawhata | Private | WHACB3 | 04/02/2026 | 11:43 | 04/02/2026 | 11:52 | 0.0007891 | 8.77e-05 | 9 | 81 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-11521-K | Raglan | Network | RAGCB3 | 06/02/2026 | 09:56 | 06/02/2026 | 10:17 | 0.015081 | 0.0007307 | 75 | 1548 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-586-M | Te Uku | Network | TEUCB13 | 10/02/2026 | 09:31 | 10/02/2026 | 15:43 | 0.14503 | 0.0003897 | 40 | 14886 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-11670-K | Sandwich Rd | Network | SANCB2 | 12/02/2026 | 07:02 | 12/02/2026 | 09:42 | 0.22758 | 0.0020557 | 211 | 23360 | Planned interruptions on the network | Planned | New Connections
|  | INCD-11730-K | Whatawhata | Network | WHACB4 | 13/02/2026 | 17:14 | 13/02/2026 | 23:22 | 0.022096 | 9.74e-05 | 10 | 2268 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-621-M | Peacockes | Network | PEACB11 | 15/02/2026 | 08:08 | 15/02/2026 | 17:11 | 0.0052902 | 9.7e-06 | 1 | 543 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-630-M | Sandwich | Network | SANCB2 | 15/02/2026 | 13:05 | 15/02/2026 | 13:43 | 0.022953 | 0.000604 | 62 | 2356 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-11807-K | Whitiora School | Network | WHICB4 | 17/02/2026 | 08:31 | 17/02/2026 | 15:38 | 0.77377 | 0.0018121 | 186 | 79422 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-12067-K | Latham Court | Network | LATCB3 | 25/02/2026 | 18:48 | 25/02/2026 | 19:45 | 0.47668 | 0.0088657 | 910 | 48928 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-12067-K | Latham Court | Network | WALCB4 | 25/02/2026 | 18:48 | 25/02/2026 | 19:45 | 0.12255 | 0.0064106 | 658 | 12579 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-12067-K | Latham Court | Network | WALCB6 | 25/02/2026 | 18:48 | 25/02/2026 | 19:45 | 0.19152 | 0.012383 | 1271 | 19658 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-12157-K | Silverdale | Network | SILCB5 | 03/03/2026 | 09:02 | 03/03/2026 | 17:41 | 1.0507 | 0.0026597 | 273 | 107849 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-12157-K | Silverdale | Network | HAMCB2862 | 03/03/2026 | 09:02 | 03/03/2026 | 17:41 | 0.15319 | 0.0016757 | 172 | 15724 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-649-M | Glasgow | Network | GLACB6 | 04/03/2026 | 08:35 | 04/03/2026 | 10:20 | 0.18802 | 0.0017829 | 183 | 19299 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-1913-L | Finlayson Rd | Network | FINCB2 | 04/03/2026 | 09:10 | 04/03/2026 | 11:20 | 0.0050661 | 3.9e-05 | 4 | 520 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-12236-K | Chartwell | Network | CHACB9 | 06/03/2026 | 09:43 | 06/03/2026 | 12:12 | 0.10708 | 0.0007209 | 74 | 10991 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-12241-K | Wallace Rd | Network | WALCB3 | 06/03/2026 | 15:51 | 06/03/2026 | 15:51 | 0.0027448 | 0.0065859 | 676 | 281.73 | Unplanned interruptions on the network | Human error | Unintentionally Disabled
|  | INCD-12272-K | Transpower Hamilton | Network | BORCB7 | 09/03/2026 | 06:33 | 09/03/2026 | 07:44 | 0.85241 | 0.013464 | 1382 | 87494 | Unplanned interruptions on the network | Defective Equipment | Loose connection
|  | INCD-269-N | Weavers | Network | WEACB5 | 09/03/2026 | 08:39 | 09/03/2026 | 14:54 | 0.021453 | 5.85e-05 | 6 | 2202 | Planned interruptions on the network | Planned | Transformer Upgrade
|  | INCD-12437-K | Silverdale | Network | SILCB5 | 16/03/2026 | 09:07 | 16/03/2026 | 15:25 | 0.51388 | 0.0015296 | 157 | 52746 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-626-M | Kent | Network | KENCB2 | 17/03/2026 | 00:12 | 17/03/2026 | 00:39 | 0.010522 | 0.0003897 | 40 | 1080 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-665-M | Wallace | Network | WALCB6 | 17/03/2026 | 15:37 | 17/03/2026 | 17:24 | 0.009382 | 8.77e-05 | 9 | 963 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-12577-K | Weavers | Network | WEACB6 | 21/03/2026 | 11:40 | 21/03/2026 | 13:40 | 0.0035073 | 2.92e-05 | 3 | 360 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-12462-K | Bryce St | Network | BRYCB6 | 18/03/2026 | 06:11 | 18/03/2026 | 07:31 | 0.031196 | 0.0021531 | 221 | 3202 | Unplanned interruptions on the network | Defective Equipment | Cable joint fails
|  | INCD-12467-K | Latham | Network | LATCB2 | 18/03/2026 | 09:12 | 18/03/2026 | 14:52 | 0.33414 | 0.000984 | 101 | 34297 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-12513-K | Hoeka | Network | HOECB3 | 20/03/2026 | 08:30 | 20/03/2026 | 16:56 | 0.60918 | 0.0013055 | 134 | 62528 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2245-L | Finlayson Rd | Network | FINCB3 | 20/03/2026 | 07:36 | 20/03/2026 | 09:56 | 0.0040919 | 2.92e-05 | 3 | 420 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-1825-L | Peacockes | Network | PEACB16 | 21/03/2026 | 09:00 | 21/03/2026 | 15:40 | 0.014731 | 0.0021044 | 216 | 1512 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-12608-K | Avalon Dr | Network | AVACB1 | 23/03/2026 | 05:06 | 23/03/2026 | 05:32 | 0.017731 | 0.000682 | 70 | 1820 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-675-M | Te Kauwhata | Network | TEKCB5 | 25/03/2026 | 09:06 | 25/03/2026 | 14:01 | 0.069815 | 0.0002533 | 26 | 7166 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2376-L | Weavers | Network | WEACB6 | 25/03/2026 | 11:49 | 25/03/2026 | 14:09 | 0.014351 | 0.0001169 | 12 | 1473 | Unplanned interruptions on the network | Defective Equipment | Nut or bolt loose
|  | INCD-12686-K | Te Uku | Network | TEUCB11 | 26/03/2026 | 17:03 | 27/03/2026 | 13:39 | 0.37467 | 0.0042964 | 441 | 38457 | Unplanned interruptions on the network | Defective Equipment | Split crossarm
|  | INCD-12691-K | Te Uku | Network | TEUCB12 | 26/03/2026 | 19:17 | 27/03/2026 | 03:07 | 0.018316 | 3.9e-05 | 4 | 1880 | Unplanned interruptions on the network | Defective Equipment | Intnl insulation failure
|  | INCD-12700-K | Avalon Dr | Network | AVACB1 | 27/03/2026 | 05:07 | 27/03/2026 | 05:15 | 0.0089631 | 0.0011204 | 115 | 920 | Planned interruptions on the network | Unknown | Mixed Asset Replacement
|  | INCD-12869-K | Te Uku | Network | TEUCB11 | 28/03/2026 | 09:58 | 02/04/2026 | 13:55 | 0.21735 | 2.92e-05 | 3 | 22309 | Unplanned interruptions on the network | Defective Equipment | Line break at twist joint
|  | INCD-683-M | Peacockes | Network | PEACB12 | 30/03/2026 | 12:37 | 30/03/2026 | 15:33 | 0.14575 | 0.0008281 | 85 | 14960 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-12800-K | Bryce St | Network | BRYCB12 | 30/03/2026 | 22:13 | 31/03/2026 | 05:47 | 0.094113 | 0.0008963 | 92 | 9660 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-12821-K | Transpower Hamilton | Network | HAMCB2822 | 31/03/2026 | 02:07 | 31/03/2026 | 14:19 | 0.008817 | 0.0030397 | 312 | 905 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-4-M | Transpower Hamilton | Network | HAMCB2902 | 10/04/2025 | 09:04 | 10/04/2025 | 14:58 | 0.17934 | 0.0005066 | 52 | 18408 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-1201-K | Weavers | Network | WEACB3 | 12/04/2025 | 08:22 | 12/04/2025 | 14:34 | 0.43492 | 0.0044718 | 459 | 44642 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-1375-K | Weavers | Network | WEACB4 | 17/04/2025 | 08:37 | 17/04/2025 | 14:23 | 0.0067418 | 1.95e-05 | 2 | 692 | Unplanned interruptions on the network | Vegetation | Tree known grows in line
|  | INCD-1437-K | Weavers | Network | NGACB3 | 17/04/2025 | 12:32 | 17/04/2025 | 13:10 | 0.33449 | 0.0088949 | 913 | 34333.13 | Unplanned interruptions on the network | Adverse weather | Line clash high wind
|  | INCD-1437-K | Weavers | Network | NGACB5 | 17/04/2025 | 12:32 | 17/04/2025 | 13:10 | 0.21628 | 0.0057091 | 586 | 22199.87 | Unplanned interruptions on the network | Adverse weather | Line clash high wind
|  | INCD-1477-K | Weavers | Network | WEACB4 | 17/04/2025 | 15:01 | 17/04/2025 | 15:11 | 0.019582 | 0.0020654 | 212 | 2010 | Unplanned interruptions on the network | Defective Equipment | Connect/jumper loose
|  | INCD-16-M | Raglan | Network | RAGCB5 | 18/04/2025 | 14:51 | 18/04/2025 | 23:45 | 0.037382 | 0.0030007 | 308 | 3837 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-1586-K | Weavers | Network | WEACB6 | 19/04/2025 | 03:16 | 19/04/2025 | 10:16 | 0.012276 | 2.92e-05 | 3 | 1260 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-1744-K | Weavers | Network | NGACB5 | 26/04/2025 | 16:02 | 26/04/2025 | 16:44 | 0.23484 | 0.0057091 | 586 | 24104.37 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-1745-K | Weavers | Network | WEACB5 | 26/04/2025 | 16:02 | 27/04/2025 | 02:20 | 0.49674 | 0.0085637 | 879 | 50987 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-1746-K | Weavers | Network | GLACB2 | 26/04/2025 | 16:02 | 26/04/2025 | 16:32 | 0.19152 | 0.006547 | 672 | 19658 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-1746-K | Weavers | Network | GLACB5 | 26/04/2025 | 16:02 | 26/04/2025 | 16:32 | 0.074326 | 0.0027376 | 281 | 7629 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-2058-K | Te Kauwhata | Network | TEKCB5 | 05/05/2025 | 08:36 | 05/05/2025 | 10:24 | 0.0031566 | 2.92e-05 | 3 | 324 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-2315-K | Te Kauwhata | Network | HPTCB2 | 11/05/2025 | 07:54 | 11/05/2025 | 08:59 | 0.001247 | 1.95e-05 | 2 | 128 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2315-K | Te Kauwhata | Network | HPTCB3 | 11/05/2025 | 07:54 | 11/05/2025 | 08:59 | 0.023246 | 0.0003605 | 37 | 2386 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-64-L | Wallace Rd | Private | WALCB6 | 12/05/2025 | 13:06 | 12/05/2025 | 13:32 | 0.0010132 | 3.9e-05 | 4 | 104 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-69-L | Weavers | Network | WEACB3 | 13/05/2025 | 11:16 | 13/05/2025 | 15:29 | 0.0049297 | 1.95e-05 | 2 | 506 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2622-K | Whatawhata | Network | WHACB3 | 20/05/2025 | 01:04 | 20/05/2025 | 05:24 | 0.012665 | 4.87e-05 | 5 | 1300 | Unplanned interruptions on the network | Defective Equipment | Loss or failure of oil
|  | INCD-2748-K | Whatawhata | Network | WHACB2 | 22/05/2025 | 11:45 | 22/05/2025 | 13:38 | 0.0033027 | 2.92e-05 | 3 | 339 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2788-K | Te Uku | Network | TEUCB11 | 23/05/2025 | 08:59 | 23/05/2025 | 12:49 | 0.12812 | 0.0005943 | 61 | 13151 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-78-L | Avalon Dr | Private | AVACB1 | 04/06/2025 | 12:47 | 04/06/2025 | 12:47 | 0.0089436 | 0.0003312 | 34 | 918 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-101-M | Peacockes | Network | PEACB18 | 06/06/2025 | 10:08 | 06/06/2025 | 13:02 | 0.011866 | 6.82e-05 | 7 | 1218 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-3432-K | Glasgow | Network | GLACB2 | 09/06/2025 | 18:55 | 09/06/2025 | 22:42 | 0.0022115 | 9.7e-06 | 1 | 227 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-80-M | Weavers | Network | WEACB3 | 10/06/2025 | 09:03 | 10/06/2025 | 13:02 | 0.1614 | 0.0006917 | 71 | 16567 | Planned interruptions on the network | Planned | Distribution Transformer Replacement
|  | INCD-3487-K | Transpower Hamilton | Network | HAMCB2802 | 11/06/2025 | 00:03 | 11/06/2025 | 00:07 | 0.0054655 | 0.0014906 | 153 | 561 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-122-M | Weavers | Network | WEACB6 | 12/06/2025 | 09:02 | 12/06/2025 | 14:55 | 0.02042 | 5.85e-05 | 6 | 2096 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-93-L | Weavers | Network | WEACB2 | 13/06/2025 | 09:53 | 13/06/2025 | 12:18 | 0.0014127 | 9.7e-06 | 1 | 145 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-3661-K | Wallace Rd | Network | WALCB6 | 14/06/2025 | 19:25 | 14/06/2025 | 20:55 | 0.0035073 | 3.9e-05 | 4 | 360 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-95-M | Avalon | Network | AVACB3 | 19/06/2025 | 09:05 | 19/06/2025 | 09:38 | 0.033758 | 0.001023 | 105 | 3465 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-3864-K | Gordonton | Network | GORCB11 | 19/06/2025 | 16:39 | 19/06/2025 | 22:52 | 0.15466 | 0.0007404 | 76 | 15875 | Unplanned interruptions on the network | Defective Equipment | Mechanism seized
|  | INCD-137-M | Hampton Downs | Network | HPTCB2 | 24/06/2025 | 08:03 | 24/06/2025 | 16:06 | 0.0089241 | 1.95e-05 | 2 | 916 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-3999-K | Whatawhata | Network | NGACB2 | 28/06/2025 | 00:00 | 28/06/2025 | 00:12 | 0.0039896 | 0.000341 | 35 | 409.5 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-3999-K | Whatawhata | Network | TEUCB11 | 28/06/2025 | 00:00 | 28/06/2025 | 00:12 | 0.086858 | 0.0074238 | 762 | 8915.34 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-4021-K | Whatawhata | Network | WHACB2 | 29/06/2025 | 08:00 | 29/06/2025 | 12:16 | 1.1477 | 0.0046374 | 476 | 117806 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-4084-K | Te Uku Wind Farm | Network | RAGCB5 | 02/07/2025 | 00:34 | 02/07/2025 | 00:46 | 0.018854 | 0.0015003 | 154 | 1935.26 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-138-M | Glasgow | Network | GLACB6 | 04/07/2025 | 09:07 | 04/07/2025 | 13:40 | 0.11437 | 0.0004189 | 43 | 11739 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-364-L | Te Uku | Network | TEUCB13 | 05/07/2025 | 09:45 | 05/07/2025 | 19:49 | 0.0058845 | 9.7e-06 | 1 | 604 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-4316-K | Weavers | Network | WEACB6 | 08/07/2025 | 10:11 | 08/07/2025 | 11:59 | 0.005261 | 4.87e-05 | 5 | 540 | Unplanned interruptions on the network | Defective Equipment | Intnl insulation failure
|  | INCD-388-L | Te Uku | Network | TEUCB11 | 10/07/2025 | 08:57 | 10/07/2025 | 22:07 | 0.0136 | 1.95e-05 | 2 | 1396 | Unplanned interruptions on the network | Defective Equipment | Stay wire/ line clash
|  | INCD-4433-K | Pukete | Network | TASCB4 | 11/07/2025 | 08:29 | 11/07/2025 | 08:33 | 0.012811 | 0.003215 | 330 | 1315 | Planned interruptions on the network | Planned | New Connections
|  | INCD-4499-K | Te Kauwhata | Network | TEKCB5 | 13/07/2025 | 00:33 | 13/07/2025 | 02:44 | 0.01021 | 7.79e-05 | 8 | 1048 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-4630-K | Weavers | Network | WEACB6 | 16/07/2025 | 10:01 | 16/07/2025 | 14:27 | 0.11332 | 0.0004482 | 46 | 11631 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-4648-K | Avalon Dr | Network | AVACB8 | 16/07/2025 | 23:27 | 17/07/2025 | 02:07 | 0.11619 | 0.0012665 | 130 | 11926 | Unplanned interruptions on the network | Third_party | Cable isolated- saftey reasons
|  | INCD-178-M | Weavers | Network | WEACB3 | 18/07/2025 | 10:12 | 18/07/2025 | 16:55 | 0.30333 | 0.0007599 | 78 | 31135 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-4719-K | Te Kauwhata | Network | TEKCB2 | 18/07/2025 | 11:27 | 18/07/2025 | 11:55 | 0.0002728 | 9.7e-06 | 1 | 28 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-4762-K | Glasgow St | Network | GLACB6 | 19/07/2025 | 18:14 | 19/07/2025 | 20:12 | 0.012587 | 0.0001072 | 11 | 1292 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-4844-K | Pukete | Network | PUKCB2 | 22/07/2025 | 07:38 | 22/07/2025 | 16:16 | 0.0050564 | 9.7e-06 | 1 | 519 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-4957-K | Ngaruawahia | Network | WEACB6 | 24/07/2025 | 07:32 | 24/07/2025 | 14:19 | 1.9678 | 0.010415 | 1069 | 201981.11 | Unplanned interruptions on the network | Defective Equipment | Line break at twist joint
|  | INCD-152-M | Horotiu | Network | HORCB5 | 24/07/2025 | 08:30 | 24/07/2025 | 15:32 | 0.44098 | 0.0011009 | 113 | 45264 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-201-M | Chartwell | Network | CHACB9 | 25/07/2025 | 09:00 | 25/07/2025 | 15:07 | 0.082237 | 0.0002241 | 23 | 8441 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-5079-K | Raglan | Network | RAGCB5 | 27/07/2025 | 10:46 | 27/07/2025 | 13:08 | 0.056468 | 0.0003994 | 41 | 5796 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-5148-K | Weavers | Private | WEACB2 | 28/07/2025 | 19:32 | 28/07/2025 | 20:08 | 0.0010522 | 2.92e-05 | 3 | 108 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-5215-K | Te Kauwhata | Network | TEKCB6 | 30/07/2025 | 08:10 | 30/07/2025 | 10:30 | 0.0027279 | 1.95e-05 | 2 | 280 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-269-M | Horotiu | Network | NGACB5 | 31/07/2025 | 10:00 | 31/07/2025 | 16:28 | 0.30565 | 0.0008184 | 84 | 31373 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-203-M | Horotiu | Network | KOHCB6 | 01/08/2025 | 08:37 | 01/08/2025 | 16:00 | 0.34256 | 0.000984 | 101 | 35161 | Planned interruptions on the network | Planned | New Connections
|  | INCD-205-M | Hoeka | Network | HOECB6 | 01/08/2025 | 09:40 | 01/08/2025 | 14:31 | 0.20379 | 0.0007209 | 74 | 20918 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-5386-K | Glasgow St | Network | GLACB2 | 05/08/2025 | 09:38 | 05/08/2025 | 16:05 | 0.65195 | 0.0020264 | 208 | 66918 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-216-M | Chartwell | Network | CHACB9 | 07/08/2025 | 10:03 | 07/08/2025 | 15:42 | 0.11232 | 0.000341 | 35 | 11529 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-218-M | Te Uku | Network | TEUCB12 | 07/08/2025 | 10:09 | 07/08/2025 | 19:26 | 0.27649 | 0.000643 | 66 | 28380 | Planned interruptions on the network | Planned | Distribution Transformer Replacement
|  | INCD-523-L | Peacockes Rd | Network | PEACB17 | 18/08/2025 | 00:22 | 18/08/2025 | 00:41 | 0.090081 | 0.0046959 | 482 | 9246.22 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-78-N | Claudeland | Network | CLACB3 | 18/08/2025 | 22:04 | 19/08/2025 | 05:26 | 0.011896 | 0.0007209 | 74 | 1221 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-5940-K | Horotiu | Network | HORCB6 | 19/08/2025 | 09:03 | 19/08/2025 | 13:38 | 0.13086 | 0.0004969 | 51 | 13432 | Planned interruptions on the network | Planned | Distribution Transformer Replacement
|  | INCD-225-M | Transpower Hamilton | Network | HAMCB2902 | 19/08/2025 | 09:04 | 19/08/2025 | 10:54 | 0.11555 | 0.0010717 | 110 | 11860 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-244-M | Horotiu | Network | HORCB5 | 21/08/2025 | 08:32 | 21/08/2025 | 14:37 | 0.21336 | 0.0005846 | 60 | 21900 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-235-M | Silverdale | Network | SILCB2 | 24/08/2025 | 09:16 | 24/08/2025 | 15:30 | 0.16069 | 0.0004384 | 45 | 16494 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-268-M | Finlayson | Network | FINCB2 | 26/08/2025 | 08:34 | 26/08/2025 | 14:34 | 0.022457 | 0.0012178 | 125 | 2305 | Planned interruptions on the network | Planned | New Connections
|  | INCD-260-M | Peacockes | Network | PEACB12 | 29/08/2025 | 10:00 | 29/08/2025 | 12:35 | 0.11944 | 0.0008086 | 83 | 12260 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-6576-K | Te Kauwhata | Network | TEKCB5 | 02/09/2025 | 14:56 | 02/09/2025 | 17:36 | 0.0062352 | 3.9e-05 | 4 | 640 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-6609-K | Peacockes | Network | PEACB12 | 03/09/2025 | 10:01 | 03/09/2025 | 16:18 | 0.065284 | 0.0022895 | 235 | 6701 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-285-M | Horotiu | Network | HORCB5 | 05/09/2025 | 08:56 | 05/09/2025 | 11:55 | 0.062781 | 0.0003507 | 36 | 6444 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-6796-K | Peacockes Rd | Network | PEACB12 | 07/09/2025 | 09:39 | 07/09/2025 | 17:11 | 0.2498 | 0.0008184 | 84 | 25640 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-300-M | Gordonton | Network | GORCB12 | 08/09/2025 | 09:42 | 08/09/2025 | 12:10 | 0.021628 | 0.0001461 | 15 | 2220 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-6883-K | Kent St | Network | KILCB6 | 09/09/2025 | 09:15 | 09/09/2025 | 09:33 | 0.13709 | 0.0077745 | 798 | 14071.32 | Unplanned interruptions on the network | Defective Equipment | Cable joint fails
|  | INCD-299-M | Peacockes | Network | PEACB12 | 09/09/2025 | 09:33 | 09/09/2025 | 16:15 | 0.080726 | 0.0002046 | 21 | 8286 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-6911-K | Raglan | Network | RAGCB6 | 09/09/2025 | 15:06 | 09/09/2025 | 20:54 | 0.023733 | 6.82e-05 | 7 | 2436 | Unplanned interruptions on the network | Third_party | Cable hit by digger
|  | INCD-591-L | Weavers | Network | WEACB2 | 10/09/2025 | 09:36 | 10/09/2025 | 11:41 | 0.0012178 | 9.7e-06 | 1 | 125 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-7009-K | Gordonton | Network | GORCB13 | 11/09/2025 | 18:47 | 11/09/2025 | 20:19 | 0.0008963 | 9.7e-06 | 1 | 92 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-7056-K | Gordonton | Network | GORCB13 | 12/09/2025 | 11:49 | 12/09/2025 | 20:59 | 0.0053584 | 9.7e-06 | 1 | 550 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-7136-K | Horotiu | Network | KOHCB6 | 14/09/2025 | 12:11 | 14/09/2025 | 13:41 | 0.014029 | 0.0001559 | 16 | 1440 | Unplanned interruptions on the network | Defective Equipment | Unsafe/Damaged pillar
|  | INCD-301-M | Hoeka | Network | HOECB1 | 15/09/2025 | 09:06 | 15/09/2025 | 13:01 | 0.068685 | 0.0002923 | 30 | 7050 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-7196-K | Peacockes Rd | Network | PEACB17 | 16/09/2025 | 07:13 | 16/09/2025 | 07:47 | 0.034781 | 0.001023 | 105 | 3570 | Planned interruptions on the network | Planned | Recloser & Sectionaliser replacement
|  | INCD-315-M | Glasgow | Network | GLACB6 | 16/09/2025 | 09:40 | 16/09/2025 | 16:14 | 0.14637 | 0.00038 | 39 | 15024 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-310-M | Chartwell | Network | CHACB9 | 17/09/2025 | 09:19 | 17/09/2025 | 16:07 | 0.12322 | 0.000302 | 31 | 12648 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-7290-K | Peacockes Rd | Network | PEACB16 | 17/09/2025 | 14:57 | 17/09/2025 | 19:04 | 0.09385 | 0.00038 | 39 | 9633 | Unplanned interruptions on the network | Defective Equipment | Faulty joint/connection
|  | INCD-7439-K | Glasgow St | Network | GLACB1 | 21/09/2025 | 09:43 | 21/09/2025 | 10:29 | 0.32148 | 0.0070243 | 721 | 32998 | Unplanned interruptions on the network | Third_party | Object thrown on line
|  | INCD-7506-K | Horotiu | Network | HORCB6 | 23/09/2025 | 07:27 | 23/09/2025 | 11:18 | 0.55788 | 0.0072484 | 744 | 57262 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-642-L | Steele Park | Network | STECB3 | 23/09/2025 | 08:33 | 23/09/2025 | 08:48 | 0.030543 | 0.0020362 | 209 | 3135 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-7765-K | Glasgow St | Network | GLACB2 | 24/09/2025 | 11:17 | 24/09/2025 | 11:41 | 0.0049102 | 0.0002046 | 21 | 504 | Unplanned interruptions on the network | Defective Equipment | Overheated connections
|  | INCD-7601-K | Te Uku | Network | TEUCB11 | 25/09/2025 | 07:52 | 25/09/2025 | 14:19 | 0.052736 | 0.0001364 | 14 | 5413 | Unplanned interruptions on the network | Defective Equipment | Connect/jumper loose
|  | INCD-7644-K | Gordonton | Network | GORCB12 | 26/09/2025 | 09:40 | 26/09/2025 | 15:24 | 0.11596 | 0.0007209 | 74 | 11903 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-331-M | Norton | Network | NORCB1 | 30/09/2025 | 09:13 | 30/09/2025 | 15:19 | 0.2496 | 0.000682 | 70 | 25620 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-321-M | Ngaruawahia | Network | NGACB3 | 03/10/2025 | 08:31 | 03/10/2025 | 13:37 | 0.17752 | 0.0006138 | 63 | 18221 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-7933-K | Finlayson | Network | FINCB2 | 04/10/2025 | 11:02 | 04/10/2025 | 19:57 | 0.015637 | 2.92e-05 | 3 | 1605 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-693-L | Glasgow | Network | GLACB2 | 07/10/2025 | 17:27 | 07/10/2025 | 20:26 | 0.0034878 | 1.95e-05 | 2 | 358 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (OUT of Zone)
|  | INCD-353-M | Finlayson | Network | FINCB2 | 08/10/2025 | 08:33 | 08/10/2025 | 17:02 | 0.23982 | 0.0007989 | 82 | 24616 | Planned interruptions on the network | Planned | Transformer Upgrade
|  | INCD-344-M | Hoeka | Network | HOECB6 | 09/10/2025 | 09:45 | 09/10/2025 | 13:15 | 0.014321 | 6.82e-05 | 7 | 1470 | Planned interruptions on the network | Planned | New Connections
|  | INCD-8115-K | Chartwell | Network | HAMCB2902 | 09/10/2025 | 21:55 | 09/10/2025 | 21:58 | 0.0033904 | 0.0011301 | 116 | 348 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-8163-K | Peacockes Rd | Network | PEACB12 | 13/10/2025 | 05:09 | 13/10/2025 | 12:27 | 0.0018818 | 9.7e-06 | 1 | 193.15 | Unplanned interruptions on the network | Defective Equipment | Incorr Protect setting ld
|  | INCD-8185-K | Te Kauwhata | Network | TEKCB5 | 13/10/2025 | 20:33 | 13/10/2025 | 20:52 | 0.0007404 | 3.9e-05 | 4 | 76 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-8192-K | Cobham Dr | Network | COBCB12 | 14/10/2025 | 08:36 | 14/10/2025 | 09:59 | 0.045361 | 0.0004579 | 47 | 4656 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-8198-K | Raglan | Network | RAGCB2 | 14/10/2025 | 09:36 | 14/10/2025 | 10:10 | 0.022193 | 0.0006527 | 67 | 2278 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-8222-K | Glasgow St | Network | GLACB2 | 15/10/2025 | 07:32 | 15/10/2025 | 09:09 | 0.00189 | 1.95e-05 | 2 | 194 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-951-L | Glasgow St | Network | GLACB6 | 17/10/2025 | 07:50 | 17/10/2025 | 09:14 | 0.0090021 | 0.0001072 | 11 | 924 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-8275-K | Raglan | Network | RAGCB6 | 17/10/2025 | 09:45 | 17/10/2025 | 13:09 | 0.19029 | 0.0009353 | 96 | 19532 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-8302-K | Sandwich | Network | SANCB7 | 19/10/2025 | 08:09 | 19/10/2025 | 11:10 | 0.0017634 | 9.7e-06 | 1 | 181 | Unplanned interruptions on the network | Defective Equipment | Loss or failure of oil
|  | INCD-8342-K | Peacockes Rd | Network | PEACB16 | 21/10/2025 | 09:30 | 21/10/2025 | 15:52 | 1.0364 | 0.0028058 | 288 | 106381 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-8362-K | Te Uku | Network | TEUCB13 | 22/10/2025 | 07:21 | 22/10/2025 | 09:35 | 0.035723 | 0.0003994 | 41 | 3666.7 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-371-M | Borman | Network | BORCB7 | 24/10/2025 | 09:07 | 24/10/2025 | 11:32 | 0.026841 | 0.0001851 | 19 | 2755 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-8442-K | Whatawhata | Network | WHACB4 | 27/10/2025 | 16:24 | 27/10/2025 | 21:43 | 0.1262 | 0.0004482 | 46 | 12954 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-396-M | Transpower Hamilton | Network | HAMCB2722 | 05/11/2025 | 08:49 | 05/11/2025 | 14:18 | 0.21796 | 0.0006625 | 68 | 22372 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-8772-K | Ngaruawahia | Network | NGACB3 | 09/11/2025 | 11:12 | 09/11/2025 | 11:39 | 0.012889 | 0.0004774 | 49 | 1323 | Unplanned interruptions on the network | Defective Equipment | Cable termination fails
|  | INCD-8892-K | Whatawhata | Network | WHACB4 | 14/11/2025 | 06:49 | 14/11/2025 | 08:03 | 0.014292 | 0.0001949 | 20 | 1467 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-9008-K | Gordonton | Network | GORCB11 | 17/11/2025 | 19:54 | 17/11/2025 | 21:48 | 0.0011106 | 9.7e-06 | 1 | 114 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-9058-K | Ngaruawahia | Network | NGACB2 | 19/11/2025 | 09:07 | 19/11/2025 | 16:05 | 0.13454 | 0.0003605 | 37 | 13810 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-426-M | Horotiu | Network | HORCB6 | 20/11/2025 | 09:30 | 20/11/2025 | 14:06 | 0.12076 | 0.0004676 | 48 | 12395 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-379-M | Pukete | Network | KOHCB4 | 27/11/2025 | 08:03 | 27/11/2025 | 17:09 | 0.079791 | 0.0001461 | 15 | 8190 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-9268-K | Transpower Hamilton | Private | HAMCB2902 | 27/11/2025 | 16:06 | 27/11/2025 | 16:22 | 0.026811 | 0.0016757 | 172 | 2752 | Unplanned interruptions on the network | Third_party | Temp Disconnect / safety isolation
|  | INCD-9346-K | Weavers | Network | WEACB6 | 02/12/2025 | 18:21 | 02/12/2025 | 20:49 | 0.0028838 | 1.95e-05 | 2 | 296 | Unplanned interruptions on the network | Defective Equipment | Line break at twist joint
|  | INCD-1609-L | Weavers | Network | WEACB6 | 04/12/2025 | 09:20 | 04/12/2025 | 15:06 | 0.0067418 | 1.95e-05 | 2 | 692 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-436-M | Peacockes | Network | PEACB14 | 06/12/2025 | 08:01 | 06/12/2025 | 10:57 | 0.13032 | 0.0007404 | 76 | 13376 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-9486-K | Finlayson Rd | Network | FINCB4 | 08/12/2025 | 06:56 | 08/12/2025 | 08:16 | 0.0007697 | 9.7e-06 | 1 | 79 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-459-M | Finlayson | Network | FINCB1 | 08/12/2025 | 09:14 | 08/12/2025 | 14:39 | 0.10765 | 0.0003312 | 34 | 11050 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-462-M | Sandwich | Network | SANCB3 | 09/12/2025 | 08:33 | 09/12/2025 | 16:25 | 0.36328 | 0.0007697 | 79 | 37288 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-9637-K | Finlayson | Network | FINCB4 | 11/12/2025 | 10:14 | 11/12/2025 | 11:25 | 0.0006917 | 9.7e-06 | 1 | 71 | Planned interruptions on the network | Planned | New Connections
|  | INCD-520-M | Finlayson | Network | FINCB3 | 14/12/2025 | 09:05 | 14/12/2025 | 22:14 | 0.067603 | 8.77e-05 | 9 | 6939 | Planned interruptions on the network | Planned | New Connections
|  | INCD-520-M | Finlayson | Network | FINCB4 | 14/12/2025 | 09:05 | 14/12/2025 | 22:14 | 0.0070633 | 9.7e-06 | 1 | 725 | Planned interruptions on the network | Planned | New Connections
|  | INCD-9761-K | Glasgow St | Network | GLACB6 | 16/12/2025 | 06:56 | 16/12/2025 | 11:01 | 0.0023869 | 9.7e-06 | 1 | 245 | Unplanned interruptions on the network | Defective Equipment | Faulty joint/connection
|  | INCD-524-M | Weavers | Network | WEACB4 | 18/12/2025 | 09:33 | 18/12/2025 | 16:03 | 0.2333 | 0.0006235 | 64 | 23947 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-9872-K | Hoeka | Network | HOECB6 | 18/12/2025 | 11:50 | 18/12/2025 | 15:51 | 0.080366 | 0.0005846 | 60 | 8249 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-1513-L | Steele Park | Network | STECB3 | 19/12/2025 | 08:09 | 19/12/2025 | 13:04 | 0.25579 | 0.0008671 | 89 | 26255 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-458-M | Avalon | Network | AVACB8 | 19/12/2025 | 09:00 | 19/12/2025 | 12:41 | 0.13434 | 0.0006722 | 69 | 13789 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-9965-K | Hoeka | Network | HOECB1 | 20/12/2025 | 22:32 | 21/12/2025 | 00:20 | 0.012539 | 0.0001169 | 12 | 1287 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-10081-K | Te Kauwhata | Network | TEKCB5 | 28/12/2025 | 19:22 | 29/12/2025 | 01:13 | 0.30645 | 0.0015588 | 160 | 31455 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-566-M | Hoeka | Network | HOECB4 | 29/12/2025 | 08:36 | 29/12/2025 | 09:58 | 0.0007989 | 9.7e-06 | 1 | 82 | Planned interruptions on the network | Planned | 11kV Fuse Replacement
|  | INCD-10091-K | Finlayson Rd | Network | FINCB2 | 29/12/2025 | 13:40 | 29/12/2025 | 20:47 | 0.21997 | 0.0042867 | 440 | 22578.1 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (IN Zone)
|  | INCD-10181-K | Finlayson Rd | Network | FINCB1 | 30/12/2025 | 05:30 | 30/12/2025 | 11:12 | 0.0033319 | 9.7e-06 | 1 | 342 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-10565-K | Finlayson | Network | FINCB1 | 13/01/2026 | 12:19 | 13/01/2026 | 12:21 | 0.0052707 | 0.0022408 | 230 | 541 | Unplanned interruptions caused by another disclosing entity | Planned | CLASS G- Other Network
|  | INCD-498-M | Claudelands | Network | CLACB16 | 13/01/2026 | 22:01 | 14/01/2026 | 03:20 | 0.22365 | 0.0007015 | 72 | 22956 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-10587-K | Weavers | Network | WEACB2 | 14/01/2026 | 04:11 | 14/01/2026 | 10:49 | 0.13559 | 0.0007599 | 78 | 13917 | Unplanned interruptions on the network | Wildlife | Bird lne clash/break
|  | INCD-10680-K | Wallace Rd | Network | WALCB1 | 15/01/2026 | 13:52 | 15/01/2026 | 15:55 | 0.010912 | 0.0001559 | 16 | 1120 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (OUT of Zone)
|  | INCD-10698-K | Alexandra St | Private | ALECB15 | 16/01/2026 | 06:46 | 16/01/2026 | 12:52 | 0.0035658 | 9.7e-06 | 1 | 366 | Unplanned interruptions on the network | Third_party | Temp Disconnect / safety isolation
|  | INCD-529-M | Peacockes | Network | PEACB12 | 16/01/2026 | 09:46 | 16/01/2026 | 14:39 | 0.22412 | 0.0008184 | 84 | 23004 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-10758-K | Finlayson Rd | Private | FINCB2 | 17/01/2026 | 13:08 | 17/01/2026 | 14:46 | 0.0047738 | 4.87e-05 | 5 | 490 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-10782-K | Weavers | Network | WEACB3 | 18/01/2026 | 22:09 | 19/01/2026 | 03:28 | 0.21093 | 0.0021628 | 222 | 21650 | Unplanned interruptions on the network | Defective Equipment | Line break at twist joint
|  | INCD-10803-K | Te Kauwhata | Network | TEKCB5 | 19/01/2026 | 09:54 | 19/01/2026 | 11:46 | 0.0043646 | 3.9e-05 | 4 | 448 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-1730-L | Peacockes Rd | Network | PEACB16 | 21/01/2026 | 09:09 | 21/01/2026 | 09:19 | 0.017049 | 0.0017049 | 175 | 1750 | Planned interruptions on the network | Unknown | OTHER Maintenance
|  | INCD-10892-K | Peacockes | Network | PEACB16 | 21/01/2026 | 09:28 | 21/01/2026 | 09:45 | 0.021648 | 0.0017049 | 175 | 2222 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-10990-K | Transpower Hamilton | Network | HAMCB2802 | 22/01/2026 | 09:30 | 22/01/2026 | 11:10 | 0.010717 | 0.0001072 | 11 | 1100 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (OUT of Zone)
|  | INCD-11090-K | Foreman Rd | Network | TASCB3 | 24/01/2026 | 08:03 | 24/01/2026 | 15:34 | 0.039545 | 8.77e-05 | 9 | 4059 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-11194-K | Raglan | Network | RAGCB6 | 27/01/2026 | 10:08 | 27/01/2026 | 17:50 | 0.078593 | 0.0054266 | 557 | 8067 | Unplanned interruptions on the network | Defective Equipment | Bus chamber flashovr
|  | INCD-568-M | Weavers | Network | WEACB3 | 28/01/2026 | 09:44 | 28/01/2026 | 14:43 | 0.074413 | 0.0002533 | 26 | 7638 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-594-M | Avalon | Network | AVACB8 | 29/01/2026 | 08:33 | 29/01/2026 | 12:05 | 0.010327 | 4.87e-05 | 5 | 1060 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-536-M | Te Uku | Network | TEUCB12 | 29/01/2026 | 09:03 | 29/01/2026 | 14:16 | 0.10978 | 0.0003507 | 36 | 11268 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-11275-K | Peacockes Rd | Network | PEACB16 | 29/01/2026 | 09:23 | 29/01/2026 | 10:34 | 1.0526 | 0.018472 | 1896 | 108046 | Unplanned interruptions on the network | Lightning | Spontaneous failure
|  | INCD-11483-K | Weavers | Network | WEACB6 | 05/02/2026 | 09:30 | 05/02/2026 | 15:12 | 0.090829 | 0.0002825 | 29 | 9323 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-11543-K | Finlayson Rd | Network | FINCB2 | 08/02/2026 | 04:34 | 08/02/2026 | 07:24 | 0.0016562 | 9.7e-06 | 1 | 170 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-11556-K | Avalon Dr | Network | AVACB6 | 09/02/2026 | 08:32 | 09/02/2026 | 15:07 | 0.52588 | 0.001666 | 171 | 53978 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-273-N | Weavers | Network | WEACB2 | 13/02/2026 | 08:38 | 13/02/2026 | 10:50 | 0.001286 | 9.7e-06 | 1 | 132 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-265-N | Hampton Downs | Network | HPTCB5 | 15/02/2026 | 08:29 | 15/02/2026 | 17:24 | 1.0899 | 0.0024941 | 256 | 111872 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-595-M | Peacockes | Network | PEACB18 | 17/02/2026 | 09:05 | 17/02/2026 | 15:50 | 0.047738 | 0.0001267 | 13 | 4900 | Planned interruptions on the network | Planned | Distribution Transformer Replacement
|  | INCD-11988-K | Weavers | Network | WEACB6 | 22/02/2026 | 14:07 | 22/02/2026 | 15:55 | 0.0073653 | 6.82e-05 | 7 | 756 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-12033-K | Horotiu | Network | HORCB5 | 24/02/2026 | 08:09 | 24/02/2026 | 12:04 | 0.23348 | 0.0009937 | 102 | 23965 | Unplanned interruptions on the network | Defective Equipment | Contact problem
|  | INCD-12067-K | Latham Court | Network | LATCB5 | 25/02/2026 | 18:48 | 25/02/2026 | 19:45 | 0.52178 | 0.015988 | 1641 | 53557 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-12067-K | Latham Court | Network | LATCB8 | 25/02/2026 | 18:48 | 25/02/2026 | 19:45 | 0.056282 | 0.0021239 | 218 | 5777 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-12067-K | Latham Court | Network | WALCB1 | 25/02/2026 | 18:48 | 25/02/2026 | 19:45 | 0.010356 | 0.0007209 | 74 | 1063 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-266-N | Finlayson | Network | FINCB2 | 27/02/2026 | 09:07 | 27/02/2026 | 13:47 | 0.088861 | 0.000341 | 35 | 9121 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-12148-K | Silverdale | Network | HAMCB2862 | 03/03/2026 | 04:13 | 03/03/2026 | 05:16 | 0.10222 | 0.0016757 | 172 | 10492 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-12226-K | Chartwell | Network | CHACB9 | 05/03/2026 | 23:43 | 06/03/2026 | 00:43 | 0.09987 | 0.0055143 | 566 | 10251 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-12241-K | Wallace Rd | Network | WALCB5 | 06/03/2026 | 15:51 | 06/03/2026 | 15:51 | 0.0031873 | 0.0076479 | 785 | 327.15 | Unplanned interruptions on the network | Human error | Unintentionally Disabled
|  | INCD-635-M | Horotiu | Network | KOHCB6 | 08/03/2026 | 08:02 | 08/03/2026 | 12:44 | 0.0027474 | 9.7e-06 | 1 | 282 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-12272-K | Transpower Hamilton | Network | BORCB6 | 09/03/2026 | 06:33 | 09/03/2026 | 07:44 | 0.31463 | 0.013922 | 1429 | 32295 | Unplanned interruptions on the network | Defective Equipment | Loose connection
|  | INCD-640-M | Finlayson | Network | FINCB2 | 09/03/2026 | 09:05 | 09/03/2026 | 12:56 | 0.020255 | 8.77e-05 | 9 | 2079 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-12280-K | Te Uku | Network | NGACB2 | 09/03/2026 | 12:41 | 09/03/2026 | 12:50 | 0.0017312 | 0.0001949 | 20 | 177.7 | Unplanned interruptions on the network | Human error | Tree felled into line (WEL)
|  | INCD-12280-K | Te Uku | Network | TEUCB13 | 09/03/2026 | 12:41 | 09/03/2026 | 12:50 | 0.0035492 | 0.0003994 | 41 | 364.3 | Unplanned interruptions on the network | Human error | Tree felled into line (WEL)
|  | INCD-12333-K | Te Uku | Network | TEUCB12 | 12/03/2026 | 11:15 | 12/03/2026 | 12:56 | 0.056828 | 0.0005651 | 58 | 5833 | Unplanned interruptions on the network | Unknown | Fire Risk Mitigation Patrol - Sucessfully reclosed
|  | INCD-12346-K | Te Kauwhata | Network | TEKCB5 | 12/03/2026 | 16:02 | 12/03/2026 | 17:42 | 0.0009743 | 9.7e-06 | 1 | 100 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-12351-K | Hoeka | Network | HOECB6 | 12/03/2026 | 23:59 | 13/03/2026 | 00:03 | 0.021044 | 0.0058455 | 600 | 2160 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-12352-K | Hoeka | Network | HOECB1 | 12/03/2026 | 23:59 | 13/03/2026 | 00:16 | 0.10898 | 0.0063424 | 651 | 11186.22 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-12363-K | Te Uku | Network | TEUCB11 | 13/03/2026 | 09:16 | 13/03/2026 | 13:34 | 0.0025136 | 9.7e-06 | 1 | 258 | Unplanned interruptions on the network | Defective Equipment | Intnl insulation failure
|  | INCD-12383-K | Transpower Hamilton | Network | HOECB1 | 15/03/2026 | 00:04 | 15/03/2026 | 00:07 | 0.020294 | 0.0063424 | 651 | 2083.06 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-12500-K | Horotiu | Network | NGACB3 | 20/03/2026 | 02:21 | 20/03/2026 | 02:35 | 0.086143 | 0.0090995 | 934 | 8842 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-272-N | Chartwell | Network | CHACB9 | 20/03/2026 | 09:05 | 20/03/2026 | 11:40 | 0.012081 | 7.79e-05 | 8 | 1240 | Planned interruptions on the network | Planned | New Connections
|  | INCD-12545-K | Whatawhata | Network | WHACB4 | 20/03/2026 | 20:10 | 20/03/2026 | 23:11 | 0.030163 | 0.0005261 | 54 | 3096 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-12562-K | Claudelands | Network | HAMCB2722 | 21/03/2026 | 00:28 | 21/03/2026 | 00:28 | 0.0036924 | 0.0055337 | 568 | 379 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-12603-K | Glasgow St | Network | GLACB5 | 22/03/2026 | 17:28 | 23/03/2026 | 00:58 | 0.2175 | 0.000984 | 101 | 22325 | Unplanned interruptions on the network | Lightning | Spontaneous failure
|  | INCD-674-M | Wallace | Network | WALCB6 | 24/03/2026 | 09:30 | 24/03/2026 | 12:26 | 0.011749 | 6.82e-05 | 7 | 1206 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-12634-K | Pukete | Network | PUKCB10 | 25/03/2026 | 08:30 | 25/03/2026 | 16:02 | 0.20185 | 0.0004676 | 48 | 20718 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-12651-K | Finlayson Rd | Network | FINCB2 | 26/03/2026 | 06:17 | 26/03/2026 | 06:30 | 0.028049 | 0.0043452 | 446 | 2879 | Unplanned interruptions on the network | Defective Equipment | Hairline crack
|  | INCD-12131-K | Chartwell | Network | CHACB12 | 26/03/2026 | 08:30 | 26/03/2026 | 10:43 | 0.022213 | 0.0029617 | 304 | 2280 | Planned interruptions on the network | Planned | New Connections
|  | INCD-12709-K | Civic Car Park | Network | CIVCB4 | 27/03/2026 | 08:00 | 27/03/2026 | 08:07 | 0.010142 | 0.0014321 | 147 | 1041 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-12810-K | Hampton Downs | Network | HPTCB5 | 31/03/2026 | 09:10 | 31/03/2026 | 10:58 | 0.0073751 | 6.82e-05 | 7 | 757 | Unplanned interruptions on the network | Defective Equipment | Faulty joint/connection
|  | INCD-849-K | Gordonton | Network | GORCB13 | 03/04/2025 | 09:52 | 03/04/2025 | 09:52 | 0.0036242 | 9.7e-06 | 1 | 372 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-21-L | Sandwich Rd | Network | SANCB6 | 09/04/2025 | 16:51 | 09/04/2025 | 17:54 | 0.021482 | 0.000341 | 35 | 2205 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-1116-K | Weavers | Private | WEACB3 | 09/04/2025 | 21:55 | 09/04/2025 | 22:09 | 0.0005456 | 3.9e-05 | 4 | 56 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-3114-E | Te Uku | Network | TEUCB11 | 11/04/2025 | 09:35 | 11/04/2025 | 13:39 | 0.0071315 | 2.92e-05 | 3 | 732 | Planned interruptions on the network | Planned | Transformer Upgrade
|  | INCD-32-M | Chartwell | Network | CHACB5 | 13/04/2025 | 09:45 | 13/04/2025 | 17:34 | 0.027415 | 5.85e-05 | 6 | 2814 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-1288-K | Whatawhata | Network | WHACB4 | 15/04/2025 | 07:12 | 15/04/2025 | 09:11 | 0.0069561 | 5.85e-05 | 6 | 714 | Unplanned interruptions on the network | Defective Equipment | Mechanism seized
|  | INCD-1383-K | Weavers | Network | WEACB3 | 17/04/2025 | 09:31 | 17/04/2025 | 16:15 | 0.91486 | 0.0078817 | 809 | 93904 | Unplanned interruptions on the network | Vegetation | Tree blown ovr on line (OUT of Zone)
|  | INCD-32-L | Weavers | Network | WEACB3 | 17/04/2025 | 16:37 | 17/04/2025 | 16:39 | 0.0027474 | 0.0015393 | 158 | 282 | Unplanned interruptions on the network | Vegetation | Tree blown ovr on line (OUT of Zone)
|  | INCD-16-M | Raglan | Network | TEUCB1 | 18/04/2025 | 14:51 | 18/04/2025 | 23:45 | 0.0003617 | 3.9e-05 | 4 | 37.13 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-1746-K | Weavers | Network | GLACB1 | 26/04/2025 | 16:02 | 26/04/2025 | 16:32 | 0.17887 | 0.0070146 | 720 | 18360 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-1866-K | Transpower Hamilton | Network | HAMCB2802 | 30/04/2025 | 00:08 | 30/04/2025 | 00:51 | 0.12121 | 0.0034586 | 355 | 12441 | Planned interruptions on the network | Planned | New Connections
|  | INCD-26-M | Te Uku | Network | TEUCB12 | 30/04/2025 | 10:06 | 30/04/2025 | 12:48 | 0.0031566 | 1.95e-05 | 2 | 324 | Planned interruptions on the network | Planned | Distribution Transformer Replacement
|  | INCD-25-M | Weavers | Network | WEACB5 | 30/04/2025 | 10:08 | 30/04/2025 | 13:15 | 0.014575 | 7.79e-05 | 8 | 1496 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-1927-K | Ngaruawahia | Network | NGACB2 | 01/05/2025 | 07:56 | 01/05/2025 | 08:11 | 0.064135 | 0.0061475 | 631 | 6583 | Unplanned interruptions on the network | Vegetation | Tree known grows in line
|  | INCD-2082-K | Te Uku | Network | TEUCB13 | 05/05/2025 | 15:42 | 05/05/2025 | 19:22 | 0.01286 | 5.85e-05 | 6 | 1320 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-41-M | Sandwich | Network | SANCB5 | 05/05/2025 | 20:09 | 05/05/2025 | 21:05 | 0.0027279 | 4.87e-05 | 5 | 280 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-44-M | Weavers | Network | WEACB2 | 07/05/2025 | 09:08 | 07/05/2025 | 14:36 | 0.049862 | 0.0001559 | 16 | 5118 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2353-K | Latham Court | Network | LATCB5 | 07/05/2025 | 17:35 | 07/05/2025 | 18:22 | 0.017858 | 0.00038 | 39 | 1833 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-2279-K | Te Uku | Network | TEUCB13 | 09/05/2025 | 14:17 | 09/05/2025 | 17:36 | 0.0019388 | 9.7e-06 | 1 | 199 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-2280-K | Peacockes Rd | Network | PEACB12 | 09/05/2025 | 18:59 | 10/05/2025 | 03:27 | 0.38085 | 0.0028253 | 290 | 39092 | Unplanned interruptions on the network | Defective Equipment | Wear or shear of pins
|  | INCD-2351-K | Wallace Rd | Network | WALCB6 | 09/05/2025 | 22:57 | 09/05/2025 | 22:58 | 0.0075734 | 0.0048323 | 496 | 777.36 | Unplanned interruptions on the network | Defective Equipment | Wear or shear of pins
|  | INCD-2287-K | Glasgow St | Network | GLACB2 | 10/05/2025 | 05:01 | 10/05/2025 | 06:35 | 0.0009158 | 9.7e-06 | 1 | 94 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2315-K | Te Kauwhata | Network | HPTCB5 | 11/05/2025 | 07:54 | 11/05/2025 | 08:59 | 0.20862 | 0.0033612 | 345 | 21413 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-70-L | Latham | Network | LATCB5 | 13/05/2025 | 18:09 | 13/05/2025 | 18:54 | 0.1004 | 0.002231 | 229 | 10305 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2489-K | Weavers | Network | WEACB6 | 15/05/2025 | 09:06 | 15/05/2025 | 17:39 | 0.62401 | 0.0012178 | 125 | 64050 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2495-K | Hospital | Network | HOSCB11 | 15/05/2025 | 06:35 | 15/05/2025 | 11:30 | 0.18681 | 0.0006333 | 65 | 19175 | Unplanned interruptions on the network | Defective Equipment | Jumpers come off
|  | INCD-2628-K | Finlayson Rd | Network | FINCB2 | 20/05/2025 | 06:52 | 20/05/2025 | 08:55 | 0.025106 | 0.0002046 | 21 | 2577 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-69-M | Transpower Hamilton | Network | HAMCB2862 | 22/05/2025 | 09:32 | 22/05/2025 | 15:19 | 0.78585 | 0.002309 | 237 | 80662 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-2865-K | Peacockes Rd | Network | PEACB14 | 26/05/2025 | 09:04 | 26/05/2025 | 14:55 | 0.25989 | 0.0007404 | 76 | 26676 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-49-M | Te Kauwhata | Network | TEKCB5 | 26/05/2025 | 09:06 | 26/05/2025 | 17:31 | 0.23124 | 0.0004579 | 47 | 23735 | Planned interruptions on the network | Planned | New Connections
|  | INCD-87-M | Gordonton | Network | GORCB12 | 28/05/2025 | 10:01 | 28/05/2025 | 16:44 | 0.20602 | 0.0005261 | 54 | 21147 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-3069-K | Finlayson Rd | Network | FINCB3 | 30/05/2025 | 01:35 | 30/05/2025 | 04:01 | 0.0021206 | 0.0024941 | 256 | 217.66 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-3069-K | Finlayson Rd | Network | FINCB4 | 30/05/2025 | 01:35 | 30/05/2025 | 04:01 | 0.13468 | 0.0023577 | 242 | 13824.34 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-3110-K | Te Uku | Network | TEUCB11 | 30/05/2025 | 12:37 | 30/05/2025 | 17:15 | 0.0054168 | 1.95e-05 | 2 | 556 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-3141-K | Weavers | Network | WEACB4 | 31/05/2025 | 20:38 | 01/06/2025 | 00:29 | 0.029257 | 0.0001267 | 13 | 3003 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-3246-K | Whatawhata | Network | WHACB4 | 04/06/2025 | 15:44 | 04/06/2025 | 21:58 | 0.021862 | 5.85e-05 | 6 | 2244 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-3430-K | Weavers | Network | WEACB2 | 09/06/2025 | 17:32 | 09/06/2025 | 20:36 | 0.0071705 | 3.9e-05 | 4 | 736 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-3495-K | Te Uku | Network | TEUCB11 | 11/06/2025 | 01:15 | 11/06/2025 | 03:45 | 0.054042 | 0.0007502 | 77 | 5547 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-83-M | Ngaruawahia | Network | NGACB2 | 12/06/2025 | 09:12 | 12/06/2025 | 15:20 | 0.051099 | 0.0001461 | 15 | 5245 | Planned interruptions on the network | Planned | Distribution Transformer Replacement
|  | INCD-3607-K | Transpower Hamilton | Network | HAMCB2862 | 13/06/2025 | 05:14 | 13/06/2025 | 06:40 | 0.19283 | 0.0022603 | 232 | 19793 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-144-M | Weavers | Network | WEACB3 | 24/06/2025 | 09:43 | 24/06/2025 | 14:29 | 0.12196 | 0.0004287 | 44 | 12518 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-174-M | Finlayson | Network | FINCB1 | 25/06/2025 | 09:45 | 25/06/2025 | 11:15 | 0.033319 | 0.0003702 | 38 | 3420 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-3999-K | Whatawhata | Network | RAGCB2 | 28/06/2025 | 00:00 | 28/06/2025 | 00:12 | 0.089707 | 0.0076674 | 787 | 9207.84 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-3999-K | Whatawhata | Network | RAGCB6 | 28/06/2025 | 00:00 | 28/06/2025 | 00:12 | 0.11638 | 0.0099471 | 1021 | 11945.62 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-3999-K | Whatawhata | Network | TEUCB13 | 28/06/2025 | 00:00 | 28/06/2025 | 00:12 | 0.0045595 | 0.0003897 | 40 | 468 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-3999-K | Whatawhata | Network | TUKCB32 | 28/06/2025 | 00:00 | 28/06/2025 | 00:12 | 0.0011399 | 9.74e-05 | 10 | 117 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-4014-K | Finlayson | Network | FINCB1 | 28/06/2025 | 18:38 | 28/06/2025 | 21:18 | 0.010912 | 6.82e-05 | 7 | 1120 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-4081-K | Whitiora School | Private | WHICB7 | 01/07/2025 | 20:05 | 01/07/2025 | 20:11 | 5.85e-05 | 9.7e-06 | 1 | 6 | Planned interruptions on the network | Planned | External Customer
|  | INCD-197-M | Rural Bank | Network | RURCB10 | 02/07/2025 | 01:00 | 02/07/2025 | 04:34 | 0.056292 | 0.000263 | 27 | 5778 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-4118-K | Latham | Network | LATCB5 | 03/07/2025 | 09:39 | 03/07/2025 | 15:42 | 1.2977 | 0.003897 | 400 | 133198 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-4142-K | Latham | Network | LATCB2 | 03/07/2025 | 16:04 | 03/07/2025 | 16:45 | 0.03555 | 0.0008671 | 89 | 3649 | Planned interruptions on the network | Planned | Distribution Transformer Replacement
|  | INCD-4194-K | Te Kauwhata | Network | TEKCB5 | 04/07/2025 | 17:47 | 04/07/2025 | 21:51 | 0.0095087 | 3.9e-05 | 4 | 976 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-4198-K | Glasgow St | Network | GLACB2 | 05/07/2025 | 08:16 | 05/07/2025 | 11:31 | 0.077891 | 0.0003994 | 41 | 7995 | Unplanned interruptions on the network | Defective Equipment | Connect/jumper loose
|  | INCD-26-N | Hampton Downs | Network | HPTCB5 | 07/07/2025 | 00:07 | 07/07/2025 | 02:35 | 0.036047 | 0.0002436 | 25 | 3700 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-161-M | Horotiu | Network | KOHCB6 | 11/07/2025 | 09:20 | 11/07/2025 | 11:21 | 0.034187 | 0.0002825 | 29 | 3509 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-4462-K | Finlayson Rd | Network | FINCB2 | 11/07/2025 | 14:24 | 12/07/2025 | 06:32 | 0.61205 | 0.0043062 | 442 | 62823 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-399-L | Weavers | Network | WEACB6 | 11/07/2025 | 16:48 | 12/07/2025 | 12:22 | 0.15709 | 0.0011106 | 114 | 16124 | Unplanned interruptions on the network | Defective Equipment | Connect/jumper loose
|  | INCD-430-L | Pukete | Network | PUKCB4 | 12/07/2025 | 15:51 | 12/07/2025 | 16:15 | 0.0002338 | 9.7e-06 | 1 | 24 | Unplanned interruptions on the network | Defective Equipment | Cable termination fails
|  | INCD-4560-K | Hampton Downs | Network | HPTCB4 | 14/07/2025 | 22:51 | 15/07/2025 | 01:28 | 0.0015296 | 9.7e-06 | 1 | 157 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-4571-K | Avalon | Network | AVACB3 | 15/07/2025 | 09:11 | 15/07/2025 | 11:30 | 0.11105 | 0.0007989 | 82 | 11398 | Unplanned interruptions on the network | Defective Equipment | Connect/jumper loose
|  | INCD-169-M | Glasgow | Network | GLACB2 | 18/07/2025 | 09:06 | 18/07/2025 | 10:58 | 0.0021823 | 1.95e-05 | 2 | 224 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-193-M | Hoeka | Network | HOECB1 | 22/07/2025 | 10:07 | 22/07/2025 | 15:11 | 0.097737 | 0.0003215 | 33 | 10032 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-202-M | Glasgow | Network | GORCB11 | 23/07/2025 | 09:05 | 23/07/2025 | 14:59 | 0.16246 | 0.0004774 | 49 | 16675 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-192-M | Hoeka | Network | HOECB1 | 24/07/2025 | 10:05 | 24/07/2025 | 17:05 | 0.56058 | 0.0013347 | 137 | 57540 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-211-M | Transpower Hamilton | Network | HAMCB2902 | 25/07/2025 | 09:13 | 25/07/2025 | 15:45 | 0.17568 | 0.0004482 | 46 | 18032 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-5034-K | Chartwell | Network | CHACB9 | 25/07/2025 | 14:49 | 25/07/2025 | 19:08 | 0.095847 | 0.0006333 | 65 | 9838 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-5166-K | Ngaruawahia | Network | HORCB3 | 29/07/2025 | 09:03 | 29/07/2025 | 17:13 | 0.012714 | 2.92e-05 | 3 | 1305 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-206-M | Finlayson | Network | FINCB1 | 30/07/2025 | 10:09 | 30/07/2025 | 14:08 | 0.020956 | 8.77e-05 | 9 | 2151 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-224-M | Gordonton | Network | GORCB11 | 11/08/2025 | 08:34 | 11/08/2025 | 13:11 | 0.067808 | 0.0002533 | 26 | 6960 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-234-M | Weavers | Network | WEACB5 | 12/08/2025 | 09:34 | 12/08/2025 | 15:26 | 0.17833 | 0.0005066 | 52 | 18304 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-5783-K | Whatawhata | Network | WHACB2 | 14/08/2025 | 18:04 | 14/08/2025 | 18:19 | 0.018715 | 0.0046277 | 475 | 1921 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-233-M | Peacockes | Network | PEACB12 | 15/08/2025 | 10:09 | 15/08/2025 | 16:27 | 0.30576 | 0.0008184 | 84 | 31384 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-5900-K | Peacockes Rd | Network | PEACB12 | 18/08/2025 | 00:22 | 18/08/2025 | 12:23 | 0.012616 | 0.0003702 | 38 | 1295 | Unplanned interruptions on the network | Defective Equipment | Broken Neutral
|  | INCD-256-M | Whatawhata | Network | WHACB4 | 19/08/2025 | 09:37 | 19/08/2025 | 14:32 | 0.05526 | 0.0001949 | 20 | 5672 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-6029-K | Transpower Hamilton | Network | HAMCB2722 | 20/08/2025 | 23:57 | 21/08/2025 | 00:07 | 0.0091969 | 0.0011496 | 118 | 944 | Unplanned interruptions on the network | Defective Equipment | Fuse blown on overload
|  | INCD-6041-K | Pukete | Network | PUKCB2 | 21/08/2025 | 09:52 | 21/08/2025 | 16:38 | 0.09234 | 0.0002338 | 24 | 9478 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-6046-K | Peacockes Rd | Network | PEACB18 | 21/08/2025 | 10:48 | 21/08/2025 | 12:02 | 0.023713 | 0.0010132 | 104 | 2434 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-262-M | Ngaruawahia | Network | NGACB2 | 22/08/2025 | 09:13 | 22/08/2025 | 14:18 | 0.038629 | 0.0001267 | 13 | 3965 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-116-N | Finlayson Rd | Network | FINCB2 | 31/08/2025 | 08:04 | 31/08/2025 | 08:21 | 0.010454 | 0.0006333 | 65 | 1073 | Unplanned interruptions on the network | Vegetation | Tree blown ovr on line (OUT of Zone)
|  | INCD-6395-K | Horotiu | Network | NGACB5 | 31/08/2025 | 17:25 | 31/08/2025 | 22:29 | 0.28488 | 0.0017342 | 178 | 29241 | Unplanned interruptions on the network | Vegetation | Tree blown ovr on line (OUT of Zone)
|  | INCD-6417-K | Ngaruawahia | Network | NGACB2 | 31/08/2025 | 18:21 | 01/09/2025 | 04:41 | 0.078447 | 0.0001267 | 13 | 8052 | Unplanned interruptions on the network | Defective Equipment | Faulty joint/connection
|  | INCD-6410-K | Horotiu | Network | GORCB12 | 31/08/2025 | 18:22 | 31/08/2025 | 18:41 | 0.08095 | 0.0046569 | 478 | 8309 | Unplanned interruptions on the network | Defective Equipment | Broken binder
|  | INCD-118-N | Te Uku | Network | TEUCB11 | 01/09/2025 | 08:58 | 01/09/2025 | 20:08 | 0.045692 | 6.82e-05 | 7 | 4690 | Unplanned interruptions on the network | Adverse weather | High wind lne break
|  | INCD-6517-K | Weavers | Network | WEACB6 | 01/09/2025 | 09:20 | 01/09/2025 | 16:59 | 0.0089436 | 1.95e-05 | 2 | 918 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-247-M | Horotiu | Network | HORCB5 | 02/09/2025 | 08:33 | 02/09/2025 | 10:15 | 0.0009937 | 9.7e-06 | 1 | 102 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-246-M | Horotiu | Network | HORCB5 | 02/09/2025 | 08:47 | 02/09/2025 | 11:15 | 0.10958 | 0.0007404 | 76 | 11248 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-6546-K | Weavers | Network | WEACB4 | 02/09/2025 | 09:30 | 02/09/2025 | 11:24 | 0.0033319 | 2.92e-05 | 3 | 342 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-278-M | Goedonton | Network | GORCB12 | 05/09/2025 | 09:49 | 05/09/2025 | 15:38 | 0.037401 | 0.0001072 | 11 | 3839 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-6829-K | Sandwich Rd | Network | SANCB5 | 06/09/2025 | 12:36 | 06/09/2025 | 14:15 | 0.14757 | 0.0014906 | 153 | 15147 | Unplanned interruptions on the network | Third_party | Hit by car
|  | INCD-6883-K | Kent St | Network | KENCB3 | 09/09/2025 | 09:15 | 09/09/2025 | 09:33 | 0.11702 | 0.0069367 | 712 | 12011 | Unplanned interruptions on the network | Defective Equipment | Cable joint fails
|  | INCD-6883-K | Kent St | Network | NORCB5 | 09/09/2025 | 09:15 | 09/09/2025 | 09:33 | 0.058753 | 0.0033319 | 342 | 6030.57 | Unplanned interruptions on the network | Defective Equipment | Cable joint fails
|  | INCD-7228-K | Weavers | Network | WEACB3 | 16/09/2025 | 12:47 | 16/09/2025 | 18:40 | 0.22934 | 0.0044621 | 458 | 23540 | Unplanned interruptions on the network | Defective Equipment | Pins fulls out
|  | INCD-7763-K | Steele Park | Network | STECB3 | 23/09/2025 | 16:41 | 23/09/2025 | 16:48 | 0.014253 | 0.0020362 | 209 | 1463 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-319-M | Avalon | Network | AVACB3 | 26/09/2025 | 10:23 | 26/09/2025 | 11:45 | 0.23248 | 0.0028351 | 291 | 23862 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-7660-K | Te Uku | Network | TEUCB11 | 27/09/2025 | 09:31 | 27/09/2025 | 12:47 | 0.0057189 | 2.92e-05 | 3 | 587 | Unplanned interruptions on the network | Wildlife | Snails on HV bushings
|  | INCD-7780-K | Sandwich | Network | SANCB4 | 01/10/2025 | 05:01 | 01/10/2025 | 05:35 | 0.0059624 | 0.0001754 | 18 | 612 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-335-M | Horotiu | Network | HORCB6 | 02/10/2025 | 20:59 | 02/10/2025 | 21:25 | 0.0005066 | 1.95e-05 | 2 | 52 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-7943-K | Te Kauwhata | Network | TEKCB6 | 04/10/2025 | 10:27 | 05/10/2025 | 09:53 | 0.013698 | 9.7e-06 | 1 | 1406 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-351-M | Avalon | Network | AVACB3 | 07/10/2025 | 09:49 | 07/10/2025 | 15:22 | 0.77584 | 0.0024064 | 247 | 79635 | Planned interruptions on the network | Planned | Recloser & Sectionaliser replacement
|  | INCD-8095-K | Transpower Hamilton | Network | HAMCB2902 | 09/10/2025 | 07:12 | 09/10/2025 | 11:29 | 1.0653 | 0.0047446 | 487 | 109344.95 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-8103-K | Chartwell | Network | CHACB9 | 09/10/2025 | 12:00 | 10/10/2025 | 02:06 | 0.38394 | 0.0035463 | 364 | 39409 | Unplanned interruptions on the network | Third_party | High vehicle contact
|  | INCD-8127-K | Wallace | Network | WALCB5 | 10/10/2025 | 09:04 | 10/10/2025 | 10:21 | 0.057013 | 0.0007404 | 76 | 5852 | Planned interruptions on the network | Planned | Transformer Upgrade
|  | INCD-8163-K | Peacockes Rd | Network | PEACB17 | 13/10/2025 | 05:09 | 13/10/2025 | 12:27 | 0.86094 | 0.011935 | 1225 | 88369.85 | Unplanned interruptions on the network | Defective Equipment | Incorr Protect setting ld
|  | INCD-8212-K | Peacockes | Network | PEACB17 | 14/10/2025 | 20:42 | 14/10/2025 | 21:02 | 0.0011691 | 5.85e-05 | 6 | 120 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-8305-K | Glasgow St | Network | GLACB2 | 19/10/2025 | 08:47 | 19/10/2025 | 10:28 | 0.003936 | 3.9e-05 | 4 | 404 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-8313-K | Weavers | Network | WEACB6 | 20/10/2025 | 06:21 | 20/10/2025 | 09:31 | 0.04426 | 0.0002338 | 24 | 4543 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-361-M | Raglan | Network | RAGCB2 | 22/10/2025 | 09:38 | 22/10/2025 | 15:28 | 0.078427 | 0.0002241 | 23 | 8050 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-373-M | Hoeka | Network | HOECB3 | 23/10/2025 | 08:41 | 23/10/2025 | 10:36 | 0.010084 | 8.77e-05 | 9 | 1035 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-8868-K | Finlayson Rd | Network | FINCB4 | 13/11/2025 | 09:51 | 13/11/2025 | 12:58 | 0.0072582 | 3.9e-05 | 4 | 745 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-8898-K | Transpower Hamilton | Network | HAMCB2722 | 14/11/2025 | 08:49 | 14/11/2025 | 13:32 | 0.6294 | 0.0022992 | 236 | 64604 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-8907-K | Glasgow St | Network | GLACB2 | 14/11/2025 | 09:45 | 14/11/2025 | 11:01 | 0.0014809 | 1.95e-05 | 2 | 152 | Unplanned interruptions on the network | Defective Equipment | Nut or bolt loose
|  | INCD-392-M | Peacockes | Network | PEACB16 | 14/11/2025 | 13:01 | 14/11/2025 | 15:59 | 0.18262 | 0.0017049 | 175 | 18745 | Planned interruptions on the network | Planned | Distribution Transformer Replacement
|  | INCD-9009-K | Transpower Hamilton | Network | HAMCB2902 | 17/11/2025 | 23:00 | 18/11/2025 | 03:18 | 0.27649 | 0.0010717 | 110 | 28380 | Unplanned interruptions on the network | Defective Equipment | Loss or failure of oil
|  | INCD-423-M | Weavers | Network | WEACB6 | 18/11/2025 | 09:37 | 18/11/2025 | 15:29 | 0.0068587 | 1.95e-05 | 2 | 704 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-9045-K | Te Kauwhata | Network | TEKCB5 | 18/11/2025 | 15:51 | 18/11/2025 | 18:28 | 0.0061183 | 3.9e-05 | 4 | 628 | Unplanned interruptions on the network | Defective Equipment | Stay wire/ line clash
|  | INCD-9060-K | Te Kauwhata | Network | TEKCB5 | 18/11/2025 | 19:07 | 19/11/2025 | 11:23 | 0.019017 | 1.95e-05 | 2 | 1952 | Unplanned interruptions on the network | Defective Equipment | Stay wire/ line clash
|  | INCD-9078-K | Bryce St | Network | BRYCB6 | 19/11/2025 | 14:07 | 19/11/2025 | 16:26 | 0.057091 | 0.0021531 | 221 | 5860 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-429-M | Pukete | Network | TASCB4 | 20/11/2025 | 08:18 | 20/11/2025 | 15:42 | 0.87811 | 0.0019777 | 203 | 90132 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-1442-L | Avalon Dr | Network | AVACB4 | 23/11/2025 | 13:22 | 23/11/2025 | 14:43 | 0.041035 | 0.0005066 | 52 | 4212 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-9246-K | Glasgow | Network | GLACB2 | 26/11/2025 | 05:41 | 26/11/2025 | 07:58 | 0.0080083 | 5.85e-05 | 6 | 822 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-1519-L | Transpower Hamilton | Private | HAMCB2902 | 27/11/2025 | 13:52 | 27/11/2025 | 14:06 | 0.02346 | 0.0016757 | 172 | 2408 | Unplanned interruptions on the network | Third_party | Temp Disconnect / safety isolation
|  | INCD-9319-K | Wallace Rd | Network | WALCB5 | 01/12/2025 | 05:43 | 01/12/2025 | 08:47 | 0.077083 | 0.0004189 | 43 | 7912 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-9321-K | Hoeka | Network | HOECB6 | 01/12/2025 | 06:31 | 01/12/2025 | 10:05 | 0.16075 | 0.0007697 | 79 | 16500 | Unplanned interruptions on the network | Defective Equipment | Line break at twist joint
|  | INCD-435-M | Gordonton | Network | GORCB12 | 02/12/2025 | 09:16 | 02/12/2025 | 14:40 | 0.18624 | 0.0005748 | 59 | 19116 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-448-M | Te Kauwhata | Network | TEKCB5 | 04/12/2025 | 09:16 | 04/12/2025 | 13:01 | 0.090313 | 0.0004579 | 47 | 9270 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-438-M | Hampton Downs | Network | HPTCB3 | 04/12/2025 | 09:30 | 04/12/2025 | 13:52 | 0.033183 | 0.0001267 | 13 | 3406 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-9523-K | Transpower Hamilton | Network | HAMCB2862 | 08/12/2025 | 17:49 | 08/12/2025 | 20:58 | 0.55649 | 0.011379 | 1168 | 57120 | Unplanned interruptions on the network | Defective Equipment | Cable termination fails
|  | INCD-8700-K | Pukete | Network | PUKCB4 | 11/12/2025 | 06:40 | 11/12/2025 | 17:20 | 0.0098789 | 0.0001169 | 12 | 1014 | Planned interruptions on the network | Planned | Transformer Upgrade
|  | INCD-9700-K | Te Kauwhata | Network | TEKCB6 | 12/12/2025 | 22:07 | 13/12/2025 | 00:14 | 0.0049492 | 3.9e-05 | 4 | 508 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-497-M | Whatawhata | Network | WHACB3 | 16/12/2025 | 09:35 | 16/12/2025 | 16:37 | 0.035989 | 8.77e-05 | 9 | 3694 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-528-M | Findlay | Network | FDLCB2 | 18/12/2025 | 08:01 | 18/12/2025 | 16:55 | 0.14302 | 0.0036437 | 374 | 14680 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-470-M | Horotiu | Network | KOHCB6 | 18/12/2025 | 09:33 | 18/12/2025 | 16:25 | 0.04653 | 0.0001169 | 12 | 4776 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-9889-K | Transpower Hamilton | Network | UNICB1 | 18/12/2025 | 16:55 | 18/12/2025 | 17:09 | 0.0001364 | 9.7e-06 | 1 | 14 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-9889-K | Transpower Hamilton | Network | HAMCB2882 | 18/12/2025 | 16:55 | 18/12/2025 | 17:09 | 0.0001364 | 9.7e-06 | 1 | 14 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-9970-K | Te Kauwhata | Network | TEKCB5 | 21/12/2025 | 09:00 | 21/12/2025 | 10:45 | 0.0092067 | 8.77e-05 | 9 | 945 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-10124-K | Finlayson Rd | Network | FINCB1 | 29/12/2025 | 15:20 | 30/12/2025 | 02:40 | 0.34409 | 0.0005066 | 52 | 35318 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-10160-K | Horotiu | Network | HORCB5 | 29/12/2025 | 15:42 | 30/12/2025 | 05:09 | 0.07076 | 8.77e-05 | 9 | 7263 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-10206-K | Raglan | Network | RAGCB3 | 30/12/2025 | 16:57 | 31/12/2025 | 10:01 | 0.019953 | 1.95e-05 | 2 | 2048 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-10256-K | Finlayson Rd | Network | FINCB1 | 03/01/2026 | 04:16 | 03/01/2026 | 12:31 | 0.12078 | 0.0075407 | 774 | 12397 | Unplanned interruptions on the network | Defective Equipment | Split crossarm
|  | INCD-10329-K | Weavers | Network | WEACB2 | 06/01/2026 | 09:14 | 06/01/2026 | 15:24 | 0.28044 | 0.0007599 | 78 | 28785 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-521-M | Tasman | Network | TASCB5 | 09/01/2026 | 09:23 | 09/01/2026 | 11:59 | 0.013678 | 8.77e-05 | 9 | 1404 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-10517-K | Finlayson Rd | Network | FINCB1 | 12/01/2026 | 09:14 | 12/01/2026 | 12:05 | 0.062518 | 0.0003994 | 41 | 6417 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-1701-L | Te Uku | Network | TEUCB11 | 13/01/2026 | 19:26 | 13/01/2026 | 22:16 | 0.0099374 | 5.85e-05 | 6 | 1020 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-10640-K | Weavers | Network | WEACB6 | 14/01/2026 | 17:08 | 14/01/2026 | 19:19 | 0.42007 | 0.0056994 | 585 | 43117 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (OUT of Zone)
|  | INCD-10727-K | Finlayson Rd | Network | FINCB2 | 16/01/2026 | 09:51 | 16/01/2026 | 14:04 | 0.0098594 | 3.9e-05 | 4 | 1012 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-556-M | Gordonton | Network | GORCB13 | 19/01/2026 | 09:08 | 19/01/2026 | 10:46 | 0.051557 | 0.0005261 | 54 | 5292 | Planned interruptions on the network | Planned | Recloser & Sectionaliser replacement
|  | INCD-10878-K | Whatawhata | Network | WHACB5 | 21/01/2026 | 04:22 | 21/01/2026 | 13:14 | 0.55739 | 0.0076381 | 784 | 57212 | Unplanned interruptions on the network | Defective Equipment | Insulator split
|  | INCD-1434-L | Finlayson | Network | FINCB2 | 21/01/2026 | 08:35 | 21/01/2026 | 13:57 | 0.025097 | 7.79e-05 | 8 | 2576 | Planned interruptions on the network | Planned | Transformer Upgrade
|  | INCD-1729-L | Gordonton | Network | GORCB13 | 21/01/2026 | 09:07 | 21/01/2026 | 13:34 | 0.0026012 | 9.7e-06 | 1 | 267 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-10944-K | Hoeka | Network | HOECB1 | 21/01/2026 | 21:56 | 22/01/2026 | 12:49 | 0.6526 | 0.0063131 | 648 | 66985 | Unplanned interruptions on the network | Vegetation | Tree blown ovr on line (OUT of Zone)
|  | INCD-11013-K | Whatawhata | Network | WHACB2 | 22/01/2026 | 10:18 | 22/01/2026 | 12:42 | 0.0042088 | 2.92e-05 | 3 | 432 | Unplanned interruptions on the network | Adverse weather | Line clash high wind
|  | INCD-11019-K | Weavers | Network | WEACB3 | 22/01/2026 | 13:32 | 22/01/2026 | 14:09 | 0.0014419 | 3.9e-05 | 4 | 148 | Unplanned interruptions on the network | Defective Equipment | Pins fulls out
|  | INCD-11744-K | Gordonton | Network | GORCB11 | 14/02/2026 | 13:02 | 14/02/2026 | 19:03 | 0.65116 | 0.0018024 | 185 | 66837 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-11837-K | Kent St | Network | KENCB4 | 17/02/2026 | 23:15 | 18/02/2026 | 00:46 | 0.44177 | 0.0083298 | 855 | 45345 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-11872-K | Kent St | Network | KENCB4 | 18/02/2026 | 00:20 | 18/02/2026 | 00:22 | 0.0092736 | 0.005563 | 571 | 951.87 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-11914-K | Peacockes | Network | PEACB12 | 19/02/2026 | 15:17 | 19/02/2026 | 16:15 | 0.010736 | 0.0001851 | 19 | 1102 | Unplanned interruptions on the network | Defective Equipment | Wear or shear of pins
|  | INCD-1911-L | Wallace Rd | Network | WALCB3 | 26/02/2026 | 00:32 | 28/02/2026 | 10:53 | 0.19892 | 0.0031955 | 328 | 20418 | Unplanned interruptions on the network | Defective Equipment | Intnl insulation failure
|  | INCD-1910-L | Steele Park | Network | STECB8 | 27/02/2026 | 09:09 | 27/02/2026 | 09:17 | 0.0088072 | 0.0011009 | 113 | 904 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-12115-K | Peachgrove Rd | Network | PCHCB6 | 01/03/2026 | 08:17 | 01/03/2026 | 15:27 | 0.16726 | 0.0003897 | 40 | 17168 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-12272-K | Transpower Hamilton | Network | BORCB5 | 09/03/2026 | 06:33 | 09/03/2026 | 07:44 | 0.77794 | 0.014205 | 1458 | 79850 | Unplanned interruptions on the network | Defective Equipment | Loose connection
|  | INCD-12293-K | Wallace | Network | WALCB6 | 10/03/2026 | 10:16 | 10/03/2026 | 12:03 | 0.0010424 | 9.7e-06 | 1 | 107 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-12309-K | Gordonton | Network | GORCB11 | 11/03/2026 | 04:19 | 11/03/2026 | 04:23 | 0.0081545 | 0.0018121 | 186 | 837 | Unplanned interruptions on the network | Defective Equipment | Flickers misaligned
|  | INCD-619-M | Chartwell | Network | CHACB9 | 11/03/2026 | 09:05 | 11/03/2026 | 17:05 | 0.17881 | 0.0017439 | 179 | 18354 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-12351-K | Hoeka | Network | HOECB3 | 12/03/2026 | 23:59 | 13/03/2026 | 00:03 | 0.014754 | 0.0085442 | 877 | 1514.4 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-642-M | Te Uku | Network | TEUCB12 | 13/03/2026 | 09:11 | 13/03/2026 | 10:04 | 0.0025818 | 4.87e-05 | 5 | 265 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-12382-K | Silverdale | Network | HOECB2 | 14/03/2026 | 23:59 | 15/03/2026 | 00:08 | 0.011047 | 0.0015296 | 157 | 1133.87 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-648-M | Hoeka | Network | HOECB3 | 17/03/2026 | 08:42 | 17/03/2026 | 13:56 | 0.078242 | 0.000263 | 27 | 8031 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-654-M | Weavers | Network | WEACB6 | 18/03/2026 | 09:44 | 18/03/2026 | 13:38 | 0.011399 | 4.87e-05 | 5 | 1170 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-12499-K | Weavers | Network | WEACB4 | 20/03/2026 | 01:06 | 20/03/2026 | 02:17 | 0.004842 | 6.82e-05 | 7 | 497 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-12500-K | Horotiu | Network | NGACB5 | 20/03/2026 | 02:21 | 20/03/2026 | 02:35 | 0.10017 | 0.0098204 | 1008 | 10282 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-716-M | Glasgow | Network | GLACB6 | 25/03/2026 | 08:31 | 25/03/2026 | 14:15 | 0.61331 | 0.0017829 | 183 | 62952 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-12647-K | Te Uku | Network | TEUCB11 | 25/03/2026 | 20:07 | 25/03/2026 | 21:36 | 0.0017342 | 1.95e-05 | 2 | 178 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-12681-K | Te Uku | Network | TEUCB11 | 26/03/2026 | 16:34 | 26/03/2026 | 22:49 | 0.31148 | 0.0010717 | 110 | 31971 | Unplanned interruptions on the network | Defective Equipment | Broken binder
|  | INCD-12682-K | Te Uku | Network | TEUCB11 | 26/03/2026 | 16:37 | 27/03/2026 | 13:05 | 0.064456 | 0.0002143 | 22 | 6616 | Unplanned interruptions on the network | Defective Equipment | Faulty joint/connection
|  | INCD-12870-K | Te Uku | Network | TEUCB11 | 27/03/2026 | 14:08 | 27/03/2026 | 15:47 | 0.0048225 | 4.87e-05 | 5 | 495 | Unplanned interruptions on the network | Defective Equipment | Insulator split
|  | INCD-12812-K | Transpower Hamilton | Network | HAMCB2822 | 30/03/2026 | 23:08 | 31/03/2026 | 11:22 | 0.012665 | 0.0030397 | 312 | 1300 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-3107-E | Peacockes | Network | PEACB12 | 01/04/2025 | 09:06 | 01/04/2025 | 12:47 | 0.015072 | 6.82e-05 | 7 | 1547 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-885-K | Te Uku | Network | TEUCB11 | 04/04/2025 | 09:00 | 04/04/2025 | 09:37 | 0.022193 | 0.0005943 | 61 | 2278 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-7-M | Latham | Network | LATCB5 | 10/04/2025 | 09:39 | 10/04/2025 | 17:08 | 1.2342 | 0.0028351 | 291 | 126680 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-1189-K | Horotiu | Private | NGACB5 | 11/04/2025 | 11:20 | 11/04/2025 | 16:25 | 0.0029715 | 9.7e-06 | 1 | 305 | Unplanned interruptions on the network | Third_party | Temp Disconnect / safety isolation
|  | INCD-1249-K | Horotiu | Private | NGACB5 | 14/04/2025 | 11:06 | 14/04/2025 | 19:33 | 0.0049395 | 9.7e-06 | 1 | 507 | Unplanned interruptions on the network | Third_party | Temp Disconnect / safety isolation
|  | INCD-8-M | Latham | Network | LATCB5 | 15/04/2025 | 09:30 | 15/04/2025 | 16:08 | 1.1085 | 0.0027864 | 286 | 113776 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-1379-K | Kent St | Network | KENCB3 | 17/04/2025 | 09:01 | 17/04/2025 | 14:36 | 0.20235 | 0.000604 | 62 | 20770 | Planned interruptions on the network | Planned | Distribution Transformer Replacement
|  | INCD-1504-K | Weavers | Network | WEACB3 | 17/04/2025 | 13:55 | 17/04/2025 | 17:36 | 0.27123 | 0.0068587 | 704 | 27840 | Unplanned interruptions on the network | Vegetation | Tree blown ovr on line (OUT of Zone)
|  | INCD-16-M | Raglan | Network | TEUCB12 | 18/04/2025 | 14:51 | 18/04/2025 | 23:45 | 0.086132 | 0.0053194 | 546 | 8840.88 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-1697-K | Te Uku | Network | TEUCB11 | 24/04/2025 | 06:08 | 24/04/2025 | 19:08 | 0.015198 | 1.95e-05 | 2 | 1560 | Unplanned interruptions on the network | Lightning | Spontaneous failure
|  | INCD-1855-K | Sandwich | Network | SANCB7 | 29/04/2025 | 15:39 | 29/04/2025 | 16:12 | 0.065811 | 0.0019972 | 205 | 6755 | Unplanned interruptions on the network | Third_party | High vehicle contact
|  | INCD-1864-K | Whatawhata | Network | WHACB5 | 29/04/2025 | 19:18 | 30/04/2025 | 01:14 | 0.23445 | 0.0007112 | 73 | 24065 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-2145-K | Weavers | Network | WEACB3 | 06/05/2025 | 19:20 | 06/05/2025 | 22:11 | 0.0066639 | 3.9e-05 | 4 | 684 | Unplanned interruptions on the network | Defective Equipment | Mechanism seized
|  | INCD-2354-K | Claudelands | Network | CLACB3 | 07/05/2025 | 00:02 | 11/05/2025 | 01:05 | 0.32669 | 0.0031761 | 326 | 33532 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-2201-K | Foreman Rd | Network | TASCB3 | 07/05/2025 | 20:20 | 08/05/2025 | 00:32 | 0.022096 | 8.77e-05 | 9 | 2268 | Unplanned interruptions on the network | Defective Equipment | Fuse blow from overload
|  | INCD-2290-K | Hoeka | Network | HOECB1 | 10/05/2025 | 06:52 | 10/05/2025 | 08:55 | 0.03594 | 0.0002923 | 30 | 3689 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2315-K | Te Kauwhata | Network | HPTCB4 | 11/05/2025 | 07:54 | 11/05/2025 | 08:59 | 0.0006235 | 9.7e-06 | 1 | 64 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-67-L | Latham | Network | LATCB5 | 13/05/2025 | 09:37 | 13/05/2025 | 16:10 | 0.13018 | 0.0003312 | 34 | 13362 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-46-M | Horotiu | Network | HORCB5 | 20/05/2025 | 08:34 | 20/05/2025 | 11:45 | 0.078154 | 0.0004092 | 42 | 8022 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-91-M | Latham | Network | LATCB5 | 21/05/2025 | 11:05 | 21/05/2025 | 17:00 | 0.76525 | 0.0023674 | 243 | 78548 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2975-K | Peacockes Rd | Network | PEACB14 | 29/05/2025 | 00:06 | 29/05/2025 | 02:20 | 0.099218 | 0.0007404 | 76 | 10184 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-3049-K | Avalon Dr | Network | AVACB1 | 29/05/2025 | 19:21 | 30/05/2025 | 03:18 | 0.45693 | 0.0009645 | 99 | 46901 | Unplanned interruptions on the network | Adverse weather | High wind lne break
|  | INCD-3062-K | Peacockes | Network | PEACB14 | 30/05/2025 | 00:01 | 30/05/2025 | 01:39 | 0.067379 | 0.0007404 | 76 | 6916 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-3103-K | Te Uku | Network | TEUCB11 | 30/05/2025 | 08:45 | 31/05/2025 | 00:10 | 0.018024 | 1.95e-05 | 2 | 1850 | Unplanned interruptions on the network | Defective Equipment | Intnl insulation failure
|  | INCD-74-L | Chartwell | Network | CHACB13 | 01/06/2025 | 05:23 | 01/06/2025 | 06:43 | 0.097045 | 0.0015198 | 156 | 9961 | Unplanned interruptions on the network | Defective Equipment | Flashovr on cable bush
|  | INCD-110-M | Glasgow | Network | GLACB2 | 03/06/2025 | 08:33 | 03/06/2025 | 12:29 | 0.018394 | 7.79e-05 | 8 | 1888 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-3208-K | Latham Court | Network | LATCB3 | 04/06/2025 | 09:03 | 04/06/2025 | 11:10 | 0.053204 | 0.0004189 | 43 | 5461 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-79-L | Avalon Dr | Network | AVACB4 | 04/06/2025 | 13:45 | 04/06/2025 | 14:34 | 0.030552 | 0.0006235 | 64 | 3136 | Unplanned interruptions on the network | Defective Equipment | Blown Fuse
|  | INCD-3292-K | Te Kauwhata | Network | TEKCB6 | 05/06/2025 | 18:02 | 05/06/2025 | 22:29 | 0.2055 | 0.0007697 | 79 | 21093 | Unplanned interruptions on the network | Defective Equipment | Faulty joint/connection
|  | INCD-99-M | Weavers | Network | WEACB6 | 06/06/2025 | 10:20 | 06/06/2025 | 14:55 | 0.013396 | 4.87e-05 | 5 | 1375 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-3376-K | Avalon Dr | Network | AVACB8 | 08/06/2025 | 09:20 | 08/06/2025 | 15:09 | 0.0034001 | 9.7e-06 | 1 | 349 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-3529-K | Gordonton | Network | GORCB13 | 11/06/2025 | 12:43 | 11/06/2025 | 14:10 | 0.0025428 | 2.92e-05 | 3 | 261 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-3650-K | Simsey | Network | SIMCB2 | 14/06/2025 | 12:13 | 14/06/2025 | 12:15 | 1.95e-05 | 9.7e-06 | 1 | 2 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-119-M | Glasgow | Network | GLACB2 | 17/06/2025 | 09:44 | 17/06/2025 | 15:52 | 0.090625 | 0.0002533 | 26 | 9302 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-3799-K | Avalon Dr | Network | AVACB4 | 18/06/2025 | 09:15 | 18/06/2025 | 15:10 | 0.41542 | 0.0012081 | 124 | 42640 | Unplanned interruptions on the network | Defective Equipment | Cable termination fails
|  | INCD-3917-K | Gordonton | Network | GORCB13 | 24/06/2025 | 09:39 | 24/06/2025 | 15:06 | 0.22986 | 0.0007404 | 76 | 23594 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-136-M | Horotiu | Network | HORCB5 | 25/06/2025 | 08:35 | 25/06/2025 | 14:43 | 0.096538 | 0.000263 | 27 | 9909 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-60-M | Glasgow | Network | GLACB5 | 26/06/2025 | 08:39 | 26/06/2025 | 14:55 | 0.12617 | 0.0003605 | 37 | 12950 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-3999-K | Whatawhata | Network | RAGCB4 | 28/06/2025 | 00:00 | 28/06/2025 | 00:12 | 0.075459 | 0.0064495 | 662 | 7745.35 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-4039-K | Latham Court | Network | LATCB2 | 30/06/2025 | 08:07 | 30/06/2025 | 13:47 | 0.29481 | 0.0008671 | 89 | 30260 | Planned interruptions on the network | Planned | Distribution Transformer Replacement
|  | INCD-4053-K | Latham | Network | LATCB1 | 01/07/2025 | 05:01 | 01/07/2025 | 06:01 | 0.049209 | 0.0010814 | 111 | 5051 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-4084-K | Te Uku Wind Farm | Network | RAGCB3 | 02/07/2025 | 00:34 | 02/07/2025 | 00:46 | 0.0091823 | 0.0007307 | 75 | 942.5 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-4084-K | Te Uku Wind Farm | Network | RAGCB4 | 02/07/2025 | 00:34 | 02/07/2025 | 00:46 | 0.081049 | 0.0064495 | 662 | 8319.12 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-140-M | Glasgow | Network | GLACB2 | 04/07/2025 | 09:49 | 04/07/2025 | 15:43 | 0.14436 | 0.0004287 | 44 | 14818 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-170-M | Te Uku | Network | TEUCB12 | 09/07/2025 | 08:39 | 09/07/2025 | 13:27 | 0.011253 | 3.9e-05 | 4 | 1155 | Planned interruptions on the network | Planned | Distribution Transformer Replacement
|  | INCD-4487-K | Claudelands | Network | CLACB13 | 11/07/2025 | 23:48 | 11/07/2025 | 23:58 | 0.011204 | 0.0011204 | 115 | 1150 | Unplanned interruptions on the network | Defective Equipment | Fuse blown on overload
|  | INCD-429-L | Pukete | Network | PUKCB4 | 12/07/2025 | 12:39 | 12/07/2025 | 13:54 | 0.0007307 | 9.7e-06 | 1 | 75 | Unplanned interruptions on the network | Defective Equipment | Cable termination fails
|  | INCD-4493-K | Te Kauwhata | Network | TEKCB6 | 12/07/2025 | 17:31 | 12/07/2025 | 19:22 | 0.01288 | 0.0001169 | 12 | 1322 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-4780-K | Wallace | Network | WALCB1 | 20/07/2025 | 16:16 | 20/07/2025 | 17:40 | 0.0016367 | 1.95e-05 | 2 | 168 | Unplanned interruptions on the network | Defective Equipment | Wear or shear of pins
|  | INCD-148-M | Cobham | Network | COBCB11 | 23/07/2025 | 08:07 | 26/07/2025 | 12:27 | 0.081058 | 0.0003118 | 32 | 8320 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-4929-K | Weavers | Network | NGACB2 | 24/07/2025 | 07:17 | 24/07/2025 | 16:50 | 0.0002299 | 2.92e-05 | 3 | 23.6 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-4957-K | Ngaruawahia | Network | NGACB2 | 24/07/2025 | 07:32 | 24/07/2025 | 14:19 | 1.4052 | 0.012373 | 1270 | 144232.89 | Unplanned interruptions on the network | Defective Equipment | Line break at twist joint
|  | INCD-3582-K | Peacockes | Network | PEACB12 | 25/07/2025 | 10:08 | 25/07/2025 | 14:34 | 0.020732 | 7.79e-05 | 8 | 2128 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-5103-K | Sandwich Rd | Network | SANCB4 | 28/07/2025 | 07:24 | 28/07/2025 | 07:52 | 0.31043 | 0.011399 | 1170 | 31863 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-5118-K | Te Kauwhata | Network | TEKCB6 | 28/07/2025 | 09:03 | 28/07/2025 | 11:38 | 0.11049 | 0.0007112 | 73 | 11341 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-5166-K | Ngaruawahia | Network | NGACB3 | 29/07/2025 | 09:03 | 29/07/2025 | 17:13 | 0.080161 | 0.0001656 | 17 | 8228 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-239-M | Hoeka | Network | HOECB3 | 31/07/2025 | 08:30 | 31/07/2025 | 12:20 | 0.013445 | 5.85e-05 | 6 | 1380 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-220-M | Hoeka | Network | HOECB6 | 05/08/2025 | 09:35 | 05/08/2025 | 14:43 | 0.021005 | 6.82e-05 | 7 | 2156 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-90-L | Avalon | Network | AVACB8 | 07/08/2025 | 08:32 | 07/08/2025 | 15:49 | 0.28628 | 0.0006625 | 68 | 29385 | Planned interruptions on the network | Planned | Distribution Transformer Replacement
|  | INCD-5563-K | Whatawhata | Network | WHACB2 | 10/08/2025 | 07:32 | 10/08/2025 | 09:24 | 0.006547 | 5.85e-05 | 6 | 672 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-5627-K | Finlayson Rd | Network | FINCB4 | 11/08/2025 | 10:03 | 11/08/2025 | 12:24 | 0.0054948 | 3.9e-05 | 4 | 564 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-5633-K | Whatawhata | Network | WHACB4 | 11/08/2025 | 10:03 | 11/08/2025 | 14:30 | 0.023411 | 8.77e-05 | 9 | 2403 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-221-M | Transpower Hamilton | Network | HAMCB2902 | 12/08/2025 | 08:36 | 12/08/2025 | 16:21 | 0.25823 | 0.0005553 | 57 | 26505 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-5763-K | Hoeka | Private | HOECB6 | 14/08/2025 | 11:10 | 14/08/2025 | 11:29 | 0.0018511 | 9.74e-05 | 10 | 190 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-519-L | Gordonton | Network | GORCB13 | 17/08/2025 | 08:05 | 17/08/2025 | 08:43 | 0.0048128 | 0.0001267 | 13 | 494 | Unplanned interruptions on the network | Defective Equipment | Overheated connections
|  | INCD-5900-K | Peacockes Rd | Network | PEACB17 | 18/08/2025 | 00:22 | 18/08/2025 | 12:23 | 0.0035463 | 0.0001851 | 19 | 364 | Unplanned interruptions on the network | Defective Equipment | Broken Neutral
|  | INCD-251-M | Gordonton | Network | GORCB13 | 19/08/2025 | 09:08 | 19/08/2025 | 14:33 | 0.037996 | 0.0001169 | 12 | 3900 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-5969-K | Horotiu | Network | GORCB13 | 19/08/2025 | 20:17 | 19/08/2025 | 20:52 | 0.20163 | 0.006167 | 633 | 20695.84 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-286-M | Sandwich | Network | SANCB3 | 20/08/2025 | 08:40 | 20/08/2025 | 15:43 | 0.2143 | 0.0005066 | 52 | 21996 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-6108-K | Sandwich Rd | Network | SANCB1 | 23/08/2025 | 07:11 | 23/08/2025 | 09:55 | 0.0015978 | 9.7e-06 | 1 | 164 | Unplanned interruptions on the network | Lightning | Spontaneous failure
|  | INCD-6214-K | Hampton Downs | Network | HPTCB5 | 26/08/2025 | 10:08 | 26/08/2025 | 15:46 | 0.13172 | 0.0003897 | 40 | 13520 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-112-N | Transpower Hamilton | Network | HAMCB2762 | 26/08/2025 | 14:01 | 26/08/2025 | 14:11 | 0.0066249 | 0.0006625 | 68 | 680 | Planned interruptions on the network | Planned | New Connections
|  | INCD-111-N | Finlayson Rd | Network | FINCB2 | 31/08/2025 | 08:04 | 31/08/2025 | 08:18 | 0.019076 | 0.0014127 | 145 | 1958 | Unplanned interruptions on the network | Vegetation | Tree blown ovr on line (OUT of Zone)
|  | INCD-6351-K | Finlayson Rd | Network | FINCB2 | 31/08/2025 | 08:04 | 31/08/2025 | 18:21 | 0.11588 | 0.0005066 | 52 | 11894 | Unplanned interruptions on the network | Vegetation | Tree blown ovr on line (OUT of Zone)
|  | INCD-6474-K | Raglan | Network | RAGCB5 | 01/09/2025 | 09:39 | 01/09/2025 | 09:58 | 0.0075894 | 0.0003994 | 41 | 779 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-6486-K | Finlayson Rd | Network | FINCB1 | 01/09/2025 | 10:50 | 01/09/2025 | 13:25 | 0.03745 | 0.0003312 | 34 | 3844 | Unplanned interruptions on the network | Defective Equipment | Faulty joint/connection
|  | INCD-6755-K | Whatawhata | Network | WHACB4 | 05/09/2025 | 15:09 | 05/09/2025 | 17:14 | 0.0073069 | 5.85e-05 | 6 | 750 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (OUT of Zone)
|  | INCD-6761-K | Te Uku | Network | TEUCB11 | 05/09/2025 | 23:48 | 06/09/2025 | 00:59 | 0.016523 | 0.0002338 | 24 | 1696 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-6794-K | Weavers | Network | WEACB4 | 06/09/2025 | 20:30 | 06/09/2025 | 22:15 | 0.021482 | 0.0002046 | 21 | 2205 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-6883-K | Kent St | Network | KENCB9 | 09/09/2025 | 09:15 | 09/09/2025 | 09:33 | 0.039408 | 0.0030591 | 314 | 4045 | Unplanned interruptions on the network | Defective Equipment | Cable joint fails
|  | INCD-6883-K | Kent St | Network | MASCB13 | 09/09/2025 | 09:15 | 09/09/2025 | 09:33 | 0.12008 | 0.00681 | 699 | 12325.63 | Unplanned interruptions on the network | Defective Equipment | Cable joint fails
|  | INCD-352-M | Glasgow | Network | GLACB2 | 09/09/2025 | 09:18 | 09/09/2025 | 12:41 | 0.033621 | 0.0001656 | 17 | 3451 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-284-M | Horotiu | Network | HORCB5 | 10/09/2025 | 09:05 | 10/09/2025 | 13:19 | 0.022271 | 8.77e-05 | 9 | 2286 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-7017-K | Wallace | Network | WALCB4 | 12/09/2025 | 08:04 | 12/09/2025 | 10:10 | 0.097386 | 0.0012276 | 126 | 9996 | Planned interruptions on the network | Planned | Transformer Upgrade
|  | INCD-318-M | Glasgow | Network | GLACB1 | 15/09/2025 | 09:50 | 15/09/2025 | 16:30 | 0.019485 | 4.87e-05 | 5 | 2000 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-7207-K | Peacockes Rd | Network | PEACB17 | 16/09/2025 | 09:02 | 16/09/2025 | 15:31 | 0.81102 | 0.0020849 | 214 | 83246 | Planned interruptions on the network | Planned | Recloser & Sectionaliser replacement
|  | INCD-302-M | Gordonton | Network | GORCB13 | 16/09/2025 | 09:12 | 16/09/2025 | 15:30 | 0.010795 | 2.92e-05 | 3 | 1108 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-7244-K | Peacockes | Network | PEACB17 | 16/09/2025 | 16:08 | 16/09/2025 | 16:37 | 0.029666 | 0.001023 | 105 | 3045 | Planned interruptions on the network | Planned | Recloser & Sectionaliser replacement
|  | INCD-304-M | Peacockes | Network | PEACB12 | 18/09/2025 | 09:41 | 18/09/2025 | 15:55 | 0.16032 | 0.0004287 | 44 | 16456 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-7501-K | Weavers | Network | WEACB5 | 23/09/2025 | 07:18 | 23/09/2025 | 15:57 | 0.28891 | 0.0042672 | 438 | 29655 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-322-M | Hoeka | Network | HOECB1 | 25/09/2025 | 09:41 | 25/09/2025 | 15:54 | 0.11208 | 0.0003118 | 32 | 11504 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-7641-K | Horotiu | Network | WEACB5 | 26/09/2025 | 09:25 | 26/09/2025 | 11:03 | 0.0019095 | 1.95e-05 | 2 | 196 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-7750-K | Transpower Hamilton | Network | HAMCB2742 | 30/09/2025 | 10:03 | 30/09/2025 | 17:52 | 1.6241 | 0.003517 | 361 | 166704 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-677-L | Peacockes | Network | PEACB12 | 03/10/2025 | 11:57 | 03/10/2025 | 13:51 | 0.045537 | 0.0003994 | 41 | 4674 | Unplanned interruptions on the network | Defective Equipment | faulty line connection
|  | INCD-7921-K | Te Kauwhata | Network | FINCB2 | 04/10/2025 | 08:21 | 04/10/2025 | 10:03 | 0.09586 | 0.0054461 | 559 | 9839.31 | Unplanned interruptions on the network | Lightning | Lightning strike surge
|  | INCD-7937-K | Weavers | Network | WEACB3 | 04/10/2025 | 09:26 | 04/10/2025 | 12:30 | 0.0053779 | 2.92e-05 | 3 | 552 | Unplanned interruptions on the network | Defective Equipment | Wear or shear of pins
|  | INCD-7939-K | Finlayson | Network | FINCB2 | 04/10/2025 | 12:17 | 05/10/2025 | 14:28 | 0.030611 | 1.95e-05 | 2 | 3142 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-7940-K | Finlayson | Network | FINCB2 | 04/10/2025 | 12:46 | 04/10/2025 | 16:33 | 0.0022115 | 9.7e-06 | 1 | 227 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-7959-K | Hoeka | Network | HOECB6 | 05/10/2025 | 02:42 | 05/10/2025 | 04:24 | 0.073536 | 0.0007209 | 74 | 7548 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-338-M | Finlayson | Network | FINCB1 | 05/10/2025 | 09:32 | 05/10/2025 | 12:51 | 0.040266 | 0.0002143 | 22 | 4133 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-7984-K | Wallace Rd | Network | WALCB5 | 06/10/2025 | 09:03 | 06/10/2025 | 15:50 | 0.30136 | 0.0007404 | 76 | 30932 | Planned interruptions on the network | Planned | Transformer Upgrade
|  | INCD-690-L | Weavers | Network | WEACB2 | 07/10/2025 | 11:37 | 07/10/2025 | 14:41 | 0.017926 | 9.74e-05 | 10 | 1840 | Unplanned interruptions on the network | Defective Equipment | Mechanism seized
|  | INCD-123-N | Hampton Downs | Network | HPTCB5 | 13/10/2025 | 08:56 | 13/10/2025 | 16:31 | 0.13951 | 0.000604 | 62 | 14320 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-8206-K | Raglan | Network | RAGCB2 | 14/10/2025 | 15:00 | 14/10/2025 | 15:18 | 0.011749 | 0.0006527 | 67 | 1206 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-346-M | Finlayson | Network | FINCB2 | 17/10/2025 | 09:40 | 17/10/2025 | 11:12 | 0.0017926 | 1.95e-05 | 2 | 184 | Planned interruptions on the network | Planned | New Connections
|  | INCD-380-M | Hoeka | Network | HOECB3 | 21/10/2025 | 08:41 | 21/10/2025 | 11:11 | 0.0058455 | 3.9e-05 | 4 | 600 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-8364-K | Crawford Rd | Network | CRACB4 | 22/10/2025 | 08:20 | 22/10/2025 | 16:17 | 0.0046472 | 9.7e-06 | 1 | 477 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-347-M | Transpower Hamilton | Network | HAMCB2902 | 28/10/2025 | 08:40 | 28/10/2025 | 14:47 | 0.2038 | 0.0005553 | 57 | 20919 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-1169-L | Whatawhata | Network | WHACB6 | 28/10/2025 | 15:22 | 28/10/2025 | 16:51 | 0.038483 | 0.000604 | 62 | 3950 | Unplanned interruptions on the network | Defective Equipment | Faulty joint/connection
|  | INCD-8505-K | Te Uku | Network | TEUCB13 | 29/10/2025 | 09:10 | 29/10/2025 | 15:35 | 0.025915 | 6.82e-05 | 7 | 2660 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-8540-K | Te Uku | Network | NGACB2 | 30/10/2025 | 09:04 | 30/10/2025 | 15:00 | 0.052122 | 0.0001461 | 15 | 5350 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-8720-K | Tranpsower Hamilton | Network | HAMCB2902 | 07/11/2025 | 13:00 | 07/11/2025 | 14:07 | 0.033105 | 0.0010717 | 110 | 3398 | Planned interruptions on the network | Planned | Transformer Upgrade
|  | INCD-8771-K | Ngaruawahia | Network | NGACB3 | 09/11/2025 | 11:12 | 09/11/2025 | 11:38 | 0.0098789 | 0.00038 | 39 | 1014 | Unplanned interruptions on the network | Defective Equipment | Cable termination fails
|  | INCD-8813-K | Gordonton | Network | GORCB13 | 11/11/2025 | 21:56 | 11/11/2025 | 23:28 | 0.0026889 | 2.92e-05 | 3 | 276 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-400-M | Gordonton | Network | GORCB13 | 12/11/2025 | 09:16 | 12/11/2025 | 12:10 | 0.020342 | 0.0001169 | 12 | 2088 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-8882-K | Finlayson Rd | Network | FINCB1 | 13/11/2025 | 09:16 | 13/11/2025 | 17:03 | 0.0045498 | 9.7e-06 | 1 | 467 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-405-M | Horotiu | Network | HORCB5 | 18/11/2025 | 09:05 | 18/11/2025 | 13:43 | 0.11142 | 0.0004189 | 43 | 11436 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-444-M | Hoeka | Network | HOECB2 | 22/11/2025 | 07:30 | 22/11/2025 | 13:37 | 0.28946 | 0.0007891 | 81 | 29711 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-1487-L | Weavers | Network | WEACB6 | 26/11/2025 | 10:09 | 26/11/2025 | 18:33 | 0.037674 | 7.79e-05 | 8 | 3867 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-427-M | Peacockes | Network | PEACB17 | 27/11/2025 | 21:04 | 28/11/2025 | 02:24 | 0.018706 | 5.85e-05 | 6 | 1920 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-9295-K | Gordonton | Network | GORCB12 | 28/11/2025 | 16:35 | 28/11/2025 | 18:55 | 0.001364 | 9.7e-06 | 1 | 140 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-9308-K | MAF | Network | MAFCB1 | 30/11/2025 | 08:02 | 30/11/2025 | 09:23 | 0.0007891 | 9.7e-06 | 1 | 81 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-9316-K | Glasgow | Network | GLACB2 | 30/11/2025 | 21:30 | 30/11/2025 | 23:13 | 0.0030104 | 2.92e-05 | 3 | 309 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-9383-K | Whatawhata | Network | WHACB4 | 03/12/2025 | 18:24 | 04/12/2025 | 12:10 | 0.031157 | 2.92e-05 | 3 | 3198 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-9455-K | Gordonton | Network | GORCB13 | 06/12/2025 | 06:12 | 06/12/2025 | 08:25 | 0.0038873 | 2.92e-05 | 3 | 399 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-1613-L | Te Kauwhata | Network | TEKCB5 | 08/12/2025 | 11:02 | 08/12/2025 | 13:28 | 0.011379 | 7.79e-05 | 8 | 1168 | Unplanned interruptions on the network | Defective Equipment | Wear or shear of pins
|  | INCD-1614-L | Gordonton | Network | GORCB13 | 08/12/2025 | 13:54 | 08/12/2025 | 15:56 | 0.0035658 | 2.92e-05 | 3 | 366 | Unplanned interruptions on the network | Defective Equipment | Split crossarm
|  | INCD-453-M | Latham | Network | LATCB2 | 09/12/2025 | 09:19 | 09/12/2025 | 13:06 | 0.22337 | 0.000984 | 101 | 22927 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-469-M | Hoeka | Network | HOECB3 | 12/12/2025 | 09:11 | 12/12/2025 | 15:42 | 0.1731 | 0.0022505 | 231 | 17768 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-497-M | Whatawhata | Network | WHACB6 | 16/12/2025 | 09:35 | 16/12/2025 | 16:37 | 0.041367 | 0.0001072 | 11 | 4246 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-1664-L | Pukete | Network | PUKCB2 | 18/12/2025 | 06:05 | 18/12/2025 | 17:29 | 0.0066639 | 9.7e-06 | 1 | 684 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-10091-K | Finlayson Rd | Network | WEACB3 | 29/12/2025 | 13:40 | 29/12/2025 | 20:47 | 0.0004374 | 5.85e-05 | 6 | 44.9 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (IN Zone)
|  | INCD-10129-K | Whatawhata | Network | WHACB2 | 29/12/2025 | 17:05 | 30/12/2025 | 00:25 | 0.5483 | 0.0046179 | 474 | 56279 | Unplanned interruptions on the network | Adverse weather | High wind lne break
|  | INCD-10320-K | Te Kauwhata | Network | TEKCB5 | 05/01/2026 | 16:36 | 06/01/2026 | 02:31 | 0.011594 | 1.95e-05 | 2 | 1190 | Unplanned interruptions on the network | Defective Equipment | Intnl insulation failure
|  | INCD-516-M | Finlayson | Network | FINCB4 | 07/01/2026 | 09:31 | 07/01/2026 | 13:44 | 0.043072 | 0.0001851 | 19 | 4421 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-10389-K | Horotiu | Network | HORCB5 | 08/01/2026 | 02:28 | 08/01/2026 | 05:51 | 0.071198 | 0.0003507 | 36 | 7308 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-10398-K | Te Uku | Network | TEUCB11 | 08/01/2026 | 09:01 | 08/01/2026 | 13:44 | 0.1585 | 0.0005943 | 61 | 16269 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-525-M | Raglan | Network | RAGCB6 | 10/01/2026 | 08:14 | 10/01/2026 | 14:53 | 0.0038873 | 9.7e-06 | 1 | 399 | Planned interruptions on the network | Planned | Distribution Transformer Replacement
|  | INCD-10548-K | Chartwell | Network | CHACB9 | 13/01/2026 | 03:17 | 13/01/2026 | 03:40 | 0.028088 | 0.003556 | 365 | 2883 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-532-M | SpringHill Rd | Network | HPTCB4 | 13/01/2026 | 10:30 | 20/01/2026 | 16:05 | 0.0048031 | 9.7e-06 | 1 | 493 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-532-M | SpringHill Rd | Network | HPTCB5 | 13/01/2026 | 10:30 | 20/01/2026 | 16:05 | 0.53872 | 0.0010717 | 110 | 55296 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-10686-K | Te Kauwhata | Network | TEKCB5 | 15/01/2026 | 12:04 | 15/01/2026 | 20:11 | 0.014234 | 2.92e-05 | 3 | 1461 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-1765-L | Finlayson Rd | Network | FINCB3 | 16/01/2026 | 10:04 | 16/01/2026 | 10:21 | 0.0004969 | 2.92e-05 | 3 | 51 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-10914-K | Te Uku | Network | TEUCB12 | 21/01/2026 | 14:08 | 21/01/2026 | 14:33 | 0.014185 | 0.0005651 | 58 | 1456 | Unplanned interruptions on the network | Defective Equipment | Loose connection
|  | INCD-10951-K | Horotiu | Network | KOHCB6 | 21/01/2026 | 22:00 | 22/01/2026 | 00:00 | 0.0058455 | 4.87e-05 | 5 | 600 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-10955-K | Hoeka | Network | HOECB2 | 22/01/2026 | 03:49 | 22/01/2026 | 06:09 | 0.10626 | 0.0007599 | 78 | 10907 | Unplanned interruptions on the network | Defective Equipment | Jumper fails on thru flt
|  | INCD-539-M | Whatawhata | Network | WHACB6 | 23/01/2026 | 09:05 | 23/01/2026 | 15:33 | 0.1173 | 0.0004969 | 51 | 12040 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-11117-K | Hampton Downs | Network | HPTCB5 | 24/01/2026 | 16:15 | 24/01/2026 | 16:30 | 0.0609 | 0.0039847 | 409 | 6251 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-11120-K | Hampton Downs | Network | HPTCB5 | 24/01/2026 | 18:40 | 24/01/2026 | 19:01 | 0.081369 | 0.0039847 | 409 | 8352 | Unplanned interruptions on the network | Vegetation | Tree contact high wind
|  | INCD-10333-K | Whatawhata | Network | WHACB4 | 04/02/2026 | 08:35 | 04/02/2026 | 14:30 | 0.04842 | 0.0001364 | 14 | 4970 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-255-N | Transpower Hamilton | Network | HAMCB2902 | 11/02/2026 | 08:27 | 11/02/2026 | 15:33 | 0.013406 | 0.0033514 | 344 | 1376 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-582-M | Gordonton | Network | GORCB13 | 11/02/2026 | 09:02 | 11/02/2026 | 13:31 | 0.26313 | 0.0010035 | 103 | 27008 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-596-M | Wallace | Network | WALCB6 | 17/02/2026 | 09:15 | 17/02/2026 | 18:39 | 0.032969 | 5.85e-05 | 6 | 3384 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-632-M | Weavers | Network | WEACB6 | 24/02/2026 | 08:09 | 24/02/2026 | 14:55 | 0.34775 | 0.0008671 | 89 | 35694 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-647-M | Peacockes | Network | PEACB12 | 25/02/2026 | 08:03 | 25/02/2026 | 10:42 | 0.029432 | 0.0001851 | 19 | 3021 | Planned interruptions on the network | Planned | New Connections
|  | INCD-12066-K | Weavers | Network | WEACB2 | 25/02/2026 | 18:17 | 25/02/2026 | 21:27 | 0.01666 | 8.77e-05 | 9 | 1710 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-12082-K | Kent St | Network | KENCB4 | 26/02/2026 | 19:04 | 26/02/2026 | 19:18 | 0.0001364 | 9.7e-06 | 1 | 14 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-12133-K | Peacockes Rd | Network | PEACB12 | 02/03/2026 | 09:34 | 02/03/2026 | 13:12 | 0.012792 | 5.85e-05 | 6 | 1313 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-12153-K | Finlayson Rd | Network | FINCB1 | 03/03/2026 | 05:37 | 03/03/2026 | 11:49 | 0.13674 | 0.0040042 | 411 | 14035 | Unplanned interruptions on the network | Defective Equipment | Line break at twist joint
|  | INCD-12235-K | Glasgow | Network | GLACB1 | 06/03/2026 | 08:09 | 06/03/2026 | 10:37 | 0.010064 | 6.82e-05 | 7 | 1033 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-12241-K | Wallace Rd | Network | WALCB6 | 06/03/2026 | 15:51 | 06/03/2026 | 15:51 | 0.0051646 | 0.012393 | 1272 | 530.11 | Unplanned interruptions on the network | Human error | Unintentionally Disabled
|  | INCD-12272-K | Transpower Hamilton | Network | BORCB1 | 09/03/2026 | 06:33 | 09/03/2026 | 07:44 | 0.2417 | 0.0087098 | 894 | 24809 | Unplanned interruptions on the network | Defective Equipment | Loose connection
|  | INCD-12272-K | Transpower Hamilton | Network | BORCB2 | 09/03/2026 | 06:33 | 09/03/2026 | 07:44 | 0.29909 | 0.0059819 | 614 | 30700 | Unplanned interruptions on the network | Defective Equipment | Loose connection
|  | INCD-274-N | Sandwich | Network | SANCB2 | 13/03/2026 | 08:26 | 13/03/2026 | 15:32 | 0.011652 | 0.0017926 | 184 | 1196 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-643-M | Ngaruawahia | Network | NGACB2 | 13/03/2026 | 09:38 | 13/03/2026 | 13:22 | 0.010912 | 4.87e-05 | 5 | 1120 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-11776-K | Avalon | Network | AVACB8 | 16/03/2026 | 08:38 | 16/03/2026 | 16:23 | 0.044894 | 0.0037411 | 384 | 4608 | Planned interruptions on the network | Planned | New Connections
|  | INCD-12461-K | Tasman | Network | TASCB6 | 18/03/2026 | 05:10 | 18/03/2026 | 10:07 | 0.040509 | 0.0001364 | 14 | 4158 | Unplanned interruptions on the network | Defective Equipment | Fuse blow from overload
|  | INCD-12500-K | Horotiu | Network | NGACB6 | 20/03/2026 | 02:21 | 20/03/2026 | 02:35 | 0.012919 | 0.0009353 | 96 | 1326 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-12620-K | Massey St | Network | MASCB13 | 20/03/2026 | 15:35 | 20/03/2026 | 17:01 | 0.18181 | 0.0021141 | 217 | 18662 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-12548-K | Transpower Hamilton | Network | HAMCB2722 | 20/03/2026 | 23:59 | 21/03/2026 | 00:01 | 0.015861 | 0.0055337 | 568 | 1628 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-679-M | Sandwich | Network | SANCB4 | 22/03/2026 | 09:09 | 22/03/2026 | 16:08 | 1.2083 | 0.0028838 | 296 | 124024 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2353-L | Avalon | Network | AVACB1 | 24/03/2026 | 14:10 | 24/03/2026 | 14:40 | 0.020459 | 0.000682 | 70 | 2100 | Planned interruptions on the network | Planned | New Connections
|  | INCD-12652-K | Finlayson Rd | Network | FINCB2 | 26/03/2026 | 07:05 | 26/03/2026 | 13:44 | 0.1876 | 0.0083006 | 852 | 19256 | Unplanned interruptions on the network | Defective Equipment | Hairline crack
|  | INCD-12655-K | Ngaruawahia | Network | NGACB6 | 26/03/2026 | 08:17 | 26/03/2026 | 12:39 | 0.13836 | 0.0009353 | 96 | 14202 | Unplanned interruptions on the network | Defective Equipment | Line break at twist joint
|  | INCD-12872-K | Te Uku | Network | TEUCB11 | 27/03/2026 | 14:30 | 27/03/2026 | 15:47 | 0.0060014 | 7.79e-05 | 8 | 616 | Unplanned interruptions on the network | Defective Equipment | Insulator split
|  | INCD-12871-K | Avalon Dr | Network | AVACB1 | 27/03/2026 | 15:06 | 27/03/2026 | 15:21 | 0.016806 | 0.0011204 | 115 | 1725 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2461-L | Hoeka | Network | HOECB1 | 27/03/2026 | 14:08 | 27/03/2026 | 20:20 | 0.0036242 | 9.7e-06 | 1 | 372 | Unplanned interruptions on the network | Defective Equipment | Twist crossarm
|  | INCD-12753-K | Civic Car Park | Network | CIVCB4 | 28/03/2026 | 08:00 | 28/03/2026 | 14:01 | 0.059653 | 0.0001656 | 17 | 6123 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-680-M | Foreaman Rd | Network | FORCB4 | 28/03/2026 | 08:22 | 28/03/2026 | 15:01 | 0.0077745 | 1.95e-05 | 2 | 798 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-12799-K | Avalon Dr | Network | AVACB3 | 30/03/2026 | 20:42 | 31/03/2026 | 17:51 | 0.67215 | 0.0033027 | 339 | 68992 | Unplanned interruptions on the network | Third_party | Hit by car
|  | INCD-12802-K | Kent St | Network | KENCB4 | 30/03/2026 | 22:55 | 30/03/2026 | 23:53 | 0.026714 | 0.0004676 | 48 | 2742 | Unplanned interruptions on the network | Defective Equipment | Loss or failure of oil
|  | INCD-12813-K | Finlayson Rd | Network | FINCB2 | 31/03/2026 | 11:54 | 31/03/2026 | 13:01 | 0.085481 | 0.0043452 | 446 | 8774 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-772-K | Te Uku | Network | TEUCB11 | 01/04/2025 | 09:04 | 01/04/2025 | 14:37 | 0.23395 | 0.0007209 | 74 | 24013 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-5-L | Weavers | Network | WEACB2 | 03/04/2025 | 14:36 | 03/04/2025 | 16:58 | 0.0013834 | 9.7e-06 | 1 | 142 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-3103-E | Foreman | Network | FORCB3 | 05/04/2025 | 07:08 | 05/04/2025 | 14:12 | 0.0041308 | 9.7e-06 | 1 | 424 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-21-M | Latham | Network | LATCB6 | 06/04/2025 | 09:02 | 06/04/2025 | 14:43 | 0.085364 | 0.0002533 | 26 | 8762 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-1-M | Finlayson | Network | FINCB2 | 09/04/2025 | 08:42 | 09/04/2025 | 13:48 | 0.030942 | 0.0001851 | 19 | 3176 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-1161-K | Weavers | Network | WEACB3 | 10/04/2025 | 17:13 | 10/04/2025 | 20:26 | 0.0075212 | 3.9e-05 | 4 | 772 | Unplanned interruptions on the network | Defective Equipment | Intnl insulation failure
|  | INCD-1190-K | Finlayson Rd | Network | FINCB1 | 11/04/2025 | 09:40 | 11/04/2025 | 12:18 | 0.0015393 | 9.7e-06 | 1 | 158 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-3098-E | Wallace | Private | WALCB6 | 14/04/2025 | 08:31 | 14/04/2025 | 15:24 | 0.028166 | 6.82e-05 | 7 | 2891 | Planned interruptions on the network | Unknown | Mixed Asset Replacement
|  | INCD-22-M | Latham | Network | LATCB6 | 15/04/2025 | 05:02 | 15/04/2025 | 05:53 | 0.011019 | 0.0002533 | 26 | 1131 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-1477-K | Weavers | Network | WEACB2 | 17/04/2025 | 15:01 | 17/04/2025 | 15:11 | 0.039399 | 0.0037703 | 387 | 4044 | Unplanned interruptions on the network | Defective Equipment | Connect/jumper loose
|  | INCD-16-M | Raglan | Network | RAGCB4 | 18/04/2025 | 14:51 | 18/04/2025 | 23:45 | 0.15971 | 0.01288 | 1322 | 16393 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-16-M | Raglan | Network | TEUCB11 | 18/04/2025 | 14:51 | 18/04/2025 | 23:45 | 0.22393 | 0.014789 | 1518 | 22984.87 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-1744-K | Weavers | Network | NGACB6 | 26/04/2025 | 16:02 | 26/04/2025 | 16:44 | 0.036992 | 0.0009255 | 95 | 3797 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-1746-K | Weavers | Network | GLACB6 | 26/04/2025 | 16:02 | 26/04/2025 | 16:32 | 0.22966 | 0.0086611 | 889 | 23573 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-1746-K | Weavers | Network | GLACB8 | 26/04/2025 | 16:02 | 26/04/2025 | 16:32 | 0.013074 | 0.0004676 | 48 | 1342 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-1814-K | Peacockes Rd | Network | PEACB16 | 28/04/2025 | 12:49 | 28/04/2025 | 15:00 | 0.050944 | 0.0003897 | 40 | 5229 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-1919-K | Hoeka | Network | HAMCB2802 | 01/05/2025 | 00:27 | 01/05/2025 | 00:50 | 0.032092 | 0.0034586 | 355 | 3294 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2283-K | Ngaruawahia | Network | NGACB2 | 01/05/2025 | 09:50 | 09/05/2025 | 22:27 | 0.0030397 | 3.9e-05 | 4 | 312 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-17-M | Te Kauwhata | Network | TEKCB6 | 06/05/2025 | 08:38 | 06/05/2025 | 14:50 | 0.14918 | 0.0004384 | 45 | 15312 | Planned interruptions on the network | Planned | New Connections
|  | INCD-2315-K | Te Kauwhata | Network | SPRCB1 | 11/05/2025 | 07:54 | 11/05/2025 | 08:59 | 0 | 9.7e-06 | 1 | 0 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-45-M | Transpower Hamilton | Network | HAMCB2902 | 16/05/2025 | 08:03 | 16/05/2025 | 17:27 | 0.46805 | 0.0008476 | 87 | 48042 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-58-M | Horotiu | Network | HORCB5 | 27/05/2025 | 08:37 | 27/05/2025 | 14:45 | 0.085607 | 0.0002338 | 24 | 8787 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2975-K | Peacockes Rd | Network | PEACB13 | 29/05/2025 | 00:06 | 29/05/2025 | 02:20 | 0.36251 | 0.0039652 | 407 | 37209 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-68-M | Glasgow | Network | GLACB2 | 04/06/2025 | 09:10 | 04/06/2025 | 13:19 | 0.029111 | 0.0001169 | 12 | 2988 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-97-M | Glasgow | Network | GLACB2 | 04/06/2025 | 10:05 | 04/06/2025 | 13:33 | 0.0081058 | 3.9e-05 | 4 | 832 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-81-L | Ngaruawahia | Network | NGACB2 | 04/06/2025 | 15:03 | 04/06/2025 | 16:23 | 0.0031176 | 3.9e-05 | 4 | 320 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-3318-K | Hoeka | Network | HOECB4 | 06/06/2025 | 10:46 | 06/06/2025 | 16:26 | 0.21461 | 0.0019485 | 200 | 22028 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-112-M | Transpower Hamilton | Network | HAMCB2862 | 11/06/2025 | 00:00 | 11/06/2025 | 08:41 | 0.15623 | 0.0095769 | 983 | 16036 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-3508-K | Hoeka | Network | HAMCB2802 | 11/06/2025 | 09:37 | 11/06/2025 | 14:12 | 0.081749 | 0.0003215 | 33 | 8391 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-92-L | Te Uku | Network | TEUCB11 | 12/06/2025 | 08:52 | 12/06/2025 | 09:23 | 0.0012081 | 3.9e-05 | 4 | 124 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-3608-K | Latham Court | Network | LATCB1 | 13/06/2025 | 06:03 | 13/06/2025 | 06:42 | 0.0015198 | 3.9e-05 | 4 | 156 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-3644-K | Latham Court | Private | LATCB1 | 13/06/2025 | 23:01 | 13/06/2025 | 23:22 | 0.0022505 | 0.0001072 | 11 | 231 | Unplanned interruptions on the network | Third_party | Temp Disconnect / safety isolation
|  | INCD-3646-K | Horotiu | Network | HORCB7 | 14/06/2025 | 08:17 | 14/06/2025 | 17:20 | 0.0052902 | 9.7e-06 | 1 | 543 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-3649-K | Simsey | Network | SIMCB2 | 14/06/2025 | 10:37 | 14/06/2025 | 10:50 | 0.0001267 | 9.7e-06 | 1 | 13 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-3653-K | Simsey | Network | SIMCB2 | 14/06/2025 | 13:48 | 14/06/2025 | 13:58 | 9.74e-05 | 9.7e-06 | 1 | 10 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-94-M | Sandwich | Network | SANCB3 | 16/06/2025 | 09:01 | 16/06/2025 | 10:03 | 0.088793 | 0.0014321 | 147 | 9114 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-3780-K | Latham | Network | LATCB1 | 17/06/2025 | 23:07 | 17/06/2025 | 23:22 | 0.0016075 | 0.0001072 | 11 | 165 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-3835-K | Weavers | Network | WEACB6 | 18/06/2025 | 19:07 | 18/06/2025 | 21:32 | 0.062157 | 0.0004287 | 44 | 6380 | Unplanned interruptions on the network | Defective Equipment | Cable short to fuse fram
|  | INCD-3849-K | Te Uku | Network | TEUCB11 | 19/06/2025 | 10:02 | 19/06/2025 | 15:15 | 0.23245 | 0.0007891 | 81 | 23859 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-137-M | Hampton Downs | Network | SPRCB1 | 24/06/2025 | 08:03 | 24/06/2025 | 16:06 | 0 | 9.7e-06 | 1 | 0 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-60-M | Glasgow | Network | GLACB2 | 26/06/2025 | 08:39 | 26/06/2025 | 14:55 | 0.22349 | 0.000604 | 62 | 22940 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-4076-K | Avalon Dr | Network | AVACB3 | 27/06/2025 | 15:57 | 27/06/2025 | 18:06 | 0.33795 | 0.0026012 | 267 | 34688 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-3999-K | Whatawhata | Network | RAGCB5 | 28/06/2025 | 00:00 | 28/06/2025 | 00:12 | 0.017554 | 0.0015003 | 154 | 1801.79 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-4037-K | Latham Court | Network | LATCB1 | 30/06/2025 | 05:01 | 30/06/2025 | 05:21 | 0.0085734 | 0.0004287 | 44 | 880 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-182-M | Te Uku | Network | TEUCB11 | 04/07/2025 | 08:02 | 04/07/2025 | 16:30 | 0.0068003 | 0.0001559 | 16 | 698 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-4184-K | Horotiu | Network | HORCB6 | 04/07/2025 | 15:37 | 04/07/2025 | 20:15 | 0.0081252 | 2.92e-05 | 3 | 834 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-30-N | Weavers | Network | WEACB4 | 07/07/2025 | 21:07 | 07/07/2025 | 22:13 | 0.013503 | 0.0002046 | 21 | 1386 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-4371-K | Gordonton | Network | GORCB13 | 09/07/2025 | 10:16 | 09/07/2025 | 12:55 | 0.019641 | 0.0001461 | 15 | 2016 | Unplanned interruptions on the network | Wildlife | Bird betw line & pole
|  | INCD-162-M | Hoeka | Network | HOECB6 | 10/07/2025 | 10:04 | 10/07/2025 | 16:08 | 0.26521 | 0.0007599 | 78 | 27222 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-4425-K | Te Kauwhata | Network | TEKCB5 | 10/07/2025 | 19:24 | 10/07/2025 | 21:21 | 0.038619 | 0.0016075 | 165 | 3964 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-164-M | Hoeka | Network | HOECB4 | 11/07/2025 | 10:12 | 11/07/2025 | 16:08 | 0.017342 | 4.87e-05 | 5 | 1780 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-4484-K | Weavers | Network | WEACB3 | 11/07/2025 | 13:39 | 11/07/2025 | 21:19 | 0.0044816 | 9.7e-06 | 1 | 460 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-150-M | Raglan | Network | RAGCB6 | 14/07/2025 | 08:34 | 14/07/2025 | 13:40 | 0.032793 | 0.0001072 | 11 | 3366 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-4558-K | Hampton Downs | Network | HPTCB3 | 14/07/2025 | 17:58 | 14/07/2025 | 22:06 | 0.0086708 | 3.9e-05 | 4 | 890 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-4614-K | Weavers | Network | WEACB2 | 16/07/2025 | 02:28 | 16/07/2025 | 03:44 | 0.37922 | 0.010629 | 1091 | 38924 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (IN Zone)
|  | INCD-166-M | Peacockes | Network | PEACB12 | 18/07/2025 | 08:54 | 18/07/2025 | 16:06 | 0.18519 | 0.0004287 | 44 | 19008 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-4748-K | Wallace Rd | Network | WALCB6 | 19/07/2025 | 07:10 | 19/07/2025 | 09:17 | 0.0098886 | 7.79e-05 | 8 | 1015 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-217-M | Peacockes | Network | PEACB16 | 25/07/2025 | 08:38 | 25/07/2025 | 13:39 | 0.020528 | 6.82e-05 | 7 | 2107 | Planned interruptions on the network | Planned | New Connections
|  | INCD-446-L | Sandwich Rd | Network | SANCB4 | 28/07/2025 | 08:52 | 28/07/2025 | 14:57 | 0.47595 | 0.0028838 | 296 | 48853 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-5286-K | Whatawhata | Private | WHACB2 | 01/08/2025 | 11:40 | 01/08/2025 | 11:51 | 0.0001072 | 9.7e-06 | 1 | 11 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-5345-K | Te Kauwhata | Network | TEKCB3 | 04/08/2025 | 09:34 | 04/08/2025 | 15:30 | 0.027747 | 7.79e-05 | 8 | 2848 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-5927-K | Avalon Dr | Private | AVACB4 | 18/08/2025 | 22:24 | 18/08/2025 | 22:36 | 0.011574 | 0.0009645 | 99 | 1188 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-5956-K | Weavers | Network | WEACB3 | 19/08/2025 | 09:38 | 19/08/2025 | 14:28 | 0.0028253 | 9.7e-06 | 1 | 290 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-5969-K | Horotiu | Network | GORCB12 | 19/08/2025 | 20:17 | 19/08/2025 | 20:52 | 0.14626 | 0.0046569 | 478 | 15012.14 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-6043-K | Te Kauwhata | Network | TEKCB5 | 21/08/2025 | 10:01 | 21/08/2025 | 13:11 | 0.011107 | 5.85e-05 | 6 | 1140 | Planned interruptions on the network | Planned | New Connections
|  | INCD-6045-K | Peacockes Rd | Network | PEACB12 | 21/08/2025 | 10:48 | 21/08/2025 | 11:08 | 0.0031955 | 0.0001656 | 17 | 328 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-6069-K | Horotiu | Network | HORCB5 | 21/08/2025 | 18:04 | 21/08/2025 | 23:34 | 0.094522 | 0.0007404 | 76 | 9702 | Unplanned interruptions on the network | Defective Equipment | Mechanism seized
|  | INCD-115-N | Finlayson Rd | Network | WEACB3 | 31/08/2025 | 08:04 | 31/08/2025 | 08:14 | 0.0005437 | 5.85e-05 | 6 | 55.81 | Unplanned interruptions on the network | Vegetation | Tree blown ovr on line (OUT of Zone)
|  | INCD-6422-K | Horotiu | Private | HORCB3 | 31/08/2025 | 18:56 | 31/08/2025 | 19:28 | 0.059498 | 0.0021921 | 225 | 6107 | Unplanned interruptions on the network | Third_party | Temp Disconnect / safety isolation
|  | INCD-6645-K | Peacockes Rd | Network | PEACB17 | 03/09/2025 | 19:29 | 03/09/2025 | 19:31 | 0.0041698 | 0.0020849 | 214 | 428 | Unplanned interruptions on the network | Defective Equipment | Fuse blown on overload
|  | INCD-6673-K | Wallace Rd | Network | WALCB4 | 04/09/2025 | 08:13 | 04/09/2025 | 10:04 | 0.094142 | 0.0012276 | 126 | 9663 | Planned interruptions on the network | Planned | Transformer Upgrade
|  | INCD-280-M | Finlayson | Network | FINCB3 | 05/09/2025 | 09:40 | 05/09/2025 | 15:20 | 0.01325 | 3.9e-05 | 4 | 1360 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-6766-K | Sandwich Rd | Network | SANCB3 | 06/09/2025 | 04:31 | 06/09/2025 | 05:24 | 0.35052 | 0.021774 | 2235 | 35978 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (OUT of Zone)
|  | INCD-6883-K | Kent St | Network | KENCB12 | 09/09/2025 | 09:15 | 09/09/2025 | 09:33 | 0.019417 | 0.0014614 | 150 | 1993 | Unplanned interruptions on the network | Defective Equipment | Cable joint fails
|  | INCD-7010-K | Borman Rd | Network | BORCB1 | 11/09/2025 | 21:11 | 12/09/2025 | 02:18 | 1.6199 | 0.0086611 | 889 | 166270 | Unplanned interruptions on the network | Lightning | Spontaneous failure
|  | INCD-295-M | Chartwell | Network | CHACB9 | 12/09/2025 | 09:11 | 12/09/2025 | 14:27 | 0.095438 | 0.000302 | 31 | 9796 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-342-M | Pukete | Network | PUKCB4 | 18/09/2025 | 09:50 | 18/09/2025 | 17:31 | 0.0044426 | 0.0001169 | 12 | 456 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-7764-K | Gordonton | Network | GORCB11 | 22/09/2025 | 09:06 | 22/09/2025 | 11:48 | 0.014205 | 8.77e-05 | 9 | 1458 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-7766-K | Gordonton | Network | GORCB11 | 22/09/2025 | 09:06 | 22/09/2025 | 11:48 | 0.052083 | 0.0003215 | 33 | 5346 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-7512-K | Peacockes Rd | Network | PEACB12 | 23/09/2025 | 10:05 | 23/09/2025 | 16:18 | 0.77923 | 0.003858 | 396 | 79983 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-7673-K | Transpower Hamilton | Network | HAMCB2782 | 28/09/2025 | 09:30 | 28/09/2025 | 15:56 | 0.16923 | 0.0004384 | 45 | 17370 | Unplanned interruptions on the network | Defective Equipment | Twist crossarm
|  | INCD-7723-K | Finlayson | Network | FINCB2 | 29/09/2025 | 16:05 | 29/09/2025 | 18:34 | 0.0086903 | 5.85e-05 | 6 | 892 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-7728-K | Finlayson | Network | FINCB2 | 29/09/2025 | 16:12 | 30/09/2025 | 13:42 | 0.025126 | 1.95e-05 | 2 | 2579 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-7921-K | Te Kauwhata | Network | FINCB4 | 04/10/2025 | 08:21 | 04/10/2025 | 10:03 | 0.019309 | 0.0011983 | 123 | 1981.91 | Unplanned interruptions on the network | Lightning | Lightning strike surge
|  | INCD-7921-K | Te Kauwhata | Network | WEACB3 | 04/10/2025 | 08:21 | 04/10/2025 | 10:03 | 0.0004159 | 5.85e-05 | 6 | 42.69 | Unplanned interruptions on the network | Lightning | Lightning strike surge
|  | INCD-7996-K | Weavers | Network | WEACB6 | 06/10/2025 | 07:59 | 06/10/2025 | 12:12 | 0.0049297 | 1.95e-05 | 2 | 506 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-8094-K | Finlayson | Network | FINCB1 | 08/10/2025 | 13:51 | 08/10/2025 | 19:06 | 0.018413 | 5.85e-05 | 6 | 1890 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-8157-K | Sandwich | Network | SANCB7 | 12/10/2025 | 08:53 | 12/10/2025 | 19:30 | 0.006206 | 9.7e-06 | 1 | 637 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-8217-K | Glasgow St | Network | GLACB6 | 15/10/2025 | 05:18 | 15/10/2025 | 06:48 | 0.022797 | 0.0002533 | 26 | 2340 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-8235-K | Peacockes Rd | Private | PEACB12 | 15/10/2025 | 13:33 | 15/10/2025 | 13:50 | 0.0004969 | 2.92e-05 | 3 | 51 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-357-M | Kent | Network | KENCB14 | 19/10/2025 | 08:06 | 19/10/2025 | 16:39 | 0.034985 | 6.82e-05 | 7 | 3591 | Planned interruptions on the network | Planned | Subdivision
|  | INCD-8380-K | Finlayson Rd | Network | FINCB4 | 22/10/2025 | 18:45 | 22/10/2025 | 21:38 | 0.0067418 | 3.9e-05 | 4 | 692 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-8397-K | Whatawhata | Network | WHACB3 | 23/10/2025 | 22:30 | 24/10/2025 | 17:03 | 0.15665 | 0.0007891 | 81 | 16079 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-377-M | Whatawhata | Network | WHACB4 | 24/10/2025 | 09:16 | 24/10/2025 | 13:02 | 0.015413 | 6.82e-05 | 7 | 1582 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-1446-L | Raglan | Network | RAGCB6 | 28/10/2025 | 10:13 | 28/10/2025 | 11:17 | 0.0006235 | 9.7e-06 | 1 | 64 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-8505-K | Te Uku | Network | NGACB2 | 29/10/2025 | 09:10 | 29/10/2025 | 15:35 | 0.075017 | 0.0001949 | 20 | 7700 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-384-M | Borman | Network | BORCB5 | 29/10/2025 | 09:24 | 29/10/2025 | 14:51 | 0.30584 | 0.0009353 | 96 | 31392 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-393-M | Te Uku | Network | TEUCB11 | 31/10/2025 | 08:36 | 31/10/2025 | 11:04 | 0.0014419 | 9.7e-06 | 1 | 148 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-8601-K | Horotiu | Network | HORCB3 | 02/11/2025 | 18:04 | 02/11/2025 | 23:46 | 0.0033319 | 9.7e-06 | 1 | 342 | Unplanned interruptions on the network | Defective Equipment | Intnl insulation failure
|  | INCD-8608-K | Transpower Hamilton | Network | HAMCB2902 | 03/11/2025 | 06:00 | 03/11/2025 | 12:42 | 0.24429 | 0.0047933 | 492 | 25074.65 | Planned interruptions on the network | Planned | Transformer Upgrade
|  | INCD-8704-K | Ngaruawahia | Network | NGACB3 | 06/11/2025 | 18:54 | 07/11/2025 | 00:21 | 0.26357 | 0.0008573 | 88 | 27054 | Unplanned interruptions on the network | Defective Equipment | Cable termination fails
|  | INCD-8767-K | Peacockes | Network | PEACB16 | 10/11/2025 | 09:14 | 10/11/2025 | 14:54 | 0.26021 | 0.0017049 | 175 | 26709 | Planned interruptions on the network | Planned | Distribution Transformer Replacement
|  | INCD-8781-K | Weavers | Network | NGACB3 | 11/11/2025 | 07:37 | 11/11/2025 | 07:45 | 0.071929 | 0.0089728 | 921 | 7383 | Unplanned interruptions on the network | Wildlife | Bird betw line & pole
|  | INCD-399-M | Latham | Network | LATCB1 | 13/11/2025 | 09:25 | 13/11/2025 | 13:12 | 0.30741 | 0.0013542 | 139 | 31553 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-8250-K | Avalon | Network | AVACB8 | 15/11/2025 | 08:48 | 15/11/2025 | 15:41 | 0.090703 | 0.0037022 | 380 | 9310 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-431-M | Hoeka | Network | HOECB4 | 15/11/2025 | 09:02 | 15/11/2025 | 16:09 | 0.054081 | 0.0001267 | 13 | 5551 | Planned interruptions on the network | Planned | New Connections
|  | INCD-403-M | Pukete | Network | PUKCB2 | 19/11/2025 | 09:22 | 19/11/2025 | 10:19 | 0.020547 | 0.0003605 | 37 | 2109 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-9129-K | Chartwell | Network | CHACB5 | 20/11/2025 | 14:08 | 20/11/2025 | 15:17 | 0.041445 | 0.0008866 | 91 | 4254 | Unplanned interruptions on the network | Defective Equipment | LV Panel fire
|  | INCD-9180-K | Hampton Downs | Network | HPTCB5 | 22/11/2025 | 10:32 | 22/11/2025 | 16:11 | 0.86443 | 0.0047154 | 484 | 88728 | Unplanned interruptions on the network | Lightning | Spontaneous failure
|  | INCD-1443-L | Avalon Dr | Network | AVACB4 | 23/11/2025 | 13:22 | 23/11/2025 | 14:31 | 0.079996 | 0.0011594 | 119 | 8211 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-1441-L | Latham | Network | LATCB2 | 24/11/2025 | 10:45 | 24/11/2025 | 14:31 | 0.10789 | 0.0004774 | 49 | 11074 | Unplanned interruptions on the network | Defective Equipment | Broken insulator/bush
|  | INCD-440-M | Finlayson | Network | FINCB2 | 03/12/2025 | 09:44 | 03/12/2025 | 14:45 | 0.077979 | 0.0002825 | 29 | 8004 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-9379-K | Te Kauwhata | Network | TEKCB5 | 03/12/2025 | 18:01 | 04/12/2025 | 01:50 | 0.022846 | 4.87e-05 | 5 | 2345 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-9384-K | Gordonton | Network | GORCB13 | 03/12/2025 | 20:02 | 03/12/2025 | 22:29 | 0.0042964 | 2.92e-05 | 3 | 441 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-9403-K | Weavers | Network | WEACB3 | 04/12/2025 | 12:57 | 04/12/2025 | 22:11 | 0.26077 | 0.0076868 | 789 | 26766 | Unplanned interruptions on the network | Vegetation | Tree blown ovr on line (OUT of Zone)
|  | INCD-9475-K | Whatawhata | Network | WHACB4 | 07/12/2025 | 08:43 | 07/12/2025 | 10:32 | 0.0031858 | 2.92e-05 | 3 | 327 | Unplanned interruptions on the network | Defective Equipment | Intnl insulation failure
|  | INCD-9492-K | Borman Rd | Network | CHACB7 | 08/12/2025 | 09:08 | 08/12/2025 | 11:26 | 0.19491 | 0.0019972 | 205 | 20006 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-454-M | Latham | Network | LATCB2 | 09/12/2025 | 09:16 | 09/12/2025 | 12:57 | 0.10335 | 0.0004676 | 48 | 10608 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-9555-K | Chartwell | Network | CHACB7 | 09/12/2025 | 14:01 | 09/12/2025 | 14:44 | 0.012568 | 0.0002923 | 30 | 1290 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-9576-K | Weavers | Network | WEACB2 | 10/12/2025 | 05:18 | 10/12/2025 | 07:07 | 0.011681 | 0.0001072 | 11 | 1199 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-9644-K | Chartwell | Network | CHACB7 | 11/12/2025 | 14:11 | 11/12/2025 | 14:49 | 0.029247 | 0.0007697 | 79 | 3002 | Planned interruptions on the network | Planned | New Connections
|  | INCD-467-M | Borman | Network | BORCB5 | 12/12/2025 | 10:04 | 12/12/2025 | 13:16 | 0.020576 | 0.0001072 | 11 | 2112 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-251-N | Finlayson Rd | Network | FINCB4 | 14/12/2025 | 12:48 | 14/12/2025 | 15:21 | 0.0014906 | 9.7e-06 | 1 | 153 | Unplanned interruptions on the network | Human error | Settings Incorrect
|  | INCD-511-M | Wallace | Network | WALCB6 | 22/12/2025 | 09:13 | 22/12/2025 | 13:59 | 0.011145 | 3.9e-05 | 4 | 1144 | Planned interruptions on the network | Planned | Distribution Transformer Replacement
|  | INCD-10055-K | Gordonton | Network | GORCB13 | 24/12/2025 | 20:27 | 24/12/2025 | 22:46 | 0.0013542 | 9.7e-06 | 1 | 139 | Unplanned interruptions on the network | Defective Equipment | Split crossarm
|  | INCD-10293-K | Weavers | Network | WEACB2 | 29/12/2025 | 00:27 | 29/12/2025 | 00:45 | 0.013858 | 0.0007599 | 78 | 1422.47 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-10296-K | Avalon Dr | Network | AVACB6 | 01/01/2026 | 11:04 | 01/01/2026 | 11:54 | 0.037996 | 0.0007599 | 78 | 3900 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-10251-K | MAF | Network | MAFCB3 | 02/01/2026 | 16:31 | 02/01/2026 | 17:32 | 0.0012276 | 2.92e-05 | 3 | 126 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-10269-K | Te Kauwhata | Network | TEKCB5 | 03/01/2026 | 17:35 | 04/01/2026 | 10:12 | 0.14929 | 0.0005651 | 58 | 15324 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-10355-K | Weavers | Network | WEACB3 | 07/01/2026 | 07:37 | 07/01/2026 | 09:32 | 0.0022408 | 1.95e-05 | 2 | 230 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-10419-K | Tasman | Private | TASCB6 | 09/01/2026 | 07:43 | 09/01/2026 | 10:48 | 0.0018024 | 9.7e-06 | 1 | 185 | Unplanned interruptions on the network | Third_party | Discon of premise
|  | INCD-230-N | Whatawhata | Network | WHACB4 | 12/01/2026 | 09:21 | 12/01/2026 | 14:05 | 0.013834 | 4.87e-05 | 5 | 1420 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-138-N | Te Uku | Network | TEUCB11 | 15/01/2026 | 09:02 | 15/01/2026 | 16:53 | 0.8879 | 0.0021823 | 224 | 91137 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-10685-K | Weavers | Network | WEACB2 | 15/01/2026 | 10:28 | 15/01/2026 | 19:07 | 0.0050564 | 9.7e-06 | 1 | 519 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-11115-K | Hampton Downs | Network | HPTCB5 | 16/01/2026 | 16:52 | 24/01/2026 | 16:08 | 0.0003507 | 1.95e-05 | 2 | 36 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-10891-K | Cobham Dr | Network | COBCB3 | 21/01/2026 | 09:33 | 21/01/2026 | 10:19 | 0.064982 | 0.0014127 | 145 | 6670 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-11025-K | Raglan | Network | RAGCB6 | 22/01/2026 | 12:28 | 22/01/2026 | 15:47 | 0.029081 | 0.0001461 | 15 | 2985 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-557-M | Avalon | Network | AVACB4 | 23/01/2026 | 09:43 | 23/01/2026 | 15:49 | 0.93922 | 0.0026792 | 275 | 96404 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-11124-K | Weavers | Network | WEACB2 | 24/01/2026 | 18:06 | 24/01/2026 | 21:58 | 0.009041 | 3.9e-05 | 4 | 928 | Unplanned interruptions on the network | Defective Equipment | Intnl insulation failure
|  | INCD-11129-K | Claudelands | Network | CLACB10 | 24/01/2026 | 21:55 | 25/01/2026 | 00:16 | 0.83684 | 0.014088 | 1446 | 85896 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-11194-K | Raglan | Network | RAGCB4 | 27/01/2026 | 10:08 | 27/01/2026 | 17:50 | 0.75244 | 0.0063911 | 656 | 77233 | Unplanned interruptions on the network | Defective Equipment | Bus chamber flashovr
|  | INCD-562-M | Avalon | Network | AVACB8 | 28/01/2026 | 09:03 | 28/01/2026 | 15:13 | 0.19105 | 0.0005164 | 53 | 19610 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-1770-L | Raglan | Network | RAGCB4 | 29/01/2026 | 00:17 | 29/01/2026 | 01:12 | 0.085734 | 0.0015588 | 160 | 8800 | Unplanned interruptions on the network | Defective Equipment | Bus chamber flashovr
|  | INCD-11369-K | Te Uku | Network | TEUCB11 | 01/02/2026 | 07:51 | 01/02/2026 | 10:16 | 0.008476 | 5.85e-05 | 6 | 870 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-11452-K | Pukete | Network | KOHCB4 | 04/02/2026 | 09:15 | 04/02/2026 | 09:55 | 0.0035073 | 8.77e-05 | 9 | 360 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-11457-K | Pukete | Network | KOHCB4 | 04/02/2026 | 10:30 | 04/02/2026 | 10:55 | 0.0002436 | 9.7e-06 | 1 | 25 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-11525-K | Weavers | Network | WEACB3 | 07/02/2026 | 03:02 | 07/02/2026 | 04:26 | 0.0024551 | 2.92e-05 | 3 | 252 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-603-M | Hoeka | Network | HOECB4 | 16/02/2026 | 09:59 | 16/02/2026 | 11:14 | 0.0021921 | 2.92e-05 | 3 | 225 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-11888-K | Ngaruawahia | Network | NGACB6 | 19/02/2026 | 09:31 | 19/02/2026 | 16:57 | 0.19428 | 0.0004774 | 49 | 19941 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-264-N | Transpower Hamilton | Network | HAMCB2722 | 20/02/2026 | 08:20 | 20/02/2026 | 16:10 | 0.77843 | 0.0016562 | 170 | 79900 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-11960-K | Kent St | Network | KENCB4 | 21/02/2026 | 10:59 | 21/02/2026 | 11:33 | 0.0003312 | 9.7e-06 | 1 | 34 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-12034-K | Horotiu | Network | HORCB5 | 24/02/2026 | 08:45 | 24/02/2026 | 08:59 | 0.010873 | 0.0040626 | 417 | 1116 | Unplanned interruptions on the network | Defective Equipment | Contact problem
|  | INCD-12067-K | Latham Court | Network | LATCB2 | 25/02/2026 | 18:48 | 25/02/2026 | 19:45 | 0.60527 | 0.013065 | 1341 | 62127 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-12067-K | Latham Court | Network | WALCB2 | 25/02/2026 | 18:48 | 25/02/2026 | 19:45 | 0.2424 | 0.011711 | 1202 | 24881 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-12085-K | Steele Park | Network | STECB8 | 27/02/2026 | 08:15 | 27/02/2026 | 08:39 | 0.026422 | 0.0011009 | 113 | 2712 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-12618-K | Steele Park | Network | STECB3 | 04/03/2026 | 15:04 | 04/03/2026 | 15:57 | 0.10792 | 0.0020362 | 209 | 11077 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-397-M | Borman | Network | BORCB1 | 05/03/2026 | 09:33 | 05/03/2026 | 15:57 | 0.24317 | 0.0006333 | 65 | 24960 | Planned interruptions on the network | Planned | New Connections
|  | INCD-12241-K | Wallace Rd | Network | WALCB1 | 06/03/2026 | 15:51 | 06/03/2026 | 15:51 | 0.0003005 | 0.0007209 | 74 | 30.84 | Unplanned interruptions on the network | Human error | Unintentionally Disabled
|  | INCD-12241-K | Wallace Rd | Network | WALCB2 | 06/03/2026 | 15:51 | 06/03/2026 | 15:51 | 0.0048804 | 0.011711 | 1202 | 500.94 | Unplanned interruptions on the network | Human error | Unintentionally Disabled
|  | INCD-634-M | Ngaruawahia | Network | NGACB3 | 07/03/2026 | 08:29 | 07/03/2026 | 12:01 | 0.18176 | 0.0008573 | 88 | 18656 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-618-M | Ngaruawahia | Network | NGACB2 | 09/03/2026 | 09:31 | 09/03/2026 | 14:50 | 0.19877 | 0.0006235 | 64 | 20402 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-12382-K | Silverdale | Network | HOECB6 | 14/03/2026 | 23:59 | 15/03/2026 | 00:08 | 0.041601 | 0.0058455 | 600 | 4270.05 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-12434-K | Avalon Dr | Network | AVACB1 | 16/03/2026 | 05:08 | 16/03/2026 | 05:49 | 0.061115 | 0.0014906 | 153 | 6273 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-678-M | Whatawhata | Network | WHACB4 | 17/03/2026 | 08:31 | 17/03/2026 | 13:39 | 0.46258 | 0.0015003 | 154 | 47481 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-12487-K | Weavers | Network | WEACB6 | 19/03/2026 | 09:30 | 19/03/2026 | 15:07 | 0.20559 | 0.0006138 | 63 | 21102 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-270-N | Hampton Downs | Network | HPTCB5 | 19/03/2026 | 09:07 | 19/03/2026 | 11:30 | 0.0013932 | 9.7e-06 | 1 | 143 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-12615-K | Chartwell | Network | CHACB9 | 23/03/2026 | 09:56 | 23/03/2026 | 11:19 | 0.0008086 | 9.7e-06 | 1 | 83 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2337-L | Whatawhata | Network | WHACB4 | 24/03/2026 | 09:13 | 24/03/2026 | 11:18 | 0.0012178 | 9.7e-06 | 1 | 125 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-12766-K | Weavers | Network | WEACB2 | 29/03/2026 | 05:32 | 29/03/2026 | 13:15 | 0.12328 | 0.0007599 | 78 | 12654 | Unplanned interruptions on the network | Defective Equipment | Line break at twist joint
|  | INCD-12803-K | Cobham Dr | Network | COBCB9 | 30/03/2026 | 23:16 | 31/03/2026 | 00:28 | 0.0007015 | 9.7e-06 | 1 | 72 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-807-K | Claudelands | Network | HAMCB2722 | 02/04/2025 | 00:09 | 02/04/2025 | 00:16 | 0.016095 | 0.0022992 | 236 | 1652 | Unplanned interruptions on the network | Defective Equipment | Wear or shear of pins
|  | INCD-6-M | Latham | Network | LATCB5 | 02/04/2025 | 09:31 | 02/04/2025 | 17:32 | 1.5244 | 0.0032637 | 335 | 156473 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-1070-K | Silverdale | Network | SILCB1 | 09/04/2025 | 08:45 | 09/04/2025 | 16:06 | 0.12889 | 0.0002923 | 30 | 13230 | Planned interruptions on the network | Planned | New Connections
|  | INCD-1401-K | Weavers | Network | WEACB4 | 17/04/2025 | 10:10 | 17/04/2025 | 19:27 | 0.15652 | 0.0006138 | 63 | 16066 | Unplanned interruptions on the network | Defective Equipment | Connect/jumper loose
|  | INCD-1528-K | Transpower Hamilton | Network | HAMCB2802 | 18/04/2025 | 07:22 | 18/04/2025 | 12:16 | 0.0028643 | 9.7e-06 | 1 | 294 | Unplanned interruptions on the network | Defective Equipment | Split crossarm
|  | INCD-1568-K | Hoeka | Network | HOECB3 | 18/04/2025 | 16:49 | 18/04/2025 | 19:49 | 0.005261 | 2.92e-05 | 3 | 540 | Unplanned interruptions on the network | Defective Equipment | Split crossarm
|  | INCD-1582-K | Weavers | Network | WEACB6 | 19/04/2025 | 08:05 | 19/04/2025 | 09:55 | 0.012831 | 0.0001169 | 12 | 1317 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-1714-K | Hoeka | Network | HOECB4 | 24/04/2025 | 19:16 | 24/04/2025 | 20:22 | 0.01969 | 0.000302 | 31 | 2021 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-1744-K | Weavers | Network | NGACB3 | 26/04/2025 | 16:02 | 26/04/2025 | 16:44 | 0.36408 | 0.0088949 | 913 | 37370.63 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-37-M | Latham | Network | LATCB5 | 29/04/2025 | 09:46 | 29/04/2025 | 16:50 | 0.93587 | 0.002231 | 229 | 96061 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-56-L | Wallace Rd | Network | WALCB6 | 06/05/2025 | 14:19 | 06/05/2025 | 18:28 | 0.0048518 | 1.95e-05 | 2 | 498 | Unplanned interruptions on the network | Defective Equipment | Corroded pin splits insul
|  | INCD-2315-K | Te Kauwhata | Network | FINCB4 | 11/05/2025 | 07:54 | 11/05/2025 | 08:59 | 0.031948 | 0.0011886 | 122 | 3279.23 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-65-L | Latham | Network | LATCB5 | 13/05/2025 | 08:08 | 13/05/2025 | 09:08 | 0.11267 | 0.002231 | 229 | 11565 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-56-M | Whatawhata | Network | WHACB4 | 14/05/2025 | 09:10 | 14/05/2025 | 11:37 | 0.054422 | 0.0003702 | 38 | 5586 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-55-M | Glasgow | Network | GLACB1 | 16/05/2025 | 09:09 | 16/05/2025 | 11:55 | 0.0016173 | 9.7e-06 | 1 | 166 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2583-K | Weavers | Network | WEACB4 | 18/05/2025 | 21:26 | 18/05/2025 | 22:36 | 0.014321 | 0.0002046 | 21 | 1470 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2591-K | Gordonton | Network | GORCB13 | 19/05/2025 | 09:34 | 19/05/2025 | 13:16 | 0.064885 | 0.0002923 | 30 | 6660 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-2699-K | Latham Court | Network | LATCB3 | 21/05/2025 | 09:51 | 21/05/2025 | 14:04 | 0.65899 | 0.0088365 | 907 | 67641 | Unplanned interruptions on the network | Defective Equipment | Wear or shear of pins
|  | INCD-57-M | Horotiu | Network | HORCB5 | 23/05/2025 | 08:33 | 23/05/2025 | 13:20 | 0.10066 | 0.0003507 | 36 | 10332 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-82-M | Horotiu | Network | HORCB6 | 28/05/2025 | 10:00 | 28/05/2025 | 13:03 | 0.081467 | 0.0004579 | 47 | 8362 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-50-M | Transpower Hamilton | Network | HAMCB2902 | 29/05/2025 | 08:36 | 29/05/2025 | 18:47 | 0.27382 | 0.0004482 | 46 | 28106 | Planned interruptions on the network | Planned | Transformer Upgrade
|  | INCD-3088-K | Wallace | Network | WALCB6 | 30/05/2025 | 08:21 | 30/05/2025 | 10:21 | 0.0081837 | 6.82e-05 | 7 | 840 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-3397-K | Pukete | Network | TASCB4 | 09/06/2025 | 09:06 | 09/06/2025 | 12:13 | 0.10245 | 0.0008184 | 84 | 10516 | Planned interruptions on the network | Planned | Distribution Transformer Replacement
|  | INCD-3456-K | Horotiu | Private | NGACB5 | 10/06/2025 | 12:06 | 10/06/2025 | 16:07 | 0.0023479 | 9.7e-06 | 1 | 241 | Unplanned interruptions on the network | Third_party | Temp Disconnect / safety isolation
|  | INCD-3543-K | Transpower Hamilton | Network | HAMCB2862 | 11/06/2025 | 16:04 | 11/06/2025 | 16:30 | 0.03217 | 0.0012373 | 127 | 3302 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-3642-K | Latham | Network | LATCB1 | 13/06/2025 | 21:03 | 13/06/2025 | 21:18 | 0.0005846 | 3.9e-05 | 4 | 60 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-3652-K | Weavers | Network | WEACB3 | 14/06/2025 | 12:38 | 14/06/2025 | 13:50 | 0.0007015 | 9.7e-06 | 1 | 72 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-1950-K | Sandwich | Network | SANCB6 | 18/06/2025 | 09:33 | 18/06/2025 | 15:05 | 0.25705 | 0.0035852 | 368 | 26384 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-3852-K | Glasgow St | Network | GLACB2 | 19/06/2025 | 10:10 | 19/06/2025 | 15:12 | 0.023538 | 7.79e-05 | 8 | 2416 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-134-M | Wallace | Network | WALCB6 | 24/06/2025 | 09:14 | 24/06/2025 | 17:02 | 1.0114 | 0.0021628 | 222 | 103809 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-3412-K | Latham | Network | LATCB3 | 25/06/2025 | 09:02 | 25/06/2025 | 13:48 | 0.45696 | 0.0015978 | 164 | 46904 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-127-M | Peacockes | Network | PEACB18 | 26/06/2025 | 09:31 | 26/06/2025 | 16:19 | 0.22595 | 0.0005748 | 59 | 23192 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-3956-K | Avalon Dr | Network | AVACB3 | 26/06/2025 | 23:55 | 27/06/2025 | 06:15 | 1.6437 | 0.0087001 | 893 | 168714 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-3999-K | Whatawhata | Network | RAGCB3 | 28/06/2025 | 00:00 | 28/06/2025 | 00:12 | 0.008549 | 0.0007307 | 75 | 877.49 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-4075-K | Avalon Dr | Network | AVACB3 | 28/06/2025 | 05:07 | 28/06/2025 | 05:54 | 0.066853 | 0.0014224 | 146 | 6862 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-4065-K | Alexandra St | Network | ALECB15 | 01/07/2025 | 12:31 | 01/07/2025 | 13:58 | 0.020303 | 0.0019777 | 203 | 2084 | Unplanned interruptions on the network | Third_party | Cable hit by digger
|  | INCD-4084-K | Te Uku Wind Farm | Network | NGACB2 | 02/07/2025 | 00:34 | 02/07/2025 | 00:46 | 0.004285 | 0.000341 | 35 | 439.83 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-4084-K | Te Uku Wind Farm | Network | TEUCB13 | 02/07/2025 | 00:34 | 02/07/2025 | 00:46 | 0.0048973 | 0.0003897 | 40 | 502.67 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-5-N | Latham | Network | LATCB1 | 02/07/2025 | 05:02 | 02/07/2025 | 05:29 | 0.017624 | 0.0006527 | 67 | 1809 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-139-M | Hoeka | Network | HOECB1 | 02/07/2025 | 09:40 | 02/07/2025 | 14:31 | 0.31145 | 0.0010717 | 110 | 31968 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-141-M | Transpower Hamilton | Network | HAMCB2802 | 02/07/2025 | 09:45 | 02/07/2025 | 14:15 | 0.21021 | 0.0007989 | 82 | 21577 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-4150-K | Transpower Hamilton | Network | HAMCB2802 | 04/07/2025 | 00:02 | 04/07/2025 | 01:14 | 0.035775 | 0.0004969 | 51 | 3672 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-142-M | Avalon | Network | AVACB3 | 04/07/2025 | 10:05 | 04/07/2025 | 14:55 | 0.7901 | 0.0028448 | 292 | 81098 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-4204-K | Te Kauwhata | Network | TEKCB2 | 05/07/2025 | 17:46 | 05/07/2025 | 22:45 | 0.002913 | 9.7e-06 | 1 | 299 | Unplanned interruptions on the network | Wildlife | Bird betw line & pole
|  | INCD-4213-K | Te Kauwhata | Network | TEKCB5 | 06/07/2025 | 09:53 | 06/07/2025 | 11:43 | 0.0042867 | 3.9e-05 | 4 | 440 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-25-N | Te Kauwhata | Network | TEKCB6 | 06/07/2025 | 21:59 | 07/07/2025 | 01:42 | 0.0043452 | 1.95e-05 | 2 | 446 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-4307-K | Chartwell | Network | CHACB6 | 08/07/2025 | 09:21 | 08/07/2025 | 16:40 | 0.78268 | 0.0017829 | 183 | 80337 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-160-M | Weavers | Network | WEACB3 | 09/07/2025 | 09:56 | 09/07/2025 | 14:22 | 0.036281 | 0.0001364 | 14 | 3724 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-402-L | Latham Court | Network | LATCB1 | 09/07/2025 | 15:01 | 09/07/2025 | 15:37 | 0.02876 | 0.0007989 | 82 | 2952 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-389-L | Horotiu | Network | KOHCB6 | 10/07/2025 | 12:19 | 10/07/2025 | 15:38 | 0.011633 | 5.85e-05 | 6 | 1194 | Unplanned interruptions on the network | Defective Equipment | Intnl insulation failure
|  | INCD-390-L | Killarney Rd | Network | KILCB6 | 10/07/2025 | 13:33 | 10/07/2025 | 13:38 | 0.003215 | 0.000643 | 66 | 330 | Unplanned interruptions on the network | Defective Equipment | Trip mechanism fails
|  | INCD-4434-K | Raglan | Network | RAGCB6 | 11/07/2025 | 08:32 | 11/07/2025 | 11:19 | 0.61579 | 0.0039944 | 410 | 63207 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-157-M | MAF | Network | MAFCB3 | 12/07/2025 | 09:49 | 12/07/2025 | 15:47 | 0.011769 | 3.9e-05 | 4 | 1208 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-176-M | Weavers | Network | WEACB3 | 14/07/2025 | 10:01 | 14/07/2025 | 11:49 | 0.041035 | 0.00038 | 39 | 4212 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-4575-K | Finlayson Rd | Network | FINCB2 | 15/07/2025 | 11:14 | 15/07/2025 | 12:46 | 0.0035852 | 3.9e-05 | 4 | 368 | Unplanned interruptions on the network | Defective Equipment | Split crossarm
|  | INCD-4839-K | Raglan | Network | RAGCB6 | 21/07/2025 | 20:19 | 21/07/2025 | 23:24 | 0.025233 | 0.0001364 | 14 | 2590 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-202-M | Glasgow | Network | GLACB2 | 23/07/2025 | 09:05 | 23/07/2025 | 14:59 | 0.012393 | 3.9e-05 | 4 | 1272 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-5166-K | Ngaruawahia | Network | HORCB6 | 29/07/2025 | 09:03 | 29/07/2025 | 17:13 | 0.033504 | 7.79e-05 | 8 | 3439 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-207-M | Avalon | Network | AVACB8 | 30/07/2025 | 10:14 | 30/07/2025 | 14:42 | 0.18769 | 0.0007209 | 74 | 19265 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-5252-K | Wallace Rd | Network | WALCB4 | 31/07/2025 | 10:28 | 31/07/2025 | 15:58 | 0.35774 | 0.0011691 | 120 | 36720 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-5342-K | Te Kauwhata | Network | TEKCB5 | 04/08/2025 | 09:10 | 04/08/2025 | 11:26 | 0.09536 | 0.0007015 | 72 | 9788 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-153-M | Horotiu | Network | HORCB5 | 05/08/2025 | 08:36 | 05/08/2025 | 15:31 | 0.44384 | 0.0011009 | 113 | 45557 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-5734-K | Raglan | Network | RAGCB2 | 14/08/2025 | 05:19 | 14/08/2025 | 07:36 | 0.030699 | 0.0002241 | 23 | 3151 | Unplanned interruptions on the network | Defective Equipment | Wear or shear of pins
|  | INCD-230-M | Gordonton | Network | GORCB13 | 14/08/2025 | 10:04 | 14/08/2025 | 15:37 | 0.2248 | 0.0007404 | 76 | 23074 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-513-L | Glasgow | Network | GLACB2 | 17/08/2025 | 14:37 | 17/08/2025 | 17:35 | 0.0017342 | 9.7e-06 | 1 | 178 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-522-L | Peacockes Rd | Network | PEACB12 | 18/08/2025 | 00:22 | 18/08/2025 | 00:32 | 0.013571 | 0.0013152 | 135 | 1393 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-58-N | Horotiu | Network | HORCB5 | 18/08/2025 | 08:32 | 18/08/2025 | 11:17 | 0.0048225 | 2.92e-05 | 3 | 495 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-5934-K | Whatawhata | Network | WHACB3 | 19/08/2025 | 06:21 | 19/08/2025 | 12:39 | 0.028663 | 8.77e-05 | 9 | 2942 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-5951-K | Weavers | Network | WEACB2 | 19/08/2025 | 10:10 | 19/08/2025 | 11:56 | 0.0010327 | 9.7e-06 | 1 | 106 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-208-M | Weavers | Network | WEACB2 | 29/08/2025 | 11:05 | 29/08/2025 | 14:47 | 0.14607 | 0.0008768 | 90 | 14993 | Planned interruptions on the network | Planned | Transformer Upgrade
|  | INCD-113-N | Finlayson Rd | Network | FINCB2 | 31/08/2025 | 08:04 | 31/08/2025 | 11:09 | 0.052278 | 0.0002825 | 29 | 5366 | Unplanned interruptions on the network | Vegetation | Tree blown ovr on line (OUT of Zone)
|  | INCD-6378-K | Raglan | Network | RAGCB5 | 31/08/2025 | 16:46 | 01/09/2025 | 05:41 | 0.23385 | 0.000302 | 31 | 24003 | Unplanned interruptions on the network | Adverse weather | Line clash high wind
|  | INCD-6433-K | Wallace | Network | WALCB6 | 31/08/2025 | 17:56 | 31/08/2025 | 20:08 | 0.0090021 | 6.82e-05 | 7 | 924 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (OUT of Zone)
|  | INCD-559-L | Ngaruawahia | Network | NGACB5 | 01/09/2025 | 15:31 | 01/09/2025 | 16:38 | 0.054685 | 0.0008184 | 84 | 5613 | Unplanned interruptions on the network | Vegetation | Tree blown ovr on line (OUT of Zone)
|  | INCD-6774-K | Simsey | Private | SIMCB2 | 06/09/2025 | 08:11 | 06/09/2025 | 15:00 | 0.0039847 | 9.7e-06 | 1 | 409 | Planned interruptions on the network | Planned | External Customer
|  | INCD-6883-K | Kent St | Network | KENCB2 | 09/09/2025 | 09:15 | 09/09/2025 | 09:33 | 0.052532 | 0.0030397 | 312 | 5392 | Unplanned interruptions on the network | Defective Equipment | Cable joint fails
|  | INCD-6883-K | Kent St | Network | NORCB4 | 09/09/2025 | 09:15 | 09/09/2025 | 09:33 | 0.0029204 | 0.0001656 | 17 | 299.76 | Unplanned interruptions on the network | Defective Equipment | Cable joint fails
|  | INCD-6883-K | Kent St | Network | KENCB14 | 09/09/2025 | 09:15 | 09/09/2025 | 09:33 | 0.047358 | 0.0034781 | 357 | 4861 | Unplanned interruptions on the network | Defective Equipment | Cable joint fails
|  | INCD-6943-K | Gordonton | Network | GORCB11 | 10/09/2025 | 09:33 | 10/09/2025 | 15:23 | 0.23339 | 0.0016952 | 174 | 23956 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-312-M | Glasgow | Network | GLACB1 | 11/09/2025 | 08:34 | 11/09/2025 | 13:58 | 0.0031566 | 9.7e-06 | 1 | 324 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-7166-K | Te Uku | Network | TEUCB13 | 15/09/2025 | 10:13 | 15/09/2025 | 10:14 | 9.7e-06 | 9.7e-06 | 1 | 1 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-291-M | Sandwich | Network | SANCB4 | 29/09/2025 | 15:03 | 29/09/2025 | 17:52 | 0.0016465 | 9.7e-06 | 1 | 169 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-7831-K | Peacockes Rd | Network | PEACB12 | 03/10/2025 | 02:21 | 03/10/2025 | 05:13 | 0.12704 | 0.0022213 | 228 | 13040 | Unplanned interruptions on the network | Defective Equipment | faulty line connection
|  | INCD-7921-K | Te Kauwhata | Network | FINCB1 | 04/10/2025 | 08:21 | 04/10/2025 | 10:03 | 0.11982 | 0.0040139 | 412 | 12299 | Unplanned interruptions on the network | Lightning | Lightning strike surge
|  | INCD-7921-K | Te Kauwhata | Network | FINCB3 | 04/10/2025 | 08:21 | 04/10/2025 | 10:03 | 0.037013 | 0.0012373 | 127 | 3799.09 | Unplanned interruptions on the network | Lightning | Lightning strike surge
|  | INCD-7951-K | Hampton Downs | Network | HPTCB5 | 04/10/2025 | 16:52 | 04/10/2025 | 21:00 | 0.0096646 | 3.9e-05 | 4 | 992 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-8099-K | Whatawhata | Network | WHACB5 | 09/10/2025 | 09:04 | 09/10/2025 | 14:42 | 0.016465 | 4.87e-05 | 5 | 1690 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-336-M | Finlayson | Network | FINCB3 | 15/10/2025 | 09:34 | 15/10/2025 | 15:01 | 0.064291 | 0.0002046 | 21 | 6599 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-1036-L | Te Kauwhata | Network | TEKCB6 | 17/10/2025 | 13:37 | 17/10/2025 | 15:23 | 0.0020654 | 1.95e-05 | 2 | 212 | Unplanned interruptions on the network | Third_party | Vehicle hits lines
|  | INCD-8282-K | Weavers | Network | WEACB5 | 17/10/2025 | 17:00 | 17/10/2025 | 19:30 | 0.076761 | 0.0007404 | 76 | 7879 | Unplanned interruptions on the network | Defective Equipment | Insulator split
|  | INCD-8320-K | Transpower Hamilton | Network | HAMCB2762 | 20/10/2025 | 09:11 | 20/10/2025 | 12:52 | 0.11196 | 0.0005066 | 52 | 11492 | Planned interruptions on the network | Planned | Distribution Transformer Replacement
|  | INCD-8353-K | Whatawhata | Network | WHACB6 | 21/10/2025 | 15:43 | 21/10/2025 | 21:25 | 0.20625 | 0.000604 | 62 | 21170 | Unplanned interruptions on the network | Vegetation | Tree blown ovr on line (OUT of Zone)
|  | INCD-8354-K | Finlayson | Network | FINCB4 | 21/10/2025 | 12:33 | 21/10/2025 | 17:20 | 0.01398 | 4.87e-05 | 5 | 1435 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-354-M | Weavers | Network | WEACB4 | 22/10/2025 | 09:13 | 22/10/2025 | 11:43 | 0.017186 | 0.0001169 | 12 | 1764 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-372-M | Borman | Network | BORCB3 | 23/10/2025 | 09:09 | 23/10/2025 | 11:17 | 0.1035 | 0.0008086 | 83 | 10624 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-8407-K | Weavers | Network | WEACB6 | 24/10/2025 | 13:49 | 24/10/2025 | 16:42 | 0.032764 | 0.0002825 | 29 | 3363 | Unplanned interruptions on the network | Third_party | Vehicle hits lines
|  | INCD-1153-L | Te Uku | Network | TEUCB11 | 28/10/2025 | 08:34 | 28/10/2025 | 10:45 | 0.0025525 | 1.95e-05 | 2 | 262 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-390-M | Peacockes | Network | PEACB12 | 30/10/2025 | 10:00 | 30/10/2025 | 13:25 | 0.41111 | 0.0022213 | 228 | 42198 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-8551-K | Glasgow St | Network | GLACB2 | 30/10/2025 | 20:52 | 30/10/2025 | 22:59 | 0.030786 | 0.0002436 | 25 | 3160 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-8608-K | Transpower Hamilton | Network | CLACB16 | 03/11/2025 | 06:00 | 03/11/2025 | 12:42 | 0.0038225 | 0.0007015 | 72 | 392.35 | Planned interruptions on the network | Planned | Transformer Upgrade
|  | INCD-8659-K | Finlayson Rd | Network | FINCB1 | 04/11/2025 | 17:20 | 04/11/2025 | 19:51 | 0.0014711 | 9.7e-06 | 1 | 151 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-395-M | Norton Rd | Network | NORCB1 | 05/11/2025 | 09:03 | 05/11/2025 | 13:14 | 0.41327 | 0.0016465 | 169 | 42419 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-394-M | Finlayson | Network | FINCB4 | 05/11/2025 | 09:17 | 05/11/2025 | 11:29 | 0.01286 | 9.74e-05 | 10 | 1320 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-136-N | Hoeka | Network | HOECB6 | 07/11/2025 | 09:38 | 07/11/2025 | 13:16 | 0.066717 | 0.000341 | 35 | 6848 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-8724-K | Latham Court | Private | LATCB5 | 07/11/2025 | 17:45 | 07/11/2025 | 18:00 | 0.0033612 | 0.0002241 | 23 | 345 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-1400-L | Sandwich | Network | SANCB1 | 08/11/2025 | 07:33 | 08/11/2025 | 16:08 | 0.0050174 | 9.7e-06 | 1 | 515 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-8781-K | Weavers | Network | NGACB6 | 11/11/2025 | 07:37 | 11/11/2025 | 07:45 | 0.0064168 | 0.0009255 | 95 | 658.64 | Unplanned interruptions on the network | Wildlife | Bird betw line & pole
|  | INCD-8864-K | Horotiu | Network | HORCB5 | 13/11/2025 | 09:02 | 13/11/2025 | 10:22 | 0.0023382 | 2.92e-05 | 3 | 240 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-430-M | Finlayson | Network | FINCB2 | 14/11/2025 | 08:33 | 14/11/2025 | 16:10 | 0.2182 | 0.0007989 | 82 | 22397 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-8979-K | Horotiu | Network | HORCB3 | 17/11/2025 | 08:24 | 17/11/2025 | 15:31 | 0.00416 | 9.7e-06 | 1 | 427 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-420-M | Hoeka | Network | HOECB1 | 28/11/2025 | 09:47 | 28/11/2025 | 11:49 | 0.0047543 | 3.9e-05 | 4 | 488 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-9283-K | Whatawhata | Network | WHACB2 | 28/11/2025 | 09:49 | 28/11/2025 | 15:47 | 0.23358 | 0.0006917 | 71 | 23975 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-9288-K | Weavers | Network | WEACB2 | 28/11/2025 | 12:30 | 28/11/2025 | 14:37 | 0.033582 | 0.000263 | 27 | 3447 | Unplanned interruptions on the network | Defective Equipment | Faulty joint/connection
|  | INCD-9303-K | Finlayson Rd | Network | FINCB2 | 29/11/2025 | 09:01 | 29/11/2025 | 14:03 | 0.021891 | 7.79e-05 | 8 | 2247 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-9311-K | MAF | Network | MAFCB4 | 30/11/2025 | 13:50 | 30/11/2025 | 14:52 | 0.0006138 | 9.7e-06 | 1 | 63 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-442-M | Weavers | Network | WEACB3 | 02/12/2025 | 09:09 | 02/12/2025 | 15:15 | 0.043383 | 0.0001754 | 18 | 4453 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-510-M | Transpower Hamilton | Network | HAMCB2722 | 04/12/2025 | 00:09 | 04/12/2025 | 00:37 | 0.064379 | 0.0022992 | 236 | 6608 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-9559-K | Transpower Hamilton | Network | HAMCB2862 | 09/12/2025 | 15:09 | 09/12/2025 | 15:58 | 0.0004774 | 9.7e-06 | 1 | 49 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-9642-K | Peacockes Rd | Network | PEACB16 | 11/12/2025 | 13:39 | 11/12/2025 | 14:34 | 0.14461 | 0.016309 | 1674 | 14843 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-9668-K | Tasman | Network | TASCB4 | 12/12/2025 | 09:09 | 12/12/2025 | 10:23 | 0.011379 | 0.0004774 | 49 | 1168 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-9796-K | Latham | Network | LATCB2 | 17/12/2025 | 07:32 | 17/12/2025 | 13:38 | 0.17116 | 0.0004676 | 48 | 17568 | Planned interruptions on the network | Planned | Transformer Upgrade
|  | INCD-496-M | Finlayson | Network | FINCB2 | 17/12/2025 | 09:16 | 17/12/2025 | 15:13 | 0.030367 | 8.77e-05 | 9 | 3117 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-512-M | Hoeka | Network | HOECB3 | 19/12/2025 | 08:36 | 19/12/2025 | 13:13 | 0.11065 | 0.0003994 | 41 | 11357 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-9944-K | Weavers | Network | WEACB6 | 19/12/2025 | 22:26 | 19/12/2025 | 22:50 | 0.056925 | 0.0025428 | 261 | 5843 | Unplanned interruptions on the network | Defective Equipment | Insulator split
|  | INCD-10141-K | Raglan | Network | RAGCB2 | 29/12/2025 | 16:10 | 29/12/2025 | 23:09 | 0.51814 | 0.0012373 | 127 | 53183 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-10176-K | Avalon Dr | Network | AVACB6 | 30/12/2025 | 08:51 | 30/12/2025 | 18:34 | 0.94951 | 0.001666 | 171 | 97461 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-10201-K | Finlayson Rd | Network | FINCB1 | 29/12/2025 | 16:20 | 30/12/2025 | 20:03 | 0.14582 | 8.77e-05 | 9 | 14967 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-10205-K | Weavers | Network | WEACB6 | 30/12/2025 | 23:48 | 31/12/2025 | 02:16 | 0.027396 | 0.0001851 | 19 | 2812 | Unplanned interruptions on the network | Defective Equipment | Split crossarm
|  | INCD-10219-K | MAF | Network | MAFCB3 | 31/12/2025 | 15:57 | 31/12/2025 | 21:17 | 0.0031176 | 9.7e-06 | 1 | 320 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-10300-K | Finlayson Rd | Network | FINCB2 | 03/01/2026 | 17:10 | 03/01/2026 | 19:27 | 0.0066736 | 4.87e-05 | 5 | 685 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-533-M | Finlayson | Network | FINCB1 | 07/01/2026 | 09:07 | 07/01/2026 | 11:17 | 0.0088657 | 6.82e-05 | 7 | 910 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-10386-K | Te Kauwhata | Network | TEKCB5 | 08/01/2026 | 00:59 | 08/01/2026 | 02:24 | 0.060248 | 0.0007112 | 73 | 6184 | Unplanned interruptions on the network | Defective Equipment | Stay wire/ line clash
|  | INCD-1694-L | Finlayson | Network | FINCB4 | 10/01/2026 | 09:39 | 10/01/2026 | 11:17 | 0.028643 | 0.0002923 | 30 | 2940 | Unplanned interruptions on the network | Defective Equipment | Broken binder
|  | INCD-10453-K | Weavers | Network | WEACB4 | 11/01/2026 | 02:07 | 11/01/2026 | 16:22 | 0.093021 | 0.0022797 | 234 | 9548 | Unplanned interruptions on the network | Defective Equipment | Line break at twist joint
|  | INCD-10512-K | Te Kauwhta | Network | TEKCB6 | 12/01/2026 | 00:14 | 12/01/2026 | 01:52 | 0.0038191 | 3.9e-05 | 4 | 392 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-10516-K | Ngaruawahia | Network | NGACB6 | 12/01/2026 | 06:45 | 12/01/2026 | 09:27 | 0.0063131 | 3.9e-05 | 4 | 648 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-498-M | Claudelands | Network | HAMCB2902 | 13/01/2026 | 22:01 | 14/01/2026 | 03:20 | 0.094931 | 0.004881 | 501 | 9744 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-10710-K | Finlayson Rd | Network | FINCB1 | 16/01/2026 | 08:25 | 16/01/2026 | 09:34 | 0.0040334 | 5.85e-05 | 6 | 414 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-1763-L | Finlason | Network | FINCB4 | 16/01/2026 | 11:20 | 16/01/2026 | 12:04 | 0.0017147 | 3.9e-05 | 4 | 176 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-10730-K | Weavers | Network | WEACB6 | 16/01/2026 | 11:49 | 16/01/2026 | 15:19 | 0.0040919 | 1.95e-05 | 2 | 420 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-1764-L | Finlayson Rd | Network | FINCB3 | 18/01/2026 | 21:42 | 18/01/2026 | 23:13 | 0.0026597 | 2.92e-05 | 3 | 273 | Unplanned interruptions on the network | Defective Equipment | Fuse blown on overload
|  | INCD-534-M | Weavers | Network | WEACB3 | 19/01/2026 | 09:35 | 19/01/2026 | 15:39 | 0.1551 | 0.0004579 | 47 | 15920 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-10802-K | Silverdale | Network | SILCB2 | 19/01/2026 | 11:23 | 19/01/2026 | 12:21 | 0.64829 | 0.011389 | 1169 | 66542 | Unplanned interruptions on the network | Wildlife | Bird betw line & pole
|  | INCD-526-M | Glasgow St | Network | GLACB2 | 20/01/2026 | 09:31 | 20/01/2026 | 17:06 | 0.0088754 | 1.95e-05 | 2 | 911 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-231-N | Wallace | Network | WALCB6 | 23/01/2026 | 09:15 | 23/01/2026 | 16:43 | 0.16819 | 0.00038 | 39 | 17264 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-11069-K | Weavers | Network | WEACB6 | 23/01/2026 | 11:22 | 23/01/2026 | 13:01 | 0.0067516 | 6.82e-05 | 7 | 693 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-11083-K | Finlayson Rd | Network | FINCB2 | 23/01/2026 | 19:38 | 23/01/2026 | 19:57 | 0.03973 | 0.0043452 | 446 | 4078 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-11178-K | Transpower Hamilton | Network | HAMCB2802 | 27/01/2026 | 05:37 | 27/01/2026 | 10:49 | 0.18438 | 0.0055337 | 568 | 18925 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-11450-K | Chartwell | Network | CHACB9 | 04/02/2026 | 09:37 | 04/02/2026 | 11:10 | 0.025087 | 0.000302 | 31 | 2575 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-1775-L | Weavers | Network | WEACB6 | 05/02/2026 | 11:42 | 05/02/2026 | 17:38 | 0.0069367 | 1.95e-05 | 2 | 712 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-11786-K | Hoeka | Network | HOECB6 | 16/02/2026 | 14:16 | 16/02/2026 | 16:04 | 0.10838 | 0.0010035 | 103 | 11124 | Unplanned interruptions on the network | Defective Equipment | Split crossarm
|  | INCD-624-M | Finlayson Rd | Network | FINCB2 | 17/02/2026 | 08:51 | 17/02/2026 | 11:23 | 0.0029617 | 1.95e-05 | 2 | 304 | Planned interruptions on the network | Planned | New Connections
|  | INCD-11872-K | Kent St | Network | KENCB14 | 18/02/2026 | 00:20 | 18/02/2026 | 00:22 | 0.0057981 | 0.0034781 | 357 | 595.13 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-11851-K | Whatawhata | Network | WHACB2 | 18/02/2026 | 09:00 | 18/02/2026 | 14:12 | 0.30781 | 0.0010912 | 112 | 31595 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-11888-K | Ngaruawahia | Network | HORCB5 | 19/02/2026 | 09:31 | 19/02/2026 | 16:57 | 0.005904 | 1.95e-05 | 2 | 606 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-11991-K | Kent St | Network | KENCB4 | 22/02/2026 | 21:19 | 22/02/2026 | 22:01 | 0.0004092 | 9.7e-06 | 1 | 42 | Unplanned interruptions on the network | Defective Equipment | Cable termination fails
|  | INCD-12067-K | Latham Court | Network | LATCB1 | 25/02/2026 | 18:48 | 25/02/2026 | 19:45 | 0.39443 | 0.010366 | 1064 | 40485 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-12067-K | Latham Court | Network | LATCB6 | 25/02/2026 | 18:48 | 25/02/2026 | 19:45 | 0.043588 | 0.0009158 | 94 | 4474 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-12067-K | Latham Court | Network | WALCB3 | 25/02/2026 | 18:48 | 25/02/2026 | 19:45 | 0.13447 | 0.0065859 | 676 | 13802 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-12067-K | Latham Court | Network | WALCB5 | 25/02/2026 | 18:48 | 25/02/2026 | 19:45 | 0.13817 | 0.0076479 | 785 | 14182 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-12208-K | Finlayson Rd | Network | FINCB2 | 05/03/2026 | 10:32 | 05/03/2026 | 13:11 | 0.0015491 | 9.7e-06 | 1 | 159 | Unplanned interruptions on the network | Defective Equipment | Split crossarm
|  | INCD-12241-K | Wallace Rd | Network | WALCB4 | 06/03/2026 | 15:51 | 06/03/2026 | 15:51 | 0.0026717 | 0.0064106 | 658 | 274.23 | Unplanned interruptions on the network | Human error | Unintentionally Disabled
|  | INCD-12248-K | Avalon Dr | Network | AVACB6 | 07/03/2026 | 00:02 | 07/03/2026 | 01:41 | 0.16493 | 0.001666 | 171 | 16929 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-12264-K | Avalon | Network | AVACB6 | 07/03/2026 | 23:08 | 08/03/2026 | 00:34 | 0.14214 | 0.001666 | 171 | 14590 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2043-L | Sandwich Rd | Private | SANCB3 | 10/03/2026 | 14:20 | 10/03/2026 | 14:28 | 0.0080278 | 0.0010035 | 103 | 824 | Unplanned interruptions on the network | Third_party | Temp Disconnect / safety isolation
|  | INCD-633-M | Weavers | Network | WEACB6 | 12/03/2026 | 10:17 | 12/03/2026 | 13:11 | 0.027123 | 0.0001559 | 16 | 2784 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-12351-K | Hoeka | Network | HOECB2 | 12/03/2026 | 23:59 | 13/03/2026 | 00:03 | 0.0037567 | 0.0015296 | 157 | 385.6 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-12352-K | Hoeka | Network | HOECB4 | 12/03/2026 | 23:59 | 13/03/2026 | 00:16 | 0.041852 | 0.0024356 | 250 | 4295.78 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-696-M | Whatawhata | Network | WHACB5 | 17/03/2026 | 09:10 | 17/03/2026 | 11:50 | 0.011711 | 7.79e-05 | 8 | 1202 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-12463-K | Peacockes | Network | PEACB16 | 18/03/2026 | 08:31 | 18/03/2026 | 12:04 | 0.56934 | 0.0028156 | 289 | 58439 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-12621-K | Silverdale | Network | SILCB5 | 18/03/2026 | 13:03 | 18/03/2026 | 13:40 | 0.034966 | 0.000945 | 97 | 3589 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-12619-K | Avalon Dr | Network | AVACB1 | 18/03/2026 | 14:04 | 18/03/2026 | 14:45 | 0.029559 | 0.0007209 | 74 | 3034 | Planned interruptions on the network | Planned | New Connections
|  | INCD-12479-K | Tasman | Network | TASCB6 | 18/03/2026 | 22:39 | 19/03/2026 | 01:43 | 0.013172 | 0.0002143 | 22 | 1352 | Unplanned interruptions on the network | Defective Equipment | Fuse blow from overload
|  | INCD-12500-K | Horotiu | Network | NGACB2 | 20/03/2026 | 02:21 | 20/03/2026 | 02:35 | 0.055776 | 0.0064983 | 667 | 5725 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-12512-K | Massey St | Network | MASCB13 | 20/03/2026 | 08:25 | 20/03/2026 | 10:11 | 0.22346 | 0.0021141 | 217 | 22937 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2270-L | Te Uku | Network | TEUCB11 | 20/03/2026 | 15:13 | 20/03/2026 | 17:57 | 0.0015978 | 9.7e-06 | 1 | 164 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-12012-K | Peacockes | Network | PEACB16 | 21/03/2026 | 09:00 | 21/03/2026 | 15:18 | 0.065645 | 0.0034099 | 350 | 6738 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-12624-K | Hoeka | Network | HOECB3 | 24/03/2026 | 08:57 | 24/03/2026 | 09:22 | 0.21043 | 0.0085539 | 878 | 21599 | Unplanned interruptions on the network | Defective Equipment | Flickers misaligned
|  | INCD-12676-K | Te Uku | Network | TEUCB11 | 26/03/2026 | 14:59 | 26/03/2026 | 15:36 | 0.032579 | 0.0052512 | 539 | 3344 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (OUT of Zone)
|  | INCD-12873-K | Te Uku | Network | TEUCB11 | 27/03/2026 | 15:16 | 27/03/2026 | 15:27 | 0.0013932 | 0.0001267 | 13 | 143 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27 |  | ¹ Extend table as necessary to disclose information for all individual interruptions