## CoverSheet
EDB Information Disclosure Requirements
Information Templates
Schedule 10a
| Company Name | WEL Networks Ltd
| Disclosure Date | 2025-08-31
| Disclosure Year (year ended) | 2025-03-31
Template for Schedule 10a
Prepared 16 February 2024.

## TOC
Table of Contents
Schedule | Schedule name
10a | REPORT ON INTERRUPTIONS

## Instructions
Disclosure Template Instructions
This document forms Schedule 10a to the Electricity Distribution Information Disclosure (Targeted Review 2024) Amendment Determination 2024 [2024] NZCC 2.
The Schedules take the form of templates for use by EDBs when making disclosures under subclause 2.5.1 of the Electricity Distribution Information Disclosure Determination 2012.
Company Name and Dates
To prepare the templates for disclosure, the supplier's company name should be entered in cell C8, the date of the last day of the current (disclosure) year should be entered in cell C12, and the date on which the information is disclosed should be entered in cell C10 of the CoverSheet worksheet.
The cell C12 entry (current year) is used to calculate disclosure years in the column headings that show above some of the tables and in labels adjacent to some entry cells. It is also used to calculate the ‘For year ended’ date in the template title blocks (the title blocks are the light green shaded areas at the top of each template). The cell C8 entry (company name) is used in the template title blocks. Dates should be entered in day/month/year order (Example -"1 April 2023").
Data Entry Cells and Calculated Cells
Data entered into this workbook may be entered only into the data entry cells. Data entry cells are the bordered, unshaded areas (white cells) in each template. Under no circumstances should data be entered into the workbook outside a data entry cell.
In some cases, where the information for disclosure is able to be ascertained from disclosures elsewhere in the workbook, such information is disclosed in a calculated cell.
Validation Settings on Data Entry Cells
To maintain a consistency of format and to help guard against errors in data entry, some data entry cells test keyboard entries for validity and accept only a limited range of values. For example, entries may be limited to a list of category names, to values between 0% and 100%, or either a numeric entry or the text entry “N/A”. Where this occurs, a validation message will appear when data is being entered. These checks are applied to keyboard entries only and not, for example, to entries made using Excel’s copy and paste facility.
Inserting Additional Rows and Columns
The schedule 10a template may require additional rows to be inserted in tables marked 'include additional rows if needed' or similar. Column A schedule references should not be entered in additional rows, and should be deleted from additional rows that are created by copying and pasting rows that have schedule references.
Additional rows in the schedule 10a template must not be inserted directly above the first row or below the last row of a table. This is to ensure that entries made in the new row are included in the totals.
Description of Calculation References
Calculation cell formulas contain links to other cells within the same template or elsewhere in the workbook. Key cell references are described in a column to the right of each template. These descriptions are provided to assist data entry. Cell references refer to the row of the template and not the schedule reference.

## S10a.Interruptions
[15 empty] | Company Name | WEL Networks Ltd
[15 empty] | For Year Ended | 2025-03-31
SCHEDULE 10a: REPORT ON INTERRUPTIONS
This schedule requires raw interruption data for the disclosure year. SAIDI and SAIFI is to be recorded using the multi-count approach.Where multiple feeders are affected, the interruption record is to be split into multiple interruptions, ie, one interruption record per feeder. This information is part of audited disclosure information (as defined in section 1.4 of this ID determination), and so is subject to the assurance report required by section 2.8.
sch ref
7 | 10a(i): Raw interruption data
8 |  | Interruption identifier | Circuit location | Sub-network (where applicable) | Feeder(s) affected by interruption | Start date (dd/mm/yyyy) | Start time (hh:mm:ss) | End date (dd/mm/yyyy) | End time (hh:mm:ss) | SAIDI value | SAIFI value | Number of ICPs interrupted | ICP interruption minutes | Planned or unplanned interruption (Class B or C) | Cause | Any explanation to help clarify the context of the interruption, including what the cause is if recorded as 'Other cause'
9 |  | INCD-171050-F | Whatawhata | Network | WHACB2 | 02/04/2024 | 21:13 | 03/04/2024 | 00:41 | 0.5962 | 0.0029065 | 295 | 60512 | Unplanned interruptions on the network | Defective Equipment | Faulty joint/connection
10 |  | INCD-2281-E | Hoeka | Network | HOECB3 | 03/04/2024 | 09:16 | 03/04/2024 | 16:44 | 0.044139 | 9.85e-05 | 10 | 4480 | Planned interruptions on the network | Planned | Mixed Asset Replacement
11 |  | INCD-2279-E | Hoeka | Network | HOECB1 | 03/04/2024 | 09:20 | 03/04/2024 | 12:23 | 0.005409 | 2.96e-05 | 3 | 549 | Planned interruptions on the network | Planned | Crossarm Replacement
12 |  | INCD-171200-F | Te Uku | Network | TEUCB12 | 06/04/2024 | 14:16 | 06/04/2024 | 14:34 | 0.0097737 | 0.0005714 | 58 | 992 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-171184-F | Raglan | Network | RAGCB5 | 07/04/2024 | 06:33 | 07/04/2024 | 08:34 | 0.039647 | 0.0004138 | 42 | 4024 | Unplanned interruptions on the network | Wildlife | Bird betw line & pole
|  | INCD-2272-E | Peacockes | Network | PEACB17 | 07/04/2024 | 09:00 | 07/04/2024 | 09:01 | 0.0069362 | 0.0047292 | 480 | 704 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-171197-F | Weavers | Private | WEACB3 | 07/04/2024 | 22:53 | 07/04/2024 | 23:09 | 0.0006306 | 3.94e-05 | 4 | 64 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-171235-F | Avalon Dr | Network | AVACB4 | 09/04/2024 | 08:05 | 09/04/2024 | 15:30 | 0.48959 | 0.0011429 | 116 | 49692 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2289-E | Hoeka | Network | HOECB6 | 09/04/2024 | 09:05 | 09/04/2024 | 14:54 | 0.11893 | 0.0003448 | 35 | 12071 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-171266-F | Wallace | Network | WALCB6 | 10/04/2024 | 06:09 | 10/04/2024 | 07:22 | 0.0014385 | 1.97e-05 | 2 | 146 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-171390-F | Te Kauwhata | Network | HPTCB3 | 11/04/2024 | 14:46 | 12/04/2024 | 14:06 | 0.0055507 | 0.0003547 | 36 | 563.38 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-171390-F | Te Kauwhata | Network | FINCB36 | 11/04/2024 | 14:46 | 12/04/2024 | 14:06 | 0.0004862 | 2.96e-05 | 3 | 49.35 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2286-E | Transpower Hamilton | Network | HAMCB2802 | 12/04/2024 | 09:08 | 12/04/2024 | 15:13 | 0.025301 | 7.88e-05 | 8 | 2568 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-2349-E | Ngaruawahia | Network | NGACB5 | 16/04/2024 | 09:04 | 16/04/2024 | 15:15 | 0.003606 | 9.9e-06 | 1 | 366 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-171599-F | Glasgow | Network | GLACB2 | 18/04/2024 | 11:35 | 18/04/2024 | 13:11 | 0.0037834 | 3.94e-05 | 4 | 384 | Unplanned interruptions on the network | Third_party | High vehicle contact
|  | INCD-171629-F | Gordonton | Network | GORCB11 | 20/04/2024 | 06:18 | 20/04/2024 | 07:26 | 0.0053598 | 7.88e-05 | 8 | 544 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-171784-F | Peacockes | Private | PEACB12 | 29/04/2024 | 18:58 | 29/04/2024 | 19:08 | 0.0006897 | 6.9e-05 | 7 | 70 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-2357-E | Sandwich | Network | CHACB5 | 01/05/2024 | 20:09 | 02/05/2024 | 02:59 | 0.024178 | 5.91e-05 | 6 | 2454 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-2336-E | Te Kauwhata | Network | TEKCB3 | 02/05/2024 | 09:06 | 02/05/2024 | 11:54 | 0.0082761 | 4.93e-05 | 5 | 840 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-171878-F | Hoeka | Network | HOECB6 | 02/05/2024 | 09:06 | 02/05/2024 | 12:29 | 0.13684 | 0.0006995 | 71 | 13889 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-172004-F | Claudelands | Network | CLACB3 | 06/05/2024 | 08:00 | 06/05/2024 | 08:16 | 0.014976 | 0.000936 | 95 | 1520 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2348-E | Te Kauwhata | Network | TEKCB5 | 06/05/2024 | 09:01 | 06/05/2024 | 10:37 | 0.024592 | 0.0002562 | 26 | 2496 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-172109-F | Avalon Dr | Network | AVACB8 | 08/05/2024 | 09:41 | 08/05/2024 | 15:37 | 0.34259 | 0.00267 | 271 | 34772 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-172152-F | Transpower Hamilton | Network | HAMCB2742 | 08/05/2024 | 15:17 | 08/05/2024 | 16:31 | 0.068672 | 0.0009853 | 100 | 6970 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2346-E | Sandwich | Network | NORCB1 | 09/05/2024 | 08:02 | 09/05/2024 | 13:43 | 0.30237 | 0.0008867 | 90 | 30690 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2366-E | Avalon | Network | AVACB6 | 09/05/2024 | 08:12 | 09/05/2024 | 16:45 | 0.37514 | 0.0022267 | 226 | 38076 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-172215-F | Te Uku | Network | TEUCB11 | 10/05/2024 | 02:00 | 10/05/2024 | 04:02 | 0.0071726 | 6.9e-05 | 7 | 728 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-172215-F | Te Uku | Network | TEUCB12 | 10/05/2024 | 02:00 | 10/05/2024 | 04:02 | 0.32779 | 0.0026799 | 272 | 33269.74 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2418-E | Horotiu | Network | HORCB3 | 12/05/2024 | 09:34 | 12/05/2024 | 14:00 | 0.047814 | 0.0001971 | 20 | 4853 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-172363-F | Weavers | Network | WEACB3 | 14/05/2024 | 08:58 | 14/05/2024 | 15:07 | 0.010907 | 2.96e-05 | 3 | 1107 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-172435-F | Weavers | Network | WEACB5 | 15/05/2024 | 13:45 | 15/05/2024 | 18:59 | 0.10419 | 0.0004631 | 47 | 10575 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-172466-F | Borman Rd | Network | BORCB7 | 16/05/2024 | 09:45 | 16/05/2024 | 13:33 | 0.42799 | 0.0075372 | 765 | 43439.26 | Unplanned interruptions on the network | Defective Equipment | Flashovr on cable bush
|  | INCD-172466-F | Borman Rd | Network | CHACB5 | 16/05/2024 | 09:45 | 16/05/2024 | 13:33 | 0.19357 | 0.003409 | 346 | 19647.04 | Unplanned interruptions on the network | Defective Equipment | Flashovr on cable bush
|  | INCD-17589-G | Te Uku | Private | TEUCB11 | 19/05/2024 | 14:45 | 19/05/2024 | 19:50 | 0.009015 | 2.96e-05 | 3 | 915 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-172658-F | Whatawhata | Network | WHACB2 | 21/05/2024 | 11:01 | 21/05/2024 | 15:41 | 0.30458 | 0.0046208 | 469 | 30914 | Unplanned interruptions on the network | Wildlife | Bird lne clash/break
|  | INCD-172917-F | Te Uku | Network | TEUCB11 | 26/05/2024 | 13:30 | 26/05/2024 | 23:33 | 0.024168 | 0.0004926 | 50 | 2453 | Unplanned interruptions on the network | Defective Equipment | Broken binder
|  | INCD-172913-F | Horotiu | Network | NGACB2 | 26/05/2024 | 14:44 | 26/05/2024 | 14:46 | 0.0030926 | 0.001734 | 176 | 313.89 | Unplanned interruptions on the network | Adverse weather | High wind lne break
|  | INCD-172893-F | Weavers | Network | WEACB3 | 27/05/2024 | 01:29 | 27/05/2024 | 05:18 | 0.031587 | 0.0001379 | 14 | 3206 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-17594-G | Weavers | Network | WEACB3 | 27/05/2024 | 12:08 | 27/05/2024 | 16:35 | 0.0052612 | 1.97e-05 | 2 | 534 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-172978-F | Gordonton | Private | GORCB12 | 28/05/2024 | 14:19 | 28/05/2024 | 14:31 | 0.0003547 | 2.96e-05 | 3 | 36 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-173022-F | Weavers | Network | WEACB2 | 29/05/2024 | 09:55 | 29/05/2024 | 13:01 | 0.35382 | 0.0020789 | 211 | 35912 | Unplanned interruptions on the network | Vegetation | Tree contact high wind
|  | INCD-173047-F | Gordonton | Network | GORCB13 | 29/05/2024 | 12:09 | 29/05/2024 | 22:47 | 0.034247 | 5.91e-05 | 6 | 3476 | Unplanned interruptions on the network | Adverse weather | Pole blown over
|  | INCD-173079-F | Whatawhata | Network | RAGCB4 | 29/05/2024 | 14:19 | 29/05/2024 | 14:38 | 0.12778 | 0.0065027 | 660 | 12968.94 | Unplanned interruptions on the network | Adverse weather | Wind line clash
|  | INCD-173082-F | Pukete | Network | PUKCB10 | 29/05/2024 | 14:25 | 29/05/2024 | 14:28 | 0.90448 | 0.0013104 | 133 | 91802.22 | Unplanned interruptions on the network | Adverse weather | High wind lne break
|  | INCD-173091-F | Transpower Hamilton | Network | BORCB1 | 29/05/2024 | 14:31 | 29/05/2024 | 19:03 | 0.89516 | 0.0087589 | 889 | 90856 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (IN Zone)
|  | INCD-173091-F | Transpower Hamilton | Network | BORCB5 | 29/05/2024 | 14:31 | 29/05/2024 | 19:03 | 1.8382 | 0.012335 | 1252 | 186576.67 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (IN Zone)
|  | INCD-173101-F | Te Uku Wind Farm | Network | RAGCB5 | 29/05/2024 | 14:42 | 30/05/2024 | 21:19 | 2.7437 | 0.0015173 | 154 | 278473 | Unplanned interruptions on the network | Lightning | Lightning strike surge
|  | INCD-173102-F | Te Uku | Network | RAGCB4 | 29/05/2024 | 14:50 | 31/05/2024 | 17:05 | 0.016567 | 0.0025419 | 258 | 1681.45 | Unplanned interruptions on the network | Vegetation | Tree blown ovr on line (OUT of Zone)
|  | INCD-2485-E | Weavers | Network | WEACB6 | 29/05/2024 | 15:18 | 29/05/2024 | 16:29 | 0.0006995 | 9.9e-06 | 1 | 71 | Unplanned interruptions on the network | Adverse weather | Line clash high wind
|  | INCD-173196-F | Weavers | Network | WEACB6 | 29/05/2024 | 18:16 | 30/05/2024 | 17:45 | 5.4674 | 0.0057342 | 582 | 554926.09 | Unplanned interruptions on the network | Vegetation | Tree blown ovr on line (OUT of Zone)
|  | INCD-173215-F | Weavers | Network | WEACB5 | 29/05/2024 | 20:48 | 29/05/2024 | 20:53 | 0.029479 | 0.0057046 | 579 | 2992 | Unplanned interruptions on the network | Adverse weather | Line clash high wind
|  | INCD-2487-E | Horotiu | Network | HORCB4 | 30/05/2024 | 06:38 | 30/05/2024 | 13:55 | 0.030139 | 6.9e-05 | 7 | 3059 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (IN Zone)
|  | INCD-173301-F | Pukete | Network | PUKCB10 | 30/05/2024 | 12:55 | 30/05/2024 | 16:08 | 0.086879 | 0.0023843 | 242 | 8818 | Unplanned interruptions on the network | Defective Equipment | Faulty joint/connection
|  | INCD-173389-F | Te Kauwhata | Network | TEKCB5 | 31/05/2024 | 10:13 | 31/05/2024 | 15:47 | 0.0034779 | 9.9e-06 | 1 | 353 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-173622-F | Sandwich Rd | Network | SANCB4 | 02/06/2024 | 10:26 | 02/06/2024 | 10:49 | 0.030592 | 0.0013301 | 135 | 3105 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-173487-F | Raglan | Network | RAGCB3 | 02/06/2024 | 13:09 | 02/06/2024 | 15:34 | 0.0014286 | 9.9e-06 | 1 | 145 | Unplanned interruptions on the network | Defective Equipment | Faulty joint/connection
|  | INCD-173499-F | Te Uku | Network | RAGCB4 | 03/06/2024 | 05:28 | 03/06/2024 | 07:00 | 0.58524 | 0.0065027 | 660 | 59400 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-173499-F | Te Uku | Network | RAGCB6 | 03/06/2024 | 05:28 | 03/06/2024 | 07:00 | 0.86544 | 0.009616 | 976 | 87840 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-173499-F | Te Uku | Network | TEUCB1 | 03/06/2024 | 05:28 | 03/06/2024 | 07:00 | 0.0008867 | 9.9e-06 | 1 | 90 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-173624-F | Whitiora School | Network | WHICB4 | 04/06/2024 | 17:22 | 04/06/2024 | 22:30 | 0.013123 | 0.0029163 | 296 | 1332 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-173657-F | Whatawhata | Network | WHACB2 | 06/06/2024 | 08:10 | 06/06/2024 | 12:59 | 0.0028474 | 9.9e-06 | 1 | 289 | Planned interruptions on the network | Planned | New Connections
|  | INCD-173665-F | Transpower Hamilton | Network | HAMCB2802 | 06/06/2024 | 09:02 | 06/06/2024 | 13:50 | 0.233 | 0.0008079 | 82 | 23649 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2467-E | Finlayson | Network | FINCB1 | 14/06/2024 | 09:06 | 14/06/2024 | 11:15 | 0.03474 | 0.0005419 | 55 | 3526 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-174015-F | Ngaruawahia | Network | NGACB6 | 15/06/2024 | 18:13 | 15/06/2024 | 20:02 | 0.024277 | 0.0003153 | 32 | 2464 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-17606-G | Finlayson Rd | Private | FINCB2 | 18/06/2024 | 11:54 | 18/06/2024 | 12:11 | 0.0001675 | 9.9e-06 | 1 | 17 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-2495-E | Glasgow | Network | GLACB2 | 19/06/2024 | 09:24 | 19/06/2024 | 13:00 | 0.029794 | 0.0001379 | 14 | 3024 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-174229-F | Gordonton | Network | GORCB13 | 20/06/2024 | 17:21 | 20/06/2024 | 20:06 | 0.08619 | 0.0005222 | 53 | 8748 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-2504-E | Gordonton | Network | GORCB11 | 21/06/2024 | 09:16 | 21/06/2024 | 14:28 | 0.052258 | 0.0001675 | 17 | 5304 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-174297-F | Te Kauwhata | Network | TEKCB5 | 23/06/2024 | 12:52 | 23/06/2024 | 21:52 | 0.29884 | 0.0005714 | 58 | 30331 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-174374-F | Tasman | Network | TASCB1 | 25/06/2024 | 19:01 | 25/06/2024 | 19:55 | 0.0069165 | 0.0001281 | 13 | 702 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-174443-F | Finlayson | Network | FINCB2 | 27/06/2024 | 07:39 | 27/06/2024 | 13:18 | 0.00668 | 1.97e-05 | 2 | 678 | Unplanned interruptions on the network | Wildlife | Rodent on HV terminals
|  | INCD-174515-F | Weavers | Network | WEACB3 | 30/06/2024 | 22:18 | 30/06/2024 | 23:04 | 0.040583 | 0.0008867 | 90 | 4119 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-2532-E | Glasgow | Network | GLACB2 | 02/07/2024 | 13:11 | 02/07/2024 | 14:28 | 0.019646 | 0.0002759 | 28 | 1994 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2532-E | Glasgow | Network | WEACB3 | 02/07/2024 | 13:11 | 02/07/2024 | 14:28 | 0.0006995 | 9.9e-06 | 1 | 71 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-174625-F | Hoeka | Network | HOECB3 | 02/07/2024 | 13:05 | 02/07/2024 | 19:54 | 0.044326 | 0.0001084 | 11 | 4499 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-174720-F | Finlayson | Network | FINCB1 | 05/07/2024 | 11:23 | 05/07/2024 | 16:45 | 0.12495 | 0.0005123 | 52 | 12682 | Unplanned interruptions on the network | Defective Equipment | Line break at twist joint
|  | INCD-174883-F | Ngaruawahia | Network | NGACB2 | 08/07/2024 | 05:07 | 08/07/2024 | 06:48 | 0.09155 | 0.0009064 | 92 | 9292 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-2538-E | Transpower Hamilton | Network | HAMCB2822 | 09/07/2024 | 09:08 | 09/07/2024 | 13:59 | 0.51526 | 0.001803 | 183 | 52297 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-174892-F | Ngaruawahia | Network | NGACB2 | 09/07/2024 | 13:09 | 09/07/2024 | 13:53 | 0.039883 | 0.0009064 | 92 | 4048 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-174922-F | Hoeka | Network | HOECB3 | 10/07/2024 | 09:03 | 10/07/2024 | 15:04 | 0.029607 | 0.0007882 | 80 | 3005 | Planned interruptions on the network | Planned | Transformer Upgrade
|  | INCD-2545-E | Hoeka | Network | HOECB3 | 16/07/2024 | 08:49 | 16/07/2024 | 14:36 | 0.034188 | 9.85e-05 | 10 | 3470 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2551-E | Weavers | Network | WEACB3 | 16/07/2024 | 09:14 | 16/07/2024 | 13:59 | 0.0056159 | 1.97e-05 | 2 | 570 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-175245-F | Transpower Hamilton | Network | HAMCB2862 | 16/07/2024 | 18:04 | 17/07/2024 | 11:44 | 0.010444 | 9.9e-06 | 1 | 1060 | Unplanned interruptions on the network | Vegetation | Tree growns in line
|  | INCD-2567-E | Hampton Downs | Network | HPTCB5 | 18/07/2024 | 09:12 | 18/07/2024 | 13:36 | 0.065027 | 0.0002463 | 25 | 6600 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-175428-F | Avalon Dr | Network | AVACB8 | 22/07/2024 | 06:25 | 22/07/2024 | 16:17 | 0.064012 | 0.0001084 | 11 | 6497 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-17631-G | Te Kauwhata | Network | TEKCB3 | 23/07/2024 | 02:17 | 23/07/2024 | 03:23 | 0.0013005 | 1.97e-05 | 2 | 132 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-175488-F | Weavers | Network | WEACB3 | 23/07/2024 | 13:39 | 23/07/2024 | 14:21 | 0.0004138 | 9.9e-06 | 1 | 42 | Unplanned interruptions on the network | Wildlife | Bird betw line & pole
|  | INCD-2565-E | Glasgow | Network | GLACB2 | 24/07/2024 | 09:39 | 24/07/2024 | 13:08 | 0.085756 | 0.0004335 | 44 | 8704 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2591-E | Kent | Network | KENCB4 | 30/07/2024 | 09:06 | 30/07/2024 | 12:48 | 0.0021873 | 9.9e-06 | 1 | 222 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-175663-F | Weavers | Network | WEACB3 | 31/07/2024 | 10:27 | 31/07/2024 | 15:44 | 0.18798 | 0.0006798 | 69 | 19079 | Unplanned interruptions on the network | Defective Equipment | Line break at twist joint
|  | INCD-175805-F | Pukete | Network | PUKCB10 | 03/08/2024 | 07:19 | 03/08/2024 | 08:20 | 0.018966 | 0.0003153 | 32 | 1925 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-175829-F | Te Uku | Network | TEUCB13 | 04/08/2024 | 10:36 | 04/08/2024 | 21:26 | 0.0038324 | 0.0029656 | 301 | 388.98 | Unplanned interruptions on the network | Defective Equipment | Stay wire/ line clash
|  | INCD-175856-F | Finlayson Rd | Network | FINCB3 | 05/08/2024 | 04:27 | 05/08/2024 | 08:17 | 0.040632 | 0.0001773 | 18 | 4124 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-2605-E | Chartwell | Network | CHACB9 | 05/08/2024 | 09:08 | 05/08/2024 | 11:06 | 0.038119 | 0.0003448 | 35 | 3869 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-175952-F | Weavers | Network | WEACB3 | 06/08/2024 | 10:41 | 06/08/2024 | 12:26 | 0.0010345 | 9.9e-06 | 1 | 105 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-2649-E | Whatawhata | Network | WHACB4 | 12/08/2024 | 09:05 | 12/08/2024 | 14:29 | 0.022346 | 6.9e-05 | 7 | 2268 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-176222-F | Transpower Hamilton | Network | HAMCB2802 | 13/08/2024 | 08:14 | 13/08/2024 | 08:32 | 0.051332 | 0.0029163 | 296 | 5210 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-2677-E | Glasgow | Network | GLACB2 | 14/08/2024 | 11:24 | 14/08/2024 | 12:25 | 0.004207 | 6.9e-05 | 7 | 427 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2678-E | Glasgow | Network | GLACB2 | 14/08/2024 | 13:52 | 14/08/2024 | 14:31 | 0.0026897 | 6.9e-05 | 7 | 273 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-176436-F | Gordonton | Network | GORCB13 | 17/08/2024 | 14:06 | 17/08/2024 | 14:15 | 0.0001773 | 1.97e-05 | 2 | 18 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-176617-F | Te Uku | Network | TEUCB2 | 19/08/2024 | 18:20 | 20/08/2024 | 15:12 | 0.0027292 | 4.93e-05 | 5 | 277.01 | Unplanned interruptions on the network | Vegetation | Tree blown ovr on line (OUT of Zone)
|  | INCD-176617-F | Te Uku | Network | TEUCB12 | 19/08/2024 | 18:20 | 20/08/2024 | 15:12 | 0.47012 | 0.0026799 | 272 | 47716.13 | Unplanned interruptions on the network | Vegetation | Tree blown ovr on line (OUT of Zone)
|  | INCD-176633-F | Horotiu | Network | HORCB6 | 19/08/2024 | 21:38 | 20/08/2024 | 00:24 | 0.024533 | 0.0001478 | 15 | 2490 | Unplanned interruptions on the network | Defective Equipment | Internal short
|  | INCD-2667-E | Latham | Network | LATCB6 | 21/08/2024 | 08:42 | 21/08/2024 | 16:43 | 0.018444 | 0.0003153 | 32 | 1872 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-176833-F | Ngaruawahia | Network | NGACB5 | 23/08/2024 | 06:12 | 23/08/2024 | 08:41 | 0.067529 | 0.0004532 | 46 | 6854 | Unplanned interruptions on the network | Defective Equipment | Intnl insulation failure
|  | INCD-2717-E | Transpower Hamilton | Network | HAMCB2902 | 23/08/2024 | 06:31 | 23/08/2024 | 17:31 | 0.43984 | 0.0012217 | 124 | 44642 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-176860-F | Hoeka | Network | HOECB4 | 24/08/2024 | 06:46 | 24/08/2024 | 09:06 | 0.0041381 | 2.96e-05 | 3 | 420 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-176958-F | Foreman Rd | Network | FORCB4 | 27/08/2024 | 10:15 | 27/08/2024 | 22:10 | 0.0070445 | 9.9e-06 | 1 | 715 | Unplanned interruptions on the network | Third_party | Hit by car
|  | INCD-177059-F | Weavers | Network | WEACB3 | 29/08/2024 | 08:14 | 29/08/2024 | 08:24 | 0.0011823 | 0.0001182 | 12 | 120 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2606-E | Whatawhata | Network | WHACB5 | 29/08/2024 | 09:32 | 29/08/2024 | 15:28 | 0.36287 | 0.0011133 | 113 | 36830 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-177152-F | Te Kauwhata | Network | TEKCB5 | 30/08/2024 | 13:03 | 30/08/2024 | 13:22 | 0.0014976 | 7.88e-05 | 8 | 152 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-177175-F | Hoeka | Network | HOECB4 | 31/08/2024 | 12:32 | 31/08/2024 | 20:00 | 0.013242 | 2.96e-05 | 3 | 1344 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-177701-F | Ngaruawahia | Network | NGACB5 | 15/09/2024 | 10:01 | 15/09/2024 | 10:05 | 0.015409 | 0.0038523 | 391 | 1564 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (OUT of Zone)
|  | INCD-2636-E | Borman | Network | BORCB5 | 17/09/2024 | 09:37 | 17/09/2024 | 14:02 | 0.060051 | 0.0002266 | 23 | 6095 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-2693-E | Gordonton | Network | GORCB11 | 19/09/2024 | 09:17 | 19/09/2024 | 15:13 | 0.088515 | 0.0002562 | 26 | 8984 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2770-E | Gordonton | Network | GORCB11 | 20/09/2024 | 09:36 | 20/09/2024 | 14:20 | 0.0083943 | 2.96e-05 | 3 | 852 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-177508-F | Peacockes | Network | PEACB12 | 24/09/2024 | 08:37 | 24/09/2024 | 13:27 | 0.064573 | 0.0002266 | 23 | 6554 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2772-E | Gordonton | Network | GORCB12 | 25/09/2024 | 09:10 | 25/09/2024 | 16:44 | 0.063923 | 0.0001478 | 15 | 6488 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-178114-F | Whatawhata | Network | WHACB3 | 25/09/2024 | 17:03 | 25/09/2024 | 18:52 | 0.0064435 | 5.91e-05 | 6 | 654 | Unplanned interruptions on the network | Defective Equipment | Loss or failure of oil
|  | INCD-178199-F | Te Kauwhata | Private | TEKCB3 | 27/09/2024 | 13:34 | 27/09/2024 | 13:51 | 0.0075076 | 0.0004434 | 45 | 762 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-178325-F | Transpower Hamilton | Network | HAMCB2742 | 01/10/2024 | 22:20 | 02/10/2024 | 04:30 | 0.99156 | 0.0026799 | 272 | 100640 | Unplanned interruptions on the network | Defective Equipment | Broken insulator/bush
|  | INCD-178369-F | Hoeka | Network | HOECB1 | 02/10/2024 | 21:30 | 03/10/2024 | 08:29 | 0.61927 | 0.0010838 | 110 | 62854 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-178373-F | Peacockes Rd | Network | PEACB16 | 03/10/2024 | 08:02 | 03/10/2024 | 09:14 | 0.097855 | 0.0022562 | 229 | 9932 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-178631-F | Finlayson Rd | Network | FINCB2 | 10/10/2024 | 19:02 | 10/10/2024 | 21:30 | 0.043745 | 0.0002956 | 30 | 4440 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-178632-F | Sandwich Rd | Network | SANCB4 | 10/10/2024 | 21:06 | 11/10/2024 | 03:37 | 0.019262 | 4.93e-05 | 5 | 1955 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-178722-F | Peacockes Rd | Network | PEACB18 | 13/10/2024 | 18:05 | 13/10/2024 | 22:07 | 0.057115 | 0.0002365 | 24 | 5797 | Unplanned interruptions on the network | Defective Equipment | Faulty joint/connection
|  | INCD-178004-F | Te Uku | Network | TEUCB11 | 15/10/2024 | 08:33 | 15/10/2024 | 10:27 | 0.039311 | 0.0003448 | 35 | 3990 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-178791-F | Whatawhata | Network | WHACB4 | 15/10/2024 | 10:00 | 15/10/2024 | 10:41 | 0.0012119 | 2.96e-05 | 3 | 123 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-178879-F | Weavers | Network | WEACB2 | 17/10/2024 | 13:20 | 17/10/2024 | 17:28 | 0.018621 | 9.85e-05 | 10 | 1890 | Unplanned interruptions on the network | Third_party | Vehicle hits lines
|  | INCD-178899-F | Whatawhata | Network | WHACB2 | 17/10/2024 | 23:07 | 17/10/2024 | 23:51 | 0.0025518 | 5.91e-05 | 6 | 259 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-179011-F | Bryce St | Network | BRYCB12 | 22/10/2024 | 07:33 | 22/10/2024 | 07:58 | 0.024631 | 0.0009853 | 100 | 2500 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2824-E | Peachgrove | Network | PCHCB1 | 22/10/2024 | 21:05 | 22/10/2024 | 21:09 | 0.0028375 | 0.0007094 | 72 | 288 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2834-E | Wallace | Network | WALCB6 | 24/10/2024 | 10:06 | 24/10/2024 | 13:20 | 0.072633 | 0.0003744 | 38 | 7372 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2833-E | Horotiu | Network | HORCB6 | 25/10/2024 | 09:00 | 25/10/2024 | 16:31 | 0.34196 | 0.0008178 | 83 | 34708 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-179156-F | Weavers | Network | WEACB6 | 26/10/2024 | 16:24 | 26/10/2024 | 20:32 | 0.0048868 | 1.97e-05 | 2 | 496 | Unplanned interruptions on the network | Vegetation | Tree blown ovr on line (OUT of Zone)
|  | INCD-179165-F | Weavers | Network | NGACB6 | 26/10/2024 | 23:59 | 27/10/2024 | 00:35 | 0.017301 | 0.000936 | 95 | 1756 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-179166-F | Weavers | Network | WEACB5 | 27/10/2024 | 00:00 | 27/10/2024 | 21:07 | 0.76339 | 0.0086209 | 875 | 77482 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-179417-F | Pukete | Network | PUKCB5 | 03/11/2024 | 16:54 | 03/11/2024 | 20:33 | 0.081993 | 0.0003744 | 38 | 8322 | Unplanned interruptions on the network | Defective Equipment | Fuse cut out/connection burnt out
|  | INCD-2862-E | Sandwich | Network | SANCB1 | 09/11/2024 | 08:04 | 09/11/2024 | 14:32 | 0.0038228 | 9.9e-06 | 1 | 388 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-179677-F | Finlayson Rd | Network | FINCB4 | 12/11/2024 | 08:27 | 12/11/2024 | 10:04 | 0.0009557 | 9.9e-06 | 1 | 97 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-17673-G | Silverdale | Network | SILCB4 | 12/11/2024 | 10:05 | 12/11/2024 | 15:01 | 0.046662 | 0.0001576 | 16 | 4736 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-179715-F | Hoeka | Network | HOECB2 | 12/11/2024 | 15:40 | 12/11/2024 | 15:45 | 0.0041676 | 0.0007882 | 80 | 423 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-2874-E | Wallace | Network | WALCB6 | 14/11/2024 | 08:00 | 14/11/2024 | 08:57 | 0.0039312 | 6.9e-05 | 7 | 399 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-17675-G | Te Uku | Network | TEUCB12 | 20/11/2024 | 08:32 | 20/11/2024 | 15:54 | 1.1161 | 0.0026799 | 272 | 113285 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-180151-F | Raglan | Private | RAGCB2 | 21/11/2024 | 21:01 | 21/11/2024 | 21:24 | 0.01201 | 0.0005222 | 53 | 1219 | Unplanned interruptions on the network | Third_party | Temp Disconnect / safety isolation
|  | INCD-180010-F | Raglan | Network | RAGCB5 | 22/11/2024 | 01:00 | 22/11/2024 | 01:32 | 0.011527 | 0.0015173 | 154 | 1170 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-180052-F | Sandwich | Network | SANCB7 | 23/11/2024 | 21:06 | 24/11/2024 | 05:22 | 0.077618 | 0.0001675 | 17 | 7878 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-180110-F | Weavers | Network | WEACB4 | 26/11/2024 | 05:37 | 26/11/2024 | 05:52 | 0.0016257 | 0.0001084 | 11 | 165 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-180126-F | Finlayson Rd | Private | FINCB3 | 26/11/2024 | 10:59 | 26/11/2024 | 11:11 | 0.0004729 | 3.94e-05 | 4 | 48 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-180145-F | Raglan | Network | RAGCB6 | 27/11/2024 | 06:57 | 27/11/2024 | 08:15 | 0.31274 | 0.0098032 | 995 | 31742 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-2946-E | Ngaruawahia | Network | NGACB2 | 02/12/2024 | 09:20 | 02/12/2024 | 12:01 | 0.054721 | 0.0003645 | 37 | 5554 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2952-E | Cobham | Network | COBCB11 | 08/12/2024 | 09:01 | 08/12/2024 | 11:18 | 0.05147 | 0.0003744 | 38 | 5224 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2960-E | Hampton Downs | Network | HPTCB5 | 08/12/2024 | 09:34 | 08/12/2024 | 15:25 | 0.10874 | 0.0006109 | 62 | 11037 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2943-E | Wallace | Network | WALCB6 | 09/12/2024 | 10:15 | 09/12/2024 | 13:17 | 0.093244 | 0.0005123 | 52 | 9464 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-17693-G | Gordonton | Network | GORCB13 | 09/12/2024 | 18:27 | 09/12/2024 | 19:18 | 0.0015074 | 2.96e-05 | 3 | 153 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-180661-F | Chartwell | Network | CHACB9 | 14/12/2024 | 09:00 | 14/12/2024 | 15:24 | 0.14162 | 0.0006404 | 65 | 14374 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2939-E | Weavers | Network | WEACB2 | 17/12/2024 | 09:15 | 17/12/2024 | 14:46 | 0.22143 | 0.0006798 | 69 | 22474 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-17703-G | Gordonton | Network | GORCB12 | 18/12/2024 | 05:46 | 18/12/2024 | 06:14 | 0.0002759 | 9.9e-06 | 1 | 28 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-180801-F | Hoeka | Network | HOECB1 | 18/12/2024 | 12:35 | 18/12/2024 | 12:58 | 0.12798 | 0.006276 | 637 | 12990 | Unplanned interruptions on the network | Defective Equipment | Contact problem
|  | INCD-2963-E | Finlayson | Network | FINCB2 | 19/12/2024 | 09:08 | 19/12/2024 | 13:55 | 0.024759 | 8.87e-05 | 9 | 2513 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-180857-F | Gordonton | Network | GORCB13 | 20/12/2024 | 09:49 | 20/12/2024 | 10:51 | 0.0006109 | 9.9e-06 | 1 | 62 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-181028-F | Horotiu | Network | HORCB4 | 29/12/2024 | 08:28 | 29/12/2024 | 11:31 | 0.079332 | 0.0004335 | 44 | 8052 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-181116-F | Transpower Hamilton | Network | HAMCB2902 | 03/01/2025 | 13:02 | 03/01/2025 | 14:16 | 0.16473 | 0.0023547 | 239 | 16720 | Unplanned interruptions on the network | Third_party | Object thrown on line
|  | INCD-2995-E | Horotiu | Network | HORCB6 | 07/01/2025 | 09:05 | 07/01/2025 | 10:58 | 0.0044533 | 3.94e-05 | 4 | 452 | Planned interruptions on the network | Planned | Transformer Upgrade
|  | INCD-2989-E | Weavers | Network | WEACB6 | 08/01/2025 | 09:23 | 08/01/2025 | 13:13 | 0.022661 | 9.85e-05 | 10 | 2300 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-181284-F | Hampton Downs | Network | HPTCB5 | 09/01/2025 | 21:54 | 09/01/2025 | 23:28 | 0.015695 | 0.0001675 | 17 | 1593 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-2885-E | Borman | Network | BORCB2 | 14/01/2025 | 09:31 | 14/01/2025 | 14:23 | 0.014385 | 4.93e-05 | 5 | 1460 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-181437-F | Sandwich Rd | Network | SANCB5 | 15/01/2025 | 08:28 | 15/01/2025 | 09:24 | 0.017104 | 0.0003054 | 31 | 1736 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-181438-F | Te Uku | Network | TEUCB11 | 15/01/2025 | 08:29 | 15/01/2025 | 14:10 | 0.19318 | 0.000601 | 61 | 19607 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-181443-F | Hoeka | Network | HOECB4 | 15/01/2025 | 09:00 | 15/01/2025 | 13:27 | 0.12928 | 0.0004828 | 49 | 13122 | Planned interruptions on the network | Unknown | Pole Replacement
|  | INCD-181580-F | Te Kauwhata | Network | TEKCB5 | 19/01/2025 | 07:42 | 19/01/2025 | 10:20 | 0.01401 | 8.87e-05 | 9 | 1422 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-181603-F | Chartwell | Network | CHACB13 | 20/01/2025 | 09:01 | 20/01/2025 | 13:30 | 0.14856 | 0.0006503 | 66 | 15078 | Planned interruptions on the network | Planned | Distribution Transformer Replacement
|  | INCD-181641-F | Te Uku | Network | TEUCB11 | 20/01/2025 | 23:39 | 20/01/2025 | 23:56 | 0.087185 | 0.0075175 | 763 | 8849 | Unplanned interruptions on the network | Unknown | Fire Risk Mitigation Patrol - Sucessfully reclosed
|  | INCD-17725-G | Te Uku | Network | TEUCB11 | 21/01/2025 | 09:37 | 21/01/2025 | 15:45 | 0.0072514 | 1.97e-05 | 2 | 736 | Unplanned interruptions on the network | Defective Equipment | Faulty joint/connection
|  | INCD-181680-F | Pukete | Network | PUKCB4 | 22/01/2025 | 08:00 | 22/01/2025 | 08:51 | 0.0054386 | 0.0001084 | 11 | 552 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2998-E | Hoeka | Network | HOECB1 | 22/01/2025 | 09:11 | 22/01/2025 | 15:07 | 0.5512 | 0.0015567 | 158 | 55945 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2889-E | Weavers | Network | WEACB3 | 22/01/2025 | 09:20 | 22/01/2025 | 14:25 | 0.003005 | 9.9e-06 | 1 | 305 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-181706-F | Chartwell | Network | CHACB12 | 22/01/2025 | 16:24 | 22/01/2025 | 18:13 | 0.70767 | 0.014296 | 1451 | 71826 | Unplanned interruptions on the network | Defective Equipment | Installed Incorrectly
|  | INCD-181805-F | Weavers | Network | WEACB6 | 25/01/2025 | 07:27 | 25/01/2025 | 11:05 | 0.0064435 | 2.96e-05 | 3 | 654 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-181815-F | Weavers | Network | WEACB2 | 26/01/2025 | 02:56 | 26/01/2025 | 04:59 | 0.24392 | 0.0021084 | 214 | 24757 | Unplanned interruptions on the network | Unknown | Fire Risk Mitigation Patrol - Sucessfully reclosed
|  | INCD-182178-F | Weavers | Network | WEACB2 | 26/01/2025 | 08:24 | 26/01/2025 | 13:52 | 0.0096949 | 2.96e-05 | 3 | 984 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-182176-F | Weavers | Network | WEACB2 | 26/01/2025 | 09:04 | 26/01/2025 | 09:17 | 0.0001281 | 9.9e-06 | 1 | 13 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-181973-F | Horotiu | Network | HORCB4 | 30/01/2025 | 07:36 | 30/01/2025 | 15:41 | 0.071677 | 0.0001478 | 15 | 7275 | Unplanned interruptions on the network | Defective Equipment | Mechanism seized
|  | INCD-17732-G | Hampton Downs | Network | HPTCB5 | 30/01/2025 | 15:35 | 30/01/2025 | 18:09 | 0.0015173 | 9.9e-06 | 1 | 154 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2982-E | Hoeka | Network | HOECB3 | 31/01/2025 | 10:07 | 31/01/2025 | 13:17 | 0.013104 | 6.9e-05 | 7 | 1330 | Planned interruptions on the network | Planned | Distribution Transformer Replacement
|  | INCD-182316-F | Transpower Hamilton | Network | HAMCB2802 | 11/02/2025 | 18:31 | 12/02/2025 | 03:15 | 0.010325 | 1.97e-05 | 2 | 1048 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-182373-F | Glasgow St | Network | GLACB2 | 12/02/2025 | 20:32 | 12/02/2025 | 22:20 | 0.0021281 | 1.97e-05 | 2 | 216 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-182413-F | Chartwell | Network | CHACB5 | 13/02/2025 | 14:34 | 13/02/2025 | 15:28 | 0.027134 | 0.0005025 | 51 | 2754 | Unplanned interruptions on the network | Defective Equipment | Cable joint fails
|  | INCD-182414-F | Chartwell | Network | CHACB5 | 13/02/2025 | 14:34 | 13/02/2025 | 15:28 | 0.017025 | 0.0003153 | 32 | 1728 | Unplanned interruptions on the network | Defective Equipment | Cable joint fails
|  | INCD-3052-E | MAF | Network | MAFCB6 | 16/02/2025 | 09:04 | 16/02/2025 | 15:18 | 0.0074386 | 2.96e-05 | 3 | 755 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-182555-F | Horotiu | Network | GORCB13 | 18/02/2025 | 07:35 | 18/02/2025 | 17:07 | 0.030257 | 0.0062169 | 631 | 3071 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-182677-F | Whatawhata | Private | WHACB3 | 20/02/2025 | 11:34 | 20/02/2025 | 12:05 | 0.0015271 | 4.93e-05 | 5 | 155 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-182854-F | Finlayson Rd | Private | FINCB2 | 26/02/2025 | 09:31 | 26/02/2025 | 15:25 | 0.048336 | 0.0001379 | 14 | 4906 | Planned interruptions on the network | Unknown | ABS Replacement
|  | INCD-182973-F | Bryce St | Network | BRYCB12 | 01/03/2025 | 08:13 | 03/03/2025 | 01:07 | 0.026681 | 0.0002759 | 28 | 2708 | Unplanned interruptions on the network | Defective Equipment | Cable insulation failure
|  | INCD-3118-E | Transpower Hamilton | Network | HAMCB2722 | 06/03/2025 | 10:02 | 06/03/2025 | 14:35 | 0.52997 | 0.0019508 | 198 | 53790 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-3080-E | Borrman | Network | BORCB2 | 11/03/2025 | 09:31 | 11/03/2025 | 15:31 | 0.061893 | 0.0001773 | 18 | 6282 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-181-K | Silverdale | Network | HOECB2 | 13/03/2025 | 23:59 | 14/03/2025 | 00:06 | 0.0087493 | 0.001537 | 156 | 888.03 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-411-K | Chartwell | Network | CHACB9 | 20/03/2025 | 17:28 | 20/03/2025 | 18:27 | 0.06209 | 0.0010444 | 106 | 6302 | Unplanned interruptions on the network | Unknown | Fire Risk Mitigation Patrol - Sucessfully reclosed
|  | INCD-514-K | Chartwell | Network | CHACB9 | 24/03/2025 | 09:00 | 24/03/2025 | 17:41 | 0.19274 | 0.0006404 | 65 | 19563 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-3095-E | Transpower Hamilton | Network | HAMCB2802 | 24/03/2025 | 09:03 | 24/03/2025 | 09:33 | 0.0002956 | 9.9e-06 | 1 | 30 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-648-K | Peacockes Rd | Network | PEACB12 | 27/03/2025 | 21:15 | 27/03/2025 | 22:11 | 0.09021 | 0.0022365 | 227 | 9156 | Unplanned interruptions on the network | Unknown | Fire Risk Mitigation Patrol - Sucessfully reclosed
|  | INCD-3097-E | Te Kauwhata | Network | TEKCB2 | 31/03/2025 | 10:02 | 31/03/2025 | 10:35 | 0.0084535 | 0.0002562 | 26 | 858 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-171019-F | Whatawhata | Network | WHACB2 | 02/04/2024 | 20:56 | 03/04/2024 | 01:02 | 0.26124 | 0.0052218 | 530 | 26515 | Unplanned interruptions on the network | Defective Equipment | Faulty joint/connection
|  | INCD-2283-E | Raglan | Network | RAGCB5 | 03/04/2024 | 10:05 | 03/04/2024 | 13:49 | 0.24497 | 0.0010936 | 111 | 24864 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-17568-G | Whatawhata | Network | WHACB2 | 03/04/2024 | 10:41 | 03/04/2024 | 12:31 | 0.009754 | 8.87e-05 | 9 | 990 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-17571-G | Te Uku | Network | TEUCB11 | 04/04/2024 | 09:49 | 04/04/2024 | 15:57 | 0.010877 | 2.96e-05 | 3 | 1104 | Unplanned interruptions on the network | Defective Equipment | Faulty joint/connection
|  | INCD-2280-E | Hoeka | Network | HOECB6 | 05/04/2024 | 09:08 | 05/04/2024 | 11:21 | 0.0039312 | 2.96e-05 | 3 | 399 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-171160-F | Sandwich | Network | SANCB4 | 05/04/2024 | 11:50 | 05/04/2024 | 17:39 | 0.2407 | 0.0006897 | 70 | 24430 | Unplanned interruptions on the network | Wildlife | Rodent on HV terminals
|  | INCD-2365-E | Te Uku | Network | TEUCB11 | 07/04/2024 | 14:59 | 20/04/2024 | 16:17 | 0.18521 | 9.9e-06 | 1 | 18798 | Unplanned interruptions on the network | Lightning | Spontaneous failure
|  | INCD-171269-F | Te Uku | Network | TEUCB13 | 09/04/2024 | 23:50 | 10/04/2024 | 08:32 | 0.1648 | 0.0003153 | 32 | 16727 | Unplanned interruptions on the network | Wildlife | Possum contacts line
|  | INCD-171270-F | Te Uku | Network | TEUCB2 | 09/04/2024 | 23:50 | 09/04/2024 | 23:54 | 0.0002183 | 4.93e-05 | 5 | 22.16 | Unplanned interruptions on the network | Wildlife | Possum contacts line
|  | INCD-171270-F | Te Uku | Network | TEUCB13 | 09/04/2024 | 23:50 | 09/04/2024 | 23:54 | 4.36e-05 | 9.9e-06 | 1 | 4.43 | Unplanned interruptions on the network | Wildlife | Possum contacts line
|  | INCD-2288-E | Hoeka | Network | HOECB3 | 10/04/2024 | 09:14 | 10/04/2024 | 14:01 | 0.025449 | 8.87e-05 | 9 | 2583 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-171390-F | Te Kauwhata | Network | HPTCB5 | 11/04/2024 | 14:46 | 12/04/2024 | 14:06 | 0.052886 | 0.0033794 | 343 | 5367.76 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2106-E | Weavers | Network | WEACB3 | 14/04/2024 | 08:35 | 14/04/2024 | 16:09 | 0.20133 | 0.0053893 | 547 | 20434 | Planned interruptions on the network | Planned | New Connections
|  | INCD-171461-F | Te Kauwhata | Network | TEKCB5 | 15/04/2024 | 11:39 | 15/04/2024 | 15:58 | 0.022947 | 8.87e-05 | 9 | 2329 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2238-E | Hoeka | Network | HOECB4 | 16/04/2024 | 09:33 | 16/04/2024 | 13:39 | 0.083933 | 0.0003448 | 35 | 8519 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-171608-F | Hoeka | Network | HOECB2 | 19/04/2024 | 09:10 | 19/04/2024 | 14:14 | 0.22634 | 0.0007783 | 79 | 22973 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2303-E | Te Uku | Network | TEUCB11 | 19/04/2024 | 10:15 | 19/04/2024 | 15:32 | 0.057667 | 0.0001872 | 19 | 5853 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-171632-F | Sandwich Rd | Network | SANCB2 | 20/04/2024 | 15:19 | 20/04/2024 | 22:23 | 0.74651 | 0.0099412 | 1009 | 75769 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-171673-F | MAF | Network | HAMCB2742 | 23/04/2024 | 09:49 | 23/04/2024 | 11:21 | 0.000904 | 9.9e-06 | 1 | 91.75 | Unplanned interruptions on the network | Defective Equipment | faulty line connection
|  | INCD-2313-E | Finlayson | Network | FINCB2 | 26/04/2024 | 09:01 | 26/04/2024 | 11:00 | 0.015518 | 0.0001379 | 14 | 1575 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-171787-F | Chartwell | Network | CHACB9 | 29/04/2024 | 20:17 | 30/04/2024 | 02:31 | 0.24652 | 0.004276 | 434 | 25021 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-2300-E | Sandwich | Network | SANCB4 | 30/04/2024 | 06:08 | 30/04/2024 | 16:19 | 0.19293 | 0.0021676 | 220 | 19582 | Planned interruptions on the network | Planned | Recloser & Sectionaliser replacement
|  | INCD-171807-F | Weavers | Private | WEACB5 | 30/04/2024 | 11:19 | 30/04/2024 | 12:00 | 0.0008079 | 1.97e-05 | 2 | 82 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-172026-F | Transpower Hamilton | Network | HAMCB2802 | 06/05/2024 | 08:23 | 06/05/2024 | 12:05 | 0.0021873 | 9.9e-06 | 1 | 222 | Unplanned interruptions on the network | Wildlife | Rodent on HV terminals
|  | INCD-172037-F | Transpower Hamilton | Network | HAMCB2802 | 07/05/2024 | 00:15 | 07/05/2024 | 00:24 | 0.01339 | 0.0014877 | 151 | 1359 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-172050-F | Te Uku | Network | TEUCB11 | 07/05/2024 | 09:02 | 07/05/2024 | 16:25 | 0.33144 | 0.0007981 | 81 | 33640 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2180-E | Te Kauwhata | Network | TEKCB5 | 07/05/2024 | 09:05 | 07/05/2024 | 16:47 | 0.049479 | 0.0001084 | 11 | 5022 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-172051-F | Hoeka | Network | HAMCB2802 | 07/05/2024 | 09:28 | 07/05/2024 | 14:08 | 0.082978 | 0.0003153 | 32 | 8422 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2399-E | Hampton Downs | Network | HPTCB5 | 09/05/2024 | 09:19 | 09/05/2024 | 14:52 | 0.0032809 | 9.9e-06 | 1 | 333 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-172215-F | Te Uku | Network | TEUCB2 | 10/05/2024 | 02:00 | 10/05/2024 | 04:02 | 0.0048204 | 3.94e-05 | 4 | 489.26 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2402-E | Gordonton | Network | GORCB13 | 10/05/2024 | 09:15 | 10/05/2024 | 13:20 | 0.015853 | 6.9e-05 | 7 | 1609 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-172286-F | Finlayson Rd | Network | FINCB2 | 12/05/2024 | 08:31 | 12/05/2024 | 10:16 | 0.0010345 | 9.9e-06 | 1 | 105 | Unplanned interruptions on the network | Wildlife | Bird lne clash/break
|  | INCD-2381-E | Finlayson | Network | FINCB2 | 13/05/2024 | 09:07 | 13/05/2024 | 10:46 | 0.027311 | 0.0002759 | 28 | 2772 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2421-E | Avalon | Network | AVACB8 | 14/05/2024 | 06:10 | 14/05/2024 | 18:04 | 0.48586 | 0.0014089 | 143 | 49313 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-172373-F | Chartwell | Network | CHACB13 | 14/05/2024 | 09:50 | 14/05/2024 | 11:03 | 0.040385 | 0.0007783 | 79 | 4099 | Unplanned interruptions on the network | Defective Equipment | Fuse cut out/connection burnt out
|  | INCD-172407-F | Transpower Hamilton | Network | HAMCB2902 | 15/05/2024 | 08:01 | 15/05/2024 | 08:39 | 0.019469 | 0.0005123 | 52 | 1976 | Planned interruptions on the network | Planned | New Connections
|  | INCD-2394-E | Wallace | Network | WALCB6 | 15/05/2024 | 09:35 | 15/05/2024 | 14:58 | 0.0063647 | 1.97e-05 | 2 | 646 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-172604-F | Transpower Hamilton | Network | HAMCB2902 | 16/05/2024 | 12:15 | 16/05/2024 | 13:25 | 0.035863 | 0.0005123 | 52 | 3640 | Planned interruptions on the network | Planned | New Connections
|  | INCD-17582-G | Weavers | Network | WEACB6 | 16/05/2024 | 08:31 | 17/05/2024 | 13:39 | 0.017222 | 9.9e-06 | 1 | 1748 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (OUT of Zone)
|  | INCD-2395-E | Wallace | Network | WALCB5 | 17/05/2024 | 09:44 | 17/05/2024 | 11:49 | 0.0012414 | 9.9e-06 | 1 | 126 | Planned interruptions on the network | Planned | 11kV Fuse Replacement
|  | INCD-2416-E | Te Kauwhata | Network | TEKCB5 | 21/05/2024 | 09:21 | 21/05/2024 | 15:20 | 0.0070741 | 1.97e-05 | 2 | 718 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-172854-F | Te Kauwhata | Network | TEKCB3 | 26/05/2024 | 01:34 | 26/05/2024 | 01:52 | 0.0040789 | 0.0002266 | 23 | 414 | Unplanned interruptions on the network | Defective Equipment | Pins fulls out
|  | INCD-172857-F | Chartwell | Network | CHACB9 | 26/05/2024 | 05:03 | 26/05/2024 | 06:33 | 0.021134 | 0.0002365 | 24 | 2145 | Unplanned interruptions on the network | Defective Equipment | Contact problem
|  | INCD-17592-G | Weavers | Network | WEACB6 | 27/05/2024 | 09:02 | 27/05/2024 | 11:24 | 0.0013991 | 9.9e-06 | 1 | 142 | Unplanned interruptions on the network | Defective Equipment | Faulty joint/connection
|  | INCD-17595-G | Wallace | Network | WALCB6 | 27/05/2024 | 09:49 | 27/05/2024 | 17:31 | 0.0045519 | 9.9e-06 | 1 | 462 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-172959-F | Raglan | Network | RAGCB4 | 28/05/2024 | 08:45 | 28/05/2024 | 15:36 | 0.3361 | 0.0008178 | 83 | 34113 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2183-E | Te Kauwhata | Network | TEKCB5 | 28/05/2024 | 09:12 | 28/05/2024 | 15:53 | 0.047331 | 0.0001182 | 12 | 4804 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-173012-F | Horotiu | Network | HORCB6 | 29/05/2024 | 09:35 | 29/05/2024 | 15:57 | 0.93926 | 0.012473 | 1266 | 95331.71 | Unplanned interruptions on the network | Vegetation | Tree blown ovr on line (IN Zone)
|  | INCD-173039-F | Gordonton | Network | GORCB11 | 29/05/2024 | 10:41 | 30/05/2024 | 15:42 | 0.05144 | 2.96e-05 | 3 | 5221 | Unplanned interruptions on the network | Adverse weather | Pole blown over
|  | INCD-173079-F | Whatawhata | Network | RAGCB6 | 29/05/2024 | 14:19 | 29/05/2024 | 14:38 | 0.18895 | 0.009616 | 976 | 19178.31 | Unplanned interruptions on the network | Adverse weather | Wind line clash
|  | INCD-173079-F | Whatawhata | Network | TUKCB32 | 29/05/2024 | 14:19 | 29/05/2024 | 14:38 | 0.014907 | 0.0007586 | 77 | 1513.04 | Unplanned interruptions on the network | Adverse weather | Wind line clash
|  | INCD-173091-F | Transpower Hamilton | Network | CHACB6 | 29/05/2024 | 14:31 | 29/05/2024 | 19:03 | 0.093934 | 0.0009951 | 101 | 9534 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (IN Zone)
|  | INCD-173091-F | Transpower Hamilton | Network | HORCB4 | 29/05/2024 | 14:31 | 29/05/2024 | 19:03 | 0.05351 | 0.0004335 | 44 | 5431.06 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (IN Zone)
|  | INCD-173101-F | Te Uku Wind Farm | Network | RAGCB3 | 29/05/2024 | 14:42 | 30/05/2024 | 21:19 | 1.3007 | 0.0007192 | 73 | 132021 | Unplanned interruptions on the network | Lightning | Lightning strike surge
|  | INCD-173101-F | Te Uku Wind Farm | Network | TEUCB11 | 29/05/2024 | 14:42 | 30/05/2024 | 21:19 | 12.086 | 0.0081973 | 832 | 1226696 | Unplanned interruptions on the network | Lightning | Lightning strike surge
|  | INCD-173102-F | Te Uku | Network | RAGCB6 | 29/05/2024 | 14:50 | 31/05/2024 | 17:05 | 0.020676 | 0.0031725 | 322 | 2098.55 | Unplanned interruptions on the network | Vegetation | Tree blown ovr on line (OUT of Zone)
|  | INCD-173138-F | Whatawhata | Network | WHACB3 | 29/05/2024 | 14:36 | 29/05/2024 | 17:41 | 0.010936 | 5.91e-05 | 6 | 1110 | Unplanned interruptions on the network | Adverse weather | Line clash high wind
|  | INCD-17602-G | Glasgow St | Network | GLACB2 | 30/05/2024 | 04:36 | 30/05/2024 | 22:18 | 0.03139 | 2.96e-05 | 3 | 3186 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-2489-E | Horotiu | Network | HORCB5 | 30/05/2024 | 13:57 | 30/05/2024 | 15:39 | 0.001005 | 9.9e-06 | 1 | 102 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (OUT of Zone)
|  | INCD-173398-F | Horotiu | Network | HORCB5 | 31/05/2024 | 11:23 | 31/05/2024 | 14:32 | 0.0055864 | 2.96e-05 | 3 | 567 | Unplanned interruptions on the network | Defective Equipment | Intnl insulation failure
|  | INCD-173411-F | Gordonton | Network | GORCB11 | 31/05/2024 | 13:48 | 31/05/2024 | 15:06 | 0.41573 | 0.0056159 | 570 | 42195.62 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (OUT of Zone)
|  | INCD-173488-F | Hampton Downs | Network | HPTCB5 | 02/06/2024 | 13:41 | 02/06/2024 | 14:26 | 0.0004434 | 9.9e-06 | 1 | 45 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2471-E | Te Kauwhata | Network | TEKCB5 | 04/06/2024 | 09:03 | 04/06/2024 | 15:31 | 0.045873 | 0.0001182 | 12 | 4656 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-2454-E | Wallace | Network | WALCB6 | 05/06/2024 | 09:11 | 05/06/2024 | 11:48 | 0.015468 | 9.85e-05 | 10 | 1570 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-173771-F | Te Uku | Network | TEUCB11 | 09/06/2024 | 08:08 | 09/06/2024 | 10:18 | 0.0012808 | 9.9e-06 | 1 | 130 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2472-E | Steele Park | Network | STECB2 | 07/06/2024 | 09:04 | 07/06/2024 | 15:26 | 0.60161 | 0.0015764 | 160 | 61062 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2455-E | Hoeka | Network | HOECB1 | 11/06/2024 | 09:18 | 11/06/2024 | 13:09 | 0.088761 | 0.0003842 | 39 | 9009 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-173877-F | Steele Park | Network | STECB3 | 12/06/2024 | 09:06 | 12/06/2024 | 09:07 | 0.32939 | 0.0008276 | 84 | 33432 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-173902-F | Killarney Rd | Network | KILCB6 | 12/06/2024 | 13:43 | 13/06/2024 | 02:15 | 0.0074091 | 9.9e-06 | 1 | 752 | Unplanned interruptions on the network | Third_party | Cable hit by digger
|  | INCD-2481-E | Horotiu | Network | HORCB5 | 18/06/2024 | 09:16 | 18/06/2024 | 16:49 | 0.0044632 | 9.9e-06 | 1 | 453 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2475-E | Te Uku | Network | TEUCB13 | 20/06/2024 | 09:00 | 20/06/2024 | 14:13 | 0.096101 | 0.0003153 | 32 | 9754 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-2476-E | Norton Rd | Network | NORCB4 | 20/06/2024 | 23:35 | 21/06/2024 | 05:59 | 0.064317 | 0.0001675 | 17 | 6528 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-174309-F | Glasgow | Network | GLACB2 | 24/06/2024 | 05:10 | 24/06/2024 | 07:31 | 0.0055568 | 3.94e-05 | 4 | 564 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2484-E | Chartwell | Network | CHACB9 | 25/06/2024 | 09:00 | 25/06/2024 | 13:38 | 0.010917 | 3.94e-05 | 4 | 1108 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-17612-G | Transpower Hamilton | Network | HAMCB2902 | 26/06/2024 | 08:20 | 26/06/2024 | 11:07 | 0.24295 | 0.0016749 | 170 | 24659 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-17614-G | Chartwell | Network | CHACB9 | 26/06/2024 | 09:18 | 26/06/2024 | 13:18 | 0.052297 | 0.0002266 | 23 | 5308 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-174430-F | Gordonton | Network | GORCB13 | 27/06/2024 | 06:11 | 27/06/2024 | 09:57 | 0.13126 | 0.000601 | 61 | 13322 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-174506-F | Glasgow | Network | GLACB1 | 30/06/2024 | 12:58 | 30/06/2024 | 13:45 | 0.0032415 | 6.9e-05 | 7 | 329 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2523-E | Finlayson | Network | FINCB2 | 01/07/2024 | 08:58 | 01/07/2024 | 12:51 | 0.041883 | 0.0019015 | 193 | 4251 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2530-E | Glasgow | Network | GLACB2 | 02/07/2024 | 09:02 | 02/07/2024 | 11:38 | 0.026129 | 0.0001675 | 17 | 2652 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2540-E | Raglan | Network | RAGCB4 | 02/07/2024 | 09:08 | 02/07/2024 | 11:05 | 0.099136 | 0.0008473 | 86 | 10062 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2525-E | Peachgrove | Network | PCHCB1 | 02/07/2024 | 09:36 | 02/07/2024 | 16:32 | 0.15985 | 0.0003842 | 39 | 16224 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2512-E | Glasgow | Network | GLACB2 | 03/07/2024 | 10:11 | 03/07/2024 | 15:59 | 0.058287 | 0.0001675 | 17 | 5916 | Planned interruptions on the network | Planned | New Connections
|  | INCD-2508-E | Weavers | Network | WEACB2 | 04/07/2024 | 09:10 | 04/07/2024 | 13:18 | 0.024237 | 9.85e-05 | 10 | 2460 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-175246-F | Ngaruawahia | Network | NGACB2 | 09/07/2024 | 13:09 | 09/07/2024 | 13:53 | 0.0086702 | 0.0001971 | 20 | 880 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-2568-E | Peacockes | Network | PEACB12 | 17/07/2024 | 09:03 | 17/07/2024 | 15:35 | 0.31627 | 0.0008276 | 84 | 32100 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2578-E | Finlayson | Network | FINCB1 | 19/07/2024 | 09:00 | 19/07/2024 | 10:49 | 0.020385 | 0.0001872 | 19 | 2069 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-175395-F | Latham Court | Network | LATCB3 | 20/07/2024 | 20:15 | 20/07/2024 | 21:12 | 0.21303 | 0.010473 | 1063 | 21622 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-175403-F | Transpower Hamilton | Network | HAMCB2722 | 20/07/2024 | 23:47 | 21/07/2024 | 00:30 | 0.035587 | 0.0008276 | 84 | 3612 | Unplanned interruptions on the network | Defective Equipment | Line break at twist joint
|  | INCD-175500-F | Chartwell | Network | CHACB9 | 23/07/2024 | 19:32 | 23/07/2024 | 19:41 | 0.0008867 | 9.85e-05 | 10 | 90 | Unplanned interruptions on the network | Third_party | Hit by vehicle
|  | INCD-175502-F | Transpower Hamilton | Private | HOECB2 | 23/07/2024 | 23:52 | 23/07/2024 | 23:54 | 0.0015764 | 0.0007882 | 80 | 160 | Unplanned interruptions on the network | Third_party | Temp Disconnect / safety isolation
|  | INCD-4608-H | Wallace | Private | AVACB1 | 24/07/2024 | 09:44 | 24/07/2024 | 10:03 | 0.020404 | 0.0010739 | 109 | 2071 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-2562-E | Peacockes | Network | PEACB12 | 25/07/2024 | 09:55 | 25/07/2024 | 15:23 | 0.26409 | 0.0008178 | 83 | 26804 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-175583-F | Raglan | Network | RAGCB5 | 27/07/2024 | 12:24 | 27/07/2024 | 12:26 | 4.93e-05 | 1.97e-05 | 2 | 5 | Unplanned interruptions on the network | Defective Equipment | Faulty joint/connection
|  | INCD-175626-F | Te Uku | Network | TEUCB13 | 29/07/2024 | 13:44 | 29/07/2024 | 14:09 | 0.0002463 | 9.9e-06 | 1 | 25 | Unplanned interruptions on the network | Defective Equipment | Stay wire/ line clash
|  | INCD-2600-E | Gordonton | Network | GORCB12 | 30/07/2024 | 09:07 | 30/07/2024 | 14:29 | 0.023902 | 7.88e-05 | 8 | 2426 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-175662-F | Weavers | Network | WEACB3 | 31/07/2024 | 10:26 | 31/07/2024 | 11:30 | 0.16104 | 0.0045124 | 458 | 16345 | Unplanned interruptions on the network | Defective Equipment | Line break at twist joint
|  | INCD-2618-E | Whatawhata | Network | WHACB5 | 01/08/2024 | 09:13 | 01/08/2024 | 13:16 | 0.095766 | 0.0003941 | 40 | 9720 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-175728-F | Avalon | Network | AVACB6 | 01/08/2024 | 17:03 | 01/08/2024 | 17:36 | 0.020483 | 0.0006207 | 63 | 2079 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-175866-F | Peacockes Rd | Network | PEACB12 | 01/08/2024 | 19:35 | 01/08/2024 | 20:24 | 0.090466 | 0.0018424 | 187 | 9182 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-175865-F | Peacockes Rd | Network | PEACB12 | 01/08/2024 | 19:35 | 02/08/2024 | 16:29 | 0.012345 | 9.9e-06 | 1 | 1253 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-175795-F | Peacockes Rd | Network | PEACB13 | 02/08/2024 | 23:36 | 03/08/2024 | 07:32 | 1.3142 | 0.0061972 | 629 | 133385 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-175829-F | Te Uku | Network | TEUCB12 | 04/08/2024 | 10:36 | 04/08/2024 | 21:26 | 1.4935 | 0.0026799 | 272 | 151582 | Unplanned interruptions on the network | Defective Equipment | Stay wire/ line clash
|  | INCD-175980-F | Sandwich Rd | Network | SANCB6 | 07/08/2024 | 07:31 | 07/08/2024 | 17:40 | 1.3453 | 0.0080101 | 813 | 136540 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-176031-F | Gordonton | Network | GORCB12 | 08/08/2024 | 09:02 | 08/08/2024 | 12:46 | 0.10368 | 0.0004828 | 49 | 10523 | Planned interruptions on the network | Planned | Transformer Upgrade
|  | INCD-176039-F | Hampton Downs | Network | HPTCB5 | 08/08/2024 | 10:04 | 08/08/2024 | 10:15 | 0.0009754 | 8.87e-05 | 9 | 99 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-176220-F | Gordonton | Network | GORCB11 | 13/08/2024 | 07:00 | 13/08/2024 | 08:23 | 0.003271 | 3.94e-05 | 4 | 332 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-2647-E | Weavers | Network | WEACB3 | 13/08/2024 | 09:33 | 13/08/2024 | 14:27 | 0.071549 | 0.0002562 | 26 | 7262 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2644-E | Sandwich | Network | SANCB6 | 14/08/2024 | 09:05 | 14/08/2024 | 13:40 | 0.32784 | 0.0011922 | 121 | 33275 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2646-E | Weavers | Network | WEACB3 | 14/08/2024 | 09:43 | 14/08/2024 | 13:03 | 0.0059115 | 2.96e-05 | 3 | 600 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-2673-E | Glasgow | Network | GLACB2 | 14/08/2024 | 09:00 | 14/08/2024 | 10:58 | 0.002069 | 5.91e-05 | 6 | 210 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-176331-F | Gordonton | Network | GORCB13 | 14/08/2024 | 12:25 | 14/08/2024 | 15:48 | 0.0040001 | 1.97e-05 | 2 | 406 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-176338-F | Whatawhata | Network | WHACB2 | 14/08/2024 | 19:38 | 14/08/2024 | 23:14 | 0.059864 | 0.0004828 | 49 | 6076 | Unplanned interruptions on the network | Defective Equipment | Mechanism seized
|  | INCD-2628-E | Findlay | Network | FDLCB4 | 15/08/2024 | 23:35 | 16/08/2024 | 05:44 | 0.27562 | 0.0007488 | 76 | 27975 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-176483-F | Te Uku | Network | TEUCB11 | 17/08/2024 | 15:38 | 18/08/2024 | 16:22 | 0.138 | 0.0054878 | 557 | 14007 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-176497-F | Whatawhata | Network | RAGCB3 | 19/08/2024 | 02:55 | 19/08/2024 | 03:13 | 0.012057 | 0.0007389 | 75 | 1223.74 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-176497-F | Whatawhata | Network | TEUCB12 | 19/08/2024 | 02:55 | 19/08/2024 | 03:13 | 0.046497 | 0.0026799 | 272 | 4719.29 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-176497-F | Whatawhata | Network | TEUCB262 | 19/08/2024 | 02:55 | 19/08/2024 | 03:13 | 0.0008547 | 4.93e-05 | 5 | 86.75 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-176533-F | Whatawhata | Network | RAGCB3 | 19/08/2024 | 06:57 | 19/08/2024 | 16:19 | 0.34441 | 0.0007389 | 75 | 34957 | Unplanned interruptions on the network | Defective Equipment | Cable termination fails
|  | INCD-176542-F | Weavers | Network | WEACB3 | 19/08/2024 | 07:50 | 19/08/2024 | 07:50 | 0.10184 | 0.0043548 | 442 | 10336 | Unplanned interruptions on the network | Wildlife | Possum contacts line
|  | INCD-176617-F | Te Uku | Network | TEUCB13 | 19/08/2024 | 18:20 | 20/08/2024 | 15:12 | 9.72e-05 | 0.0007389 | 75 | 9.87 | Unplanned interruptions on the network | Vegetation | Tree blown ovr on line (OUT of Zone)
|  | INCD-176640-F | Borman | Network | BORCB5 | 20/08/2024 | 06:13 | 20/08/2024 | 07:15 | 0.0006109 | 9.9e-06 | 1 | 62 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-2682-E | Peacockes | Network | PEACB12 | 20/08/2024 | 09:09 | 20/08/2024 | 13:55 | 0.1845 | 0.0006798 | 69 | 18726 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2664-E | Weavers | Network | WEACB2 | 22/08/2024 | 09:17 | 22/08/2024 | 13:49 | 0.065421 | 0.0002463 | 25 | 6640 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-176890-F | Ngaruawahia | Network | NGACB5 | 25/08/2024 | 22:01 | 25/08/2024 | 23:11 | 0.031725 | 0.0004532 | 46 | 3220 | Unplanned interruptions on the network | Defective Equipment | Intnl insulation failure
|  | INCD-176939-F | Ngaruawahia | Network | NGACB5 | 26/08/2024 | 22:03 | 26/08/2024 | 23:31 | 0.057223 | 0.0006503 | 66 | 5808 | Unplanned interruptions on the network | Defective Equipment | Intnl insulation failure
|  | INCD-176978-F | Weavers | Network | WEACB4 | 27/08/2024 | 11:52 | 27/08/2024 | 14:16 | 0.017025 | 0.0001182 | 12 | 1728 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-177094-F | Chartwell | Network | CHACB13 | 28/08/2024 | 09:20 | 28/08/2024 | 10:14 | 0.016493 | 0.0003054 | 31 | 1674 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-177125-F | Hoeka | Network | HOECB1 | 30/08/2024 | 06:22 | 30/08/2024 | 13:55 | 0.85226 | 0.005675 | 576 | 86502 | Unplanned interruptions on the network | Defective Equipment | Line break at twist joint
|  | INCD-177133-F | Te Kauwhata | Network | TEKCB5 | 30/08/2024 | 08:32 | 30/08/2024 | 08:50 | 0.0026602 | 0.0001478 | 15 | 270 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-177252-F | Gordonton | Network | GORCB12 | 02/09/2024 | 09:54 | 02/09/2024 | 10:44 | 0.0009853 | 1.97e-05 | 2 | 100 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-177321-F | Whatawhata | Private | WHACB5 | 03/09/2024 | 16:16 | 03/09/2024 | 16:40 | 0.0016552 | 6.9e-05 | 7 | 168 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-2713-E | Glasgow | Network | GLACB2 | 06/09/2024 | 09:08 | 06/09/2024 | 13:21 | 0.0099707 | 3.94e-05 | 4 | 1012 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-177478-F | Simsey | Network | SIMCB2 | 07/09/2024 | 08:30 | 07/09/2024 | 14:49 | 0.0037341 | 9.9e-06 | 1 | 379 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-177482-F | Gordonton | Network | GORCB11 | 07/09/2024 | 09:42 | 07/09/2024 | 12:34 | 0.02542 | 0.0001478 | 15 | 2580 | Unplanned interruptions on the network | Defective Equipment | Cond not fully in sleeve
|  | INCD-2738-E | Gordonton | Network | GORCB11 | 09/09/2024 | 09:43 | 09/09/2024 | 12:22 | 0.031331 | 0.0001971 | 20 | 3180 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2799-E | Weavers | Network | WEACB2 | 10/09/2024 | 13:49 | 10/09/2024 | 18:52 | 0.0029853 | 9.9e-06 | 1 | 303 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-2736-E | Gordonton | Network | GORCB13 | 11/09/2024 | 09:12 | 11/09/2024 | 13:21 | 0.0073598 | 2.96e-05 | 3 | 747 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-177615-F | Hampton Downs | Network | HPTCB5 | 12/09/2024 | 06:07 | 12/09/2024 | 09:14 | 0.012887 | 6.9e-05 | 7 | 1308 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2651-E | Cobham | Network | COBCB11 | 15/09/2024 | 21:02 | 15/09/2024 | 23:14 | 0.042484 | 0.0003547 | 36 | 4312 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-2758-E | Latham | Network | LATCB2 | 19/09/2024 | 09:09 | 19/09/2024 | 09:29 | 0.014877 | 0.001468 | 149 | 1510 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-177949-F | Ngaruawahia | Network | NGACB6 | 21/09/2024 | 10:01 | 21/09/2024 | 12:33 | 0.0044927 | 2.96e-05 | 3 | 456 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-177958-F | Weavers | Network | WEACB3 | 22/09/2024 | 05:41 | 22/09/2024 | 07:17 | 0.0028375 | 2.96e-05 | 3 | 288 | Unplanned interruptions on the network | Wildlife | Bird betw line & pole
|  | INCD-177969-F | Transpower Hamilton | Network | HAMCB2902 | 23/09/2024 | 06:30 | 23/09/2024 | 06:32 | 0.0047982 | 0.0043647 | 443 | 487 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-178041-F | Gordonton | Network | GORCB11 | 24/09/2024 | 02:20 | 24/09/2024 | 03:37 | 0.099855 | 0.0013005 | 132 | 10135 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-178036-F | Weavers | Network | WEACB6 | 24/09/2024 | 05:56 | 24/09/2024 | 11:18 | 0.19785 | 0.0012217 | 124 | 20081 | Unplanned interruptions on the network | Defective Equipment | Line break at twist joint
|  | INCD-2765-E | Horotiu | Network | HORCB6 | 27/09/2024 | 09:12 | 27/09/2024 | 12:26 | 0.06144 | 0.000335 | 34 | 6236 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-178293-F | Te Uku | Network | TEUCB11 | 01/10/2024 | 08:30 | 01/10/2024 | 13:47 | 0.193 | 0.0007291 | 74 | 19589 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-178325-F | Transpower Hamilton | Network | HAMCB2722 | 01/10/2024 | 22:20 | 02/10/2024 | 04:30 | 0.0065421 | 1.97e-05 | 2 | 664 | Unplanned interruptions on the network | Defective Equipment | Broken insulator/bush
|  | INCD-2814-E | Peacockes | Network | PEACB12 | 07/10/2024 | 08:50 | 07/10/2024 | 12:39 | 0.0090249 | 3.94e-05 | 4 | 916 | Planned interruptions on the network | Planned | 11kV Fuse Replacement
|  | INCD-17662-G | Borman Rd | Network | CHACB13 | 09/10/2024 | 04:05 | 09/10/2024 | 05:10 | 0.080988 | 0.0014188 | 144 | 8220 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-2810-E | Transpower Hamilton | Network | HAMCB2802 | 09/10/2024 | 09:05 | 09/10/2024 | 15:10 | 0.16587 | 0.0014976 | 152 | 16835 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2836-E | Weavers | Network | WEACB3 | 14/10/2024 | 09:50 | 14/10/2024 | 14:52 | 0.10117 | 0.000335 | 34 | 10268 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2837-E | Whatawhata | Network | WHACB3 | 17/10/2024 | 09:33 | 17/10/2024 | 15:26 | 0.089658 | 0.0002562 | 26 | 9100 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-178896-F | Ngaruawahia | Network | NGACB6 | 17/10/2024 | 20:03 | 17/10/2024 | 21:58 | 0.035971 | 0.0003153 | 32 | 3651 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-178902-F | Hoeka | Network | HOECB1 | 18/10/2024 | 04:18 | 18/10/2024 | 06:00 | 0.0080396 | 7.88e-05 | 8 | 816 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2858-E | Borman | Network | BORCB7 | 25/10/2024 | 10:00 | 25/10/2024 | 12:15 | 0.14232 | 0.0010542 | 107 | 14445 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-179140-F | Whatawhata | Network | WHACB4 | 25/10/2024 | 13:01 | 25/10/2024 | 15:47 | 0.003271 | 1.97e-05 | 2 | 332 | Unplanned interruptions on the network | Wildlife | Bird causes flashover
|  | INCD-179247-F | Horotiu | Network | HORCB5 | 28/10/2024 | 06:00 | 28/10/2024 | 08:16 | 0.033311 | 0.0002463 | 25 | 3381 | Unplanned interruptions on the network | Defective Equipment | Jumpers come off
|  | INCD-2844-E | Hoeka | Network | HOECB3 | 29/10/2024 | 09:02 | 29/10/2024 | 12:15 | 0.0038031 | 1.97e-05 | 2 | 386 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2850-E | Borman | Network | BORCB5 | 31/10/2024 | 04:06 | 31/10/2024 | 05:36 | 0.0044336 | 4.93e-05 | 5 | 450 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2864-E | Glasgow | Network | GLACB2 | 07/11/2024 | 08:42 | 07/11/2024 | 09:50 | 0.0053598 | 7.88e-05 | 8 | 544 | Planned interruptions on the network | Planned | New Connections
|  | INCD-2879-E | Weavers | Network | WEACB6 | 08/11/2024 | 09:44 | 08/11/2024 | 12:32 | 0.011586 | 6.9e-05 | 7 | 1176 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-179668-F | Whatawhata | Private | WHACB5 | 11/11/2024 | 15:57 | 11/11/2024 | 16:21 | 0.0004729 | 1.97e-05 | 2 | 48 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-179682-F | Gordonton | Network | GORCB12 | 12/11/2024 | 09:27 | 12/11/2024 | 17:57 | 0.8987 | 0.0054484 | 553 | 91215 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-2875-E | Te Uku | Network | TEUCB12 | 14/11/2024 | 10:00 | 14/11/2024 | 10:49 | 0.0019311 | 3.94e-05 | 4 | 196 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2902-E | Te Uku | Network | TEUCB11 | 15/11/2024 | 09:02 | 15/11/2024 | 13:24 | 0.064534 | 0.0002463 | 25 | 6550 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2903-E | Wallace | Network | WALCB6 | 18/11/2024 | 09:38 | 18/11/2024 | 11:59 | 0.0083352 | 5.91e-05 | 6 | 846 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2860-E | Weavers | Network | WEACB3 | 19/11/2024 | 08:44 | 19/11/2024 | 14:53 | 0.066268 | 0.0001872 | 19 | 6726 | Planned interruptions on the network | Planned | Transformer Upgrade
|  | INCD-179988-F | Te Uku | Network | TEUCB11 | 21/11/2024 | 09:22 | 21/11/2024 | 14:15 | 0.020207 | 6.9e-05 | 7 | 2051 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-180008-F | Te Uku | Network | TEUCB2 | 21/11/2024 | 23:59 | 22/11/2024 | 00:09 | 0.0004177 | 5.91e-05 | 6 | 42.4 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-180008-F | Te Uku | Network | TEUCB13 | 21/11/2024 | 23:59 | 22/11/2024 | 00:09 | 0.0026871 | 0.0007389 | 75 | 272.73 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-180080-F | Transpower Hamilton | Network | HAMCB2802 | 25/11/2024 | 09:30 | 25/11/2024 | 09:55 | 0.013833 | 0.0005517 | 56 | 1404 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-180322-F | Weavers | Network | WEACB6 | 28/11/2024 | 16:00 | 28/11/2024 | 16:38 | 0.093106 | 0.002473 | 251 | 9450 | Unplanned interruptions on the network | Defective Equipment | Protection didn't work
|  | INCD-180345-F | Hoeka | Network | HOECB1 | 03/12/2024 | 08:36 | 03/12/2024 | 10:31 | 0.044179 | 0.0003842 | 39 | 4484 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (OUT of Zone)
|  | INCD-2926-E | Hampton Downs | Network | HPTCB5 | 03/12/2024 | 09:09 | 03/12/2024 | 13:22 | 0.0049854 | 1.97e-05 | 2 | 506 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2930-E | Latham | Network | LATCB6 | 05/12/2024 | 21:54 | 06/12/2024 | 03:29 | 0.0004828 | 1.97e-05 | 2 | 49 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-180473-F | Hoeka | Network | SILCB1 | 06/12/2024 | 15:05 | 06/12/2024 | 15:14 | 0.0041183 | 0.0005123 | 52 | 418 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-180526-F | Horotiu | Network | HORCB5 | 09/12/2024 | 09:00 | 09/12/2024 | 12:02 | 0.16497 | 0.0009064 | 92 | 16744 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-180540-F | Weavers | Private | WEACB4 | 09/12/2024 | 16:26 | 09/12/2024 | 16:38 | 0.0009458 | 7.88e-05 | 8 | 96 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-180596-F | Gordonon | Network | GORCB11 | 11/12/2024 | 13:43 | 11/12/2024 | 19:34 | 0.61715 | 0.013409 | 1361 | 62639 | Unplanned interruptions on the network | Defective Equipment | Insulator split
|  | INCD-180689-F | Kent | Network | KENCB9 | 15/12/2024 | 18:17 | 16/12/2024 | 01:18 | 0.075194 | 0.0003547 | 36 | 7632 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-180722-F | Peacockes Rd | Network | PEACB16 | 16/12/2024 | 12:21 | 16/12/2024 | 19:40 | 0.24329 | 0.0028375 | 288 | 24693 | Unplanned interruptions on the network | Adverse weather | Pole blown over
|  | INCD-180752-F | Pukete | Network | PUKCB5 | 17/12/2024 | 09:04 | 17/12/2024 | 09:23 | 0.011715 | 0.0006404 | 65 | 1189 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-181171-F | Pukete | Network | PUKCB5 | 17/12/2024 | 13:59 | 17/12/2024 | 14:19 | 0.012808 | 0.0006404 | 65 | 1300 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-180841-F | Avalon Dr | Network | AVACB6 | 19/12/2024 | 13:43 | 19/12/2024 | 13:56 | 0.013064 | 0.001005 | 102 | 1326 | Unplanned interruptions on the network | Defective Equipment | Connect/jumper loose
|  | INCD-17712-G | Whatawhata | Network | WHACB2 | 23/12/2024 | 14:23 | 23/12/2024 | 17:13 | 0.0050248 | 2.96e-05 | 3 | 510 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-180952-F | Avalon Dr | Network | AVACB6 | 23/12/2024 | 23:02 | 24/12/2024 | 03:17 | 0.25626 | 0.001005 | 102 | 26010 | Unplanned interruptions on the network | Defective Equipment | Connect/jumper loose
|  | INCD-180965-F | Horotiu | Network | HORCB5 | 24/12/2024 | 11:42 | 24/12/2024 | 12:15 | 0.022109 | 0.00067 | 68 | 2244 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-181042-F | Glasgow | Network | GLACB2 | 30/12/2024 | 10:08 | 30/12/2024 | 10:39 | 0.0012217 | 3.94e-05 | 4 | 124 | Unplanned interruptions on the network | Defective Equipment | Mal adjusted from wear
|  | INCD-181075-F | Te Uku | Network | RAGCB6 | 01/01/2025 | 00:50 | 01/01/2025 | 01:33 | 0.0025419 | 5.91e-05 | 6 | 258 | Unplanned interruptions on the network | Vegetation | Tree growns in line
|  | INCD-2968-E | Weavers | Network | WEACB6 | 08/01/2025 | 10:03 | 08/01/2025 | 12:26 | 0.0070445 | 4.93e-05 | 5 | 715 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-181291-F | Te Uku | Network | TEUCB11 | 10/01/2025 | 10:24 | 10/01/2025 | 10:56 | 0.0009458 | 2.96e-05 | 3 | 96 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-181468-F | Sandwich | Network | SANCB5 | 15/01/2025 | 15:47 | 15/01/2025 | 16:13 | 0.0079411 | 0.0003054 | 31 | 806 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-181503-F | Finlayson Rd | Network | FINCB2 | 16/01/2025 | 09:46 | 16/01/2025 | 14:05 | 0.0025518 | 9.9e-06 | 1 | 259 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-180950-F | Transpower Hamilton | Network | HAMCB2742 | 17/01/2025 | 09:31 | 17/01/2025 | 10:39 | 0.0073697 | 0.0001084 | 11 | 748 | Planned interruptions on the network | Planned | 11kV Fuse Replacement
|  | INCD-2977-E | Te Kauwhata | Network | TEKCB3 | 21/01/2025 | 08:56 | 21/01/2025 | 10:52 | 0.017143 | 0.0001478 | 15 | 1740 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-181676-F | Ngaruawahia | Network | NGACB2 | 21/01/2025 | 17:56 | 22/01/2025 | 01:14 | 0.23981 | 0.0008867 | 90 | 24340 | Unplanned interruptions on the network | Vegetation | Tree blown ovr on line (OUT of Zone)
|  | INCD-181679-F | Chartwell | Network | CHACB9 | 22/01/2025 | 01:48 | 22/01/2025 | 02:13 | 0.082022 | 0.0035863 | 364 | 8325 | Unplanned interruptions on the network | Unknown | Fire Risk Mitigation Patrol - Sucessfully reclosed
|  | INCD-181706-F | Chartwell | Network | CHACB9 | 22/01/2025 | 16:24 | 22/01/2025 | 18:13 | 1.0073 | 0.01338 | 1358 | 102233 | Unplanned interruptions on the network | Defective Equipment | Installed Incorrectly
|  | INCD-182175-F | Steele Park | Network | STECB3 | 24/01/2025 | 15:03 | 24/01/2025 | 15:06 | 0.0059115 | 0.0019705 | 200 | 600 | Planned interruptions on the network | Planned | New Connections
|  | INCD-181802-F | Wallace Rd | Network | WALCB6 | 25/01/2025 | 07:03 | 25/01/2025 | 09:24 | 0.0055568 | 3.94e-05 | 4 | 564 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-181899-F | Glasgow St | Network | GLACB2 | 29/01/2025 | 03:34 | 29/01/2025 | 03:52 | 0.040494 | 0.0026602 | 270 | 4110 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-3004-E | Transpower Hamilton | Network | HAMCB2802 | 04/02/2025 | 09:06 | 04/02/2025 | 12:45 | 0.0021577 | 9.9e-06 | 1 | 219 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-3025-E | Weavers | Network | WEACB6 | 04/02/2025 | 09:09 | 04/02/2025 | 13:44 | 0.0054189 | 1.97e-05 | 2 | 550 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-182378-F | Te Kauwhata | Network | TEKCB5 | 13/02/2025 | 01:22 | 13/02/2025 | 03:06 | 0.05943 | 0.0005714 | 58 | 6032 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-182411-F | Chartwell | Network | CHACB5 | 13/02/2025 | 14:34 | 13/02/2025 | 15:28 | 0.021281 | 0.0003941 | 40 | 2160 | Unplanned interruptions on the network | Defective Equipment | Cable joint fails
|  | INCD-182522-F | Weavers | Network | WEACB3 | 17/02/2025 | 09:48 | 17/02/2025 | 11:53 | 0.0012316 | 9.9e-06 | 1 | 125 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-182555-F | Horotiu | Network | HORCB4 | 18/02/2025 | 07:35 | 18/02/2025 | 17:07 | 0.26499 | 0.0011035 | 112 | 26896 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-182792-F | Hoeka | Private | HOECB3 | 24/02/2025 | 14:09 | 24/02/2025 | 14:23 | 0.0031725 | 0.0002266 | 23 | 322 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-3030-E | Finlayson | Network | FINCB2 | 25/02/2025 | 10:06 | 25/02/2025 | 16:01 | 0.066366 | 0.0001872 | 19 | 6736 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-3064-E | Whatawhata | Network | WHACB3 | 04/03/2025 | 09:00 | 04/03/2025 | 13:30 | 0.050701 | 0.0001971 | 20 | 5146 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-15-K | Weavers | Network | WEACB3 | 08/03/2025 | 23:29 | 09/03/2025 | 02:07 | 0.20068 | 0.0022661 | 230 | 20368 | Unplanned interruptions on the network | Wildlife | Possum contacts line
|  | INCD-3048-E | Tasman | Network | TASCB0 | 09/03/2025 | 08:05 | 09/03/2025 | 12:24 | 0.040829 | 0.0001576 | 16 | 4144 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-3062-E | Peacockes | Network | PEACB12 | 12/03/2025 | 08:43 | 12/03/2025 | 11:30 | 0.0016454 | 9.9e-06 | 1 | 167 | Planned interruptions on the network | Planned | Transformer Upgrade
|  | INCD-144-K | Hoeka | Network | HOECB4 | 12/03/2025 | 23:59 | 13/03/2025 | 00:11 | 0.027968 | 0.0024533 | 249 | 2838.66 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-146-K | Hoeka | Network | HOECB3 | 12/03/2025 | 23:59 | 13/03/2025 | 00:00 | 0.0088673 | 0.0061184 | 621 | 900 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-243-K | Weavers | Network | WEACB4 | 17/03/2025 | 00:01 | 17/03/2025 | 01:09 | 0.014069 | 0.0002069 | 21 | 1428 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-3079-E | Gordonton | Network | GORCB13 | 18/03/2025 | 09:02 | 18/03/2025 | 11:06 | 0.037873 | 0.0003054 | 31 | 3844 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-312-K | Peacockes Rd | Network | PEACB12 | 18/03/2025 | 14:29 | 18/03/2025 | 20:35 | 0.40349 | 0.0013695 | 139 | 40953 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-3089-E | Ngaruawahia | Network | NGACB3 | 19/03/2025 | 08:35 | 19/03/2025 | 14:45 | 0.28728 | 0.0008178 | 83 | 29158 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-3081-E | Horotiu | Network | HORCB5 | 19/03/2025 | 09:34 | 19/03/2025 | 10:23 | 0.0077244 | 0.0001576 | 16 | 784 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-444-K | Chartwell | Network | CHACB9 | 21/03/2025 | 11:17 | 21/03/2025 | 13:40 | 0.053401 | 0.0003744 | 38 | 5420 | Unplanned interruptions on the network | Vegetation | Tree known grows in line
|  | INCD-491-K | Te Uku | Network | TEUCB11 | 23/03/2025 | 09:32 | 23/03/2025 | 14:08 | 0.0081579 | 2.96e-05 | 3 | 828 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-515-K | Steele Park | Network | STECB3 | 24/03/2025 | 09:00 | 24/03/2025 | 09:04 | 0.0049263 | 0.0012316 | 125 | 500 | Planned interruptions on the network | Planned | Relocations
|  | INCD-3113-E | Transpower Hamilton | Network | HAMCB2862 | 29/03/2025 | 09:04 | 29/03/2025 | 14:28 | 0.038307 | 0.0001182 | 12 | 3888 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2299-E | Sandwich | Network | SANCB4 | 05/04/2024 | 08:23 | 05/04/2024 | 12:48 | 0.41775 | 0.0015764 | 160 | 42400 | Planned interruptions on the network | Planned | Distribution Transformer Replacement
|  | INCD-2282-E | Gordonton | Network | GORCB12 | 05/04/2024 | 09:04 | 05/04/2024 | 14:32 | 0.032316 | 9.85e-05 | 10 | 3280 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2285-E | Hoeka | Network | HOECB6 | 08/04/2024 | 09:10 | 08/04/2024 | 15:34 | 0.057135 | 0.0001576 | 16 | 5799 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-171264-F | Te Uku | Network | TEUCB2 | 09/04/2024 | 21:52 | 09/04/2024 | 23:59 | 8.54e-05 | 4.93e-05 | 5 | 8.67 | Unplanned interruptions on the network | Wildlife | Possum contacts line
|  | INCD-171328-F | Peacockes Rd | Network | PEACB16 | 11/04/2024 | 09:30 | 11/04/2024 | 13:58 | 0.68495 | 0.0028375 | 288 | 69520 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2278-E | Gordonton | Network | GORCB13 | 11/04/2024 | 10:00 | 11/04/2024 | 14:57 | 0.011705 | 3.94e-05 | 4 | 1188 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-171390-F | Te Kauwhata | Network | FINCB1 | 11/04/2024 | 14:46 | 12/04/2024 | 14:06 | 0.10347 | 0.0050642 | 514 | 10502.07 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2290-E | Hoeka | Network | HOECB1 | 12/04/2024 | 09:09 | 12/04/2024 | 14:38 | 0.029173 | 8.87e-05 | 9 | 2961 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-171388-F | Silverdale | Network | SILCB4 | 12/04/2024 | 12:35 | 12/04/2024 | 22:03 | 0.74787 | 0.003005 | 305 | 75907 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-171443-F | Hoeka | Network | HOECB6 | 15/04/2024 | 08:33 | 15/04/2024 | 11:42 | 0.081658 | 0.0010345 | 105 | 8288 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2266-E | Silverdale | Network | SILCB5 | 16/04/2024 | 09:34 | 16/04/2024 | 17:17 | 0.0045617 | 9.9e-06 | 1 | 463 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-171539-F | Silverdale | Private | SILCB1 | 16/04/2024 | 15:34 | 16/04/2024 | 15:59 | 0.0012316 | 4.93e-05 | 5 | 125 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-2350-E | Sandwich | Network | NORCB1 | 17/04/2024 | 05:10 | 17/04/2024 | 16:18 | 0.23929 | 0.0020789 | 211 | 24287 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-2316-E | Finlayson | Network | FINCB2 | 18/04/2024 | 09:04 | 18/04/2024 | 13:42 | 0.056543 | 0.0002069 | 21 | 5739 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-4525-H | Horotiu | Network | HORCB5 | 19/04/2024 | 14:29 | 19/04/2024 | 17:29 | 0.0017735 | 9.9e-06 | 1 | 180 | Unplanned interruptions on the network | Wildlife | Bird betw line & pole
|  | INCD-4526-H | MAF | Network | MAFCB6 | 23/04/2024 | 13:23 | 23/04/2024 | 13:27 | 0.0001576 | 3.94e-05 | 4 | 16 | Unplanned interruptions on the network | Defective Equipment | faulty line connection
|  | INCD-171757-F | Te Kauwhata | Network | TEKCB5 | 29/04/2024 | 06:21 | 29/04/2024 | 14:25 | 0.0095372 | 1.97e-05 | 2 | 968 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-171777-F | Horotiu | Network | HORCB5 | 29/04/2024 | 09:33 | 29/04/2024 | 13:00 | 0.0020395 | 9.9e-06 | 1 | 207 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-171813-F | Weavers | Network | WEACB2 | 30/04/2024 | 13:32 | 30/04/2024 | 15:15 | 0.0040592 | 3.94e-05 | 4 | 412 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-171839-F | Glasgow St | Network | GLACB2 | 01/05/2024 | 09:01 | 01/05/2024 | 11:32 | 0.07014 | 0.0004631 | 47 | 7119 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-171850-F | Horotiu | Network | HORCB5 | 01/05/2024 | 11:59 | 01/05/2024 | 13:01 | 0.0006109 | 9.9e-06 | 1 | 62 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-171973-F | Borman Rd | Network | BORCB2 | 04/05/2024 | 08:05 | 04/05/2024 | 12:15 | 0.14804 | 0.000601 | 61 | 15026 | Unplanned interruptions on the network | Defective Equipment | Trip mechanism fails
|  | INCD-2360-E | Finlayson | Network | HPTCB5 | 05/05/2024 | 10:00 | 05/05/2024 | 15:35 | 0.082564 | 0.000266 | 27 | 8380 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-2369-E | Te Uku | Network | TEUCB11 | 07/05/2024 | 10:26 | 07/05/2024 | 15:25 | 0.017675 | 5.91e-05 | 6 | 1794 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2370-E | Hoeka | Network | HOECB1 | 09/05/2024 | 09:13 | 09/05/2024 | 13:55 | 0.019449 | 6.9e-05 | 7 | 1974 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2411-E | Hoeka | Network | HOECB6 | 15/05/2024 | 09:10 | 15/05/2024 | 14:07 | 0.032188 | 0.0001084 | 11 | 3267 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-172435-F | Weavers | Network | WEACB3 | 15/05/2024 | 13:45 | 15/05/2024 | 18:59 | 0.43545 | 0.0017439 | 177 | 44197 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-2181-E | Te Kauwhata | Network | TEKCB5 | 16/05/2024 | 09:05 | 16/05/2024 | 16:32 | 0.061657 | 0.0001379 | 14 | 6258 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-17585-G | Te Uku | Private | TEUCB11 | 18/05/2024 | 10:17 | 18/05/2024 | 10:17 | 0.0012808 | 1.97e-05 | 2 | 130 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-172612-F | Transpower Hamilton | Network | HAMCB2902 | 20/05/2024 | 14:01 | 20/05/2024 | 15:51 | 0.056356 | 0.0005123 | 52 | 5720 | Unplanned interruptions on the network | Third_party | Cable isolated - safety reasons
|  | INCD-172622-F | Ngaruawahia | Network | NGACB2 | 20/05/2024 | 19:38 | 20/05/2024 | 21:03 | 0.13077 | 0.0043942 | 446 | 13272.72 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-172643-F | Weavers | Network | WEACB4 | 21/05/2024 | 07:45 | 21/05/2024 | 13:30 | 0.0067982 | 1.97e-05 | 2 | 690 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-172918-F | Te Kauwhata | Network | TEKCB3 | 26/05/2024 | 06:27 | 26/05/2024 | 12:07 | 0.077047 | 0.0002266 | 23 | 7820 | Unplanned interruptions on the network | Defective Equipment | Pins fulls out
|  | INCD-172916-F | Horotiu | Network | HORCB6 | 26/05/2024 | 14:44 | 26/05/2024 | 16:00 | 0.057795 | 0.001133 | 115 | 5866 | Unplanned interruptions on the network | Adverse weather | High wind lne break
|  | INCD-172960-F | Gordonton | Network | GORCB12 | 28/05/2024 | 09:01 | 28/05/2024 | 13:45 | 0.1331 | 0.0004828 | 49 | 13509 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-172967-F | Wallace Rd | Network | AVACB1 | 28/05/2024 | 11:04 | 28/05/2024 | 11:26 | 0.021416 | 0.0041183 | 418 | 2173.7 | Unplanned interruptions on the network | Human error | Unintentionally Disabled
|  | INCD-173041-F | Te Uku | Network | TEUCB12 | 29/05/2024 | 11:52 | 30/05/2024 | 20:44 | 1.1272 | 0.0005714 | 58 | 114407 | Unplanned interruptions on the network | Adverse weather | Line clash high wind
|  | INCD-173079-F | Whatawhata | Network | TEUCB13 | 29/05/2024 | 14:19 | 29/05/2024 | 14:38 | 0.014326 | 0.0007291 | 74 | 1454.09 | Unplanned interruptions on the network | Adverse weather | Wind line clash
|  | INCD-173091-F | Transpower Hamilton | Network | BORCB3 | 29/05/2024 | 14:31 | 29/05/2024 | 19:03 | 1.1501 | 0.01138 | 1155 | 116732 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (IN Zone)
|  | INCD-173091-F | Transpower Hamilton | Network | BORCB4 | 29/05/2024 | 14:31 | 29/05/2024 | 19:03 | 3.3601 | 0.014483 | 1470 | 341040 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (IN Zone)
|  | INCD-173091-F | Transpower Hamilton | Network | CHACB10 | 29/05/2024 | 14:31 | 29/05/2024 | 19:03 | 0.89918 | 0.0094289 | 957 | 91263.8 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (IN Zone)
|  | INCD-173091-F | Transpower Hamilton | Network | CHACB13 | 29/05/2024 | 14:31 | 29/05/2024 | 19:03 | 1.1412 | 0.012188 | 1237 | 115824 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (IN Zone)
|  | INCD-173101-F | Te Uku Wind Farm | Network | RAGCB4 | 29/05/2024 | 14:42 | 30/05/2024 | 21:19 | 7.519 | 0.0065125 | 661 | 763152.1 | Unplanned interruptions on the network | Lightning | Lightning strike surge
|  | INCD-173102-F | Te Uku | Network | TEUCB2 | 29/05/2024 | 14:50 | 31/05/2024 | 17:05 | 0.087486 | 4.93e-05 | 5 | 8879.59 | Unplanned interruptions on the network | Vegetation | Tree blown ovr on line (OUT of Zone)
|  | INCD-173116-F | Pukete | Network | PUKCB10 | 29/05/2024 | 14:58 | 30/05/2024 | 15:33 | 0.39227 | 0.000266 | 27 | 39814 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-173108-F | Weavers | Network | NGACB3 | 29/05/2024 | 15:01 | 29/05/2024 | 15:06 | 0.023534 | 0.0051726 | 525 | 2388.66 | Unplanned interruptions on the network | Adverse weather | Wind line clash
|  | INCD-173177-F | Weavers | Network | WEACB6 | 29/05/2024 | 15:11 | 30/05/2024 | 00:11 | 0.031902 | 5.91e-05 | 6 | 3238 | Unplanned interruptions on the network | Adverse weather | Line clash high wind
|  | INCD-173202-F | Weavers | Network | WEACB2 | 29/05/2024 | 18:41 | 29/05/2024 | 21:32 | 0.011764 | 6.9e-05 | 7 | 1194 | Unplanned interruptions on the network | Adverse weather | Line clash high wind
|  | INCD-17599-G | Glasgow St | Network | GLACB2 | 30/05/2024 | 01:48 | 30/05/2024 | 23:59 | 0.026227 | 1.97e-05 | 2 | 2662 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-17600-G | Ngaruawahia | Network | NGACB2 | 30/05/2024 | 02:07 | 30/05/2024 | 02:22 | 0.0002956 | 1.97e-05 | 2 | 30 | Unplanned interruptions on the network | Adverse weather | Line clash high wind
|  | INCD-173371-F | Gordonton | Network | GORCB13 | 31/05/2024 | 08:00 | 31/05/2024 | 15:52 | 0.074771 | 0.0008867 | 90 | 7589 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-173380-F | Finlayson Rd | Network | FINCB2 | 31/05/2024 | 09:02 | 31/05/2024 | 13:06 | 0.007212 | 2.96e-05 | 3 | 732 | Unplanned interruptions on the network | Defective Equipment | Faulty joint/connection
|  | INCD-173497-F | Finlayson | Network | FINCB2 | 02/06/2024 | 21:56 | 02/06/2024 | 22:19 | 0.0002266 | 9.9e-06 | 1 | 23 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-173627-F | Finlayson Rd | Network | FINCB2 | 05/06/2024 | 12:18 | 05/06/2024 | 14:55 | 0.043302 | 0.0002759 | 28 | 4395 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-173702-F | Peacockes | Network | PEACB12 | 06/06/2024 | 16:16 | 06/06/2024 | 17:06 | 0.0004926 | 9.9e-06 | 1 | 50 | Unplanned interruptions on the network | Defective Equipment | Faulty line spacer
|  | INCD-173727-F | Weavers | Network | WEACB5 | 07/06/2024 | 09:16 | 07/06/2024 | 12:43 | 0.012237 | 5.91e-05 | 6 | 1242 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-173829-F | Weavers | Network | WEACB6 | 10/06/2024 | 18:26 | 10/06/2024 | 21:15 | 0.0033301 | 1.97e-05 | 2 | 338 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (OUT of Zone)
|  | INCD-173939-F | Weavers | Network | WEACB2 | 13/06/2024 | 10:59 | 13/06/2024 | 11:47 | 0.0004729 | 9.9e-06 | 1 | 48 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2464-E | Transpower Hamilton | Network | HAMCB2802 | 20/06/2024 | 09:46 | 20/06/2024 | 14:25 | 0.14019 | 0.0005025 | 51 | 14229 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-174234-F | Gordonton | Network | GORCB13 | 20/06/2024 | 20:47 | 20/06/2024 | 20:49 | 0.0028769 | 0.0012513 | 127 | 292 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (OUT of Zone)
|  | INCD-2482-E | Wallace | Network | WALCB6 | 25/06/2024 | 09:37 | 25/06/2024 | 14:40 | 0.020897 | 6.9e-05 | 7 | 2121 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-17615-G | Weavers | Network | WEACB3 | 28/06/2024 | 19:44 | 29/06/2024 | 01:15 | 0.097835 | 0.0002956 | 30 | 9930 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-174538-F | Weavers | Network | WEACB2 | 01/07/2024 | 11:15 | 01/07/2024 | 13:24 | 0.0012808 | 9.9e-06 | 1 | 130 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-174585-F | Whatawhata | Network | WHACB4 | 02/07/2024 | 05:20 | 02/07/2024 | 07:33 | 0.0078623 | 5.91e-05 | 6 | 798 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (OUT of Zone)
|  | INCD-2527-E | Glasgow | Network | GLACB2 | 02/07/2024 | 09:24 | 02/07/2024 | 11:34 | 0.0012808 | 9.9e-06 | 1 | 130 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2526-E | Finlayson | Network | FINCB2 | 03/07/2024 | 09:02 | 03/07/2024 | 14:37 | 0.10351 | 0.0005222 | 53 | 10506 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-174898-F | Gordonton | Network | GORCB11 | 09/07/2024 | 14:32 | 09/07/2024 | 14:37 | 0.0013104 | 0.0002463 | 25 | 133 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-17621-G | Weavers | Network | WEACB2 | 11/07/2024 | 09:04 | 11/07/2024 | 09:04 | 0.0374 | 0.0001281 | 13 | 3796 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-175127-F | Transpower Hamilton | Network | HAMCB2862 | 15/07/2024 | 10:03 | 16/07/2024 | 16:00 | 0.017705 | 9.9e-06 | 1 | 1797 | Unplanned interruptions on the network | Vegetation | Tree growns in line
|  | INCD-175143-F | Finlayson | Network | FINCB2 | 15/07/2024 | 11:42 | 15/07/2024 | 14:32 | 0.0016749 | 9.9e-06 | 1 | 170 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-175177-F | Weavers | Network | WEACB3 | 16/07/2024 | 08:19 | 16/07/2024 | 08:32 | 0.0001281 | 9.9e-06 | 1 | 13 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-175190-F | Whatawhata | Network | WHACB2 | 16/07/2024 | 09:45 | 16/07/2024 | 16:59 | 0.004276 | 9.9e-06 | 1 | 434 | Unplanned interruptions on the network | Defective Equipment | Intnl insulation failure
|  | INCD-175197-F | Hoeka | Private | HOECB1 | 16/07/2024 | 10:01 | 16/07/2024 | 10:30 | 0.0034287 | 0.0001182 | 12 | 348 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-2561-E | Latham | Network | LATCB3 | 17/07/2024 | 09:02 | 17/07/2024 | 10:33 | 0.13422 | 0.0015665 | 159 | 13623 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2596-E | Avalon | Network | AVACB6 | 26/07/2024 | 09:05 | 26/07/2024 | 14:13 | 0.39447 | 0.0012808 | 130 | 40038 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-175619-F | Te Uku | Network | TEUCB11 | 29/07/2024 | 09:43 | 29/07/2024 | 11:18 | 0.000936 | 9.9e-06 | 1 | 95 | Unplanned interruptions on the network | Defective Equipment | Connect/jumper loose
|  | INCD-2539-E | Transpower Hamilton | Network | HAMCB2822 | 01/08/2024 | 10:18 | 01/08/2024 | 13:28 | 0.3407 | 0.0017932 | 182 | 34580 | Planned interruptions on the network | Planned | Relocations
|  | INCD-175867-F | Avalon Dr | Network | AVACB6 | 01/08/2024 | 17:03 | 01/08/2024 | 17:36 | 0.021784 | 0.0006601 | 67 | 2211 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2645-E | Horotiu | Network | HORCB5 | 02/08/2024 | 09:07 | 02/08/2024 | 11:07 | 0.13534 | 0.001133 | 115 | 13737 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-175775-F | Horotiu | Private | HORCB5 | 02/08/2024 | 11:53 | 02/08/2024 | 13:45 | 0.0011035 | 9.9e-06 | 1 | 112 | Unplanned interruptions on the network | Third_party | Temp Disconnect / safety isolation
|  | INCD-175829-F | Te Uku | Network | TEUCB2 | 04/08/2024 | 10:36 | 04/08/2024 | 21:26 | 0.023193 | 8.87e-05 | 9 | 2354.02 | Unplanned interruptions on the network | Defective Equipment | Stay wire/ line clash
|  | INCD-2597-E | MAF | Network | MAFCB6 | 05/08/2024 | 09:00 | 05/08/2024 | 15:17 | 0.0037144 | 9.9e-06 | 1 | 377 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2641-E | Raglan | Network | RAGCB4 | 09/08/2024 | 09:08 | 09/08/2024 | 14:36 | 0.27792 | 0.0008473 | 86 | 28208 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-17639-G | Gordonton | Network | GORCB13 | 13/08/2024 | 05:01 | 13/08/2024 | 06:40 | 0.016542 | 0.0002168 | 22 | 1679 | Planned interruptions on the network | Planned | Distribution Transformer Replacement
|  | INCD-176540-F | Transpower Hamilton | Network | HAMCB2802 | 13/08/2024 | 09:52 | 13/08/2024 | 16:09 | 0.034188 | 0.0030346 | 308 | 3470 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-2676-E | Glasgow | Network | GLACB2 | 14/08/2024 | 08:52 | 14/08/2024 | 10:36 | 0.0061184 | 5.91e-05 | 6 | 621 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-176545-F | Gordonton | Network | GORCB13 | 15/08/2024 | 19:31 | 15/08/2024 | 21:13 | 0.019094 | 0.0001872 | 19 | 1938 | Unplanned interruptions on the network | Defective Equipment | Loss or failure of oil
|  | INCD-176422-F | Weavers | Network | WEACB4 | 17/08/2024 | 05:43 | 17/08/2024 | 06:39 | 0.0066209 | 0.0001182 | 12 | 672 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-176497-F | Whatawhata | Network | RAGCB5 | 19/08/2024 | 02:55 | 19/08/2024 | 03:13 | 0.024918 | 0.0015271 | 155 | 2529.06 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-176497-F | Whatawhata | Network | RAGCB36 | 19/08/2024 | 02:55 | 19/08/2024 | 03:13 | 0.011414 | 0.0006995 | 71 | 1158.47 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-176533-F | Whatawhata | Network | TEUCB2 | 19/08/2024 | 06:57 | 19/08/2024 | 16:19 | 0.022856 | 4.93e-05 | 5 | 2319.86 | Unplanned interruptions on the network | Defective Equipment | Cable termination fails
|  | INCD-176533-F | Whatawhata | Network | TEUCB13 | 19/08/2024 | 06:57 | 19/08/2024 | 16:19 | 0.34285 | 0.0007389 | 75 | 34797.87 | Unplanned interruptions on the network | Defective Equipment | Cable termination fails
|  | INCD-17649-G | Wallace | Network | WALCB6 | 20/08/2024 | 16:08 | 20/08/2024 | 20:02 | 0.016138 | 6.9e-05 | 7 | 1638 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2706-E | Weavers | Network | WEACB3 | 26/08/2024 | 09:34 | 26/08/2024 | 15:23 | 0.044169 | 0.0001379 | 14 | 4483 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2710-E | Gordonton | Network | GORCB11 | 26/08/2024 | 10:17 | 26/08/2024 | 11:32 | 0.0007389 | 9.9e-06 | 1 | 75 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-176929-F | Weavers | Network | WEACB4 | 26/08/2024 | 15:43 | 26/08/2024 | 16:45 | 0.0073303 | 0.0001182 | 12 | 744 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-177005-F | Gordonton | Network | GORCB11 | 28/08/2024 | 09:01 | 28/08/2024 | 14:46 | 0.11725 | 0.000601 | 61 | 11901 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-2686-E | Gordonton | Network | GORCB11 | 28/08/2024 | 09:12 | 28/08/2024 | 14:24 | 0.19978 | 0.0007389 | 75 | 20277 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-177053-F | Horotiu | Network | HORCB4 | 28/08/2024 | 17:17 | 28/08/2024 | 17:24 | 0.008286 | 0.0010641 | 108 | 841 | Unplanned interruptions on the network | Defective Equipment | BBG contacts line
|  | INCD-177056-F | Te Uku | Network | TEUCB11 | 29/08/2024 | 02:39 | 29/08/2024 | 10:42 | 0.30469 | 0.014188 | 1440 | 30925 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-177162-F | Weavers | Network | WEACB3 | 30/08/2024 | 14:31 | 30/08/2024 | 14:46 | 0.0004434 | 2.96e-05 | 3 | 45 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-177198-F | Wallace Rd | Network | WALCB6 | 01/09/2024 | 04:07 | 01/09/2024 | 13:13 | 0.027193 | 0.0002365 | 24 | 2760 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-177200-F | Te Kauwhata | Network | TEKCB3 | 01/09/2024 | 02:35 | 01/09/2024 | 13:15 | 0.025222 | 3.94e-05 | 4 | 2560 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-177228-F | Wallace | Network | WALCB6 | 01/09/2024 | 13:24 | 01/09/2024 | 19:42 | 0.0037242 | 9.9e-06 | 1 | 378 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-2711-E | Raglan | Network | TEUCB11 | 02/09/2024 | 09:03 | 02/09/2024 | 12:34 | 0.098515 | 0.0004828 | 49 | 9999 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2721-E | Chartwell | Network | CHACB9 | 02/09/2024 | 10:14 | 02/09/2024 | 14:41 | 0.018414 | 6.9e-05 | 7 | 1869 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2635-E | Borman | Network | BORCB5 | 04/09/2024 | 06:33 | 04/09/2024 | 16:49 | 0.035174 | 0.0001084 | 11 | 3570 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-2743-E | Glasgow | Network | GLACB2 | 04/09/2024 | 09:00 | 04/09/2024 | 10:52 | 0.033124 | 0.0003054 | 31 | 3362 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2729-E | Whatawhata | Network | WHACB3 | 06/09/2024 | 09:19 | 06/09/2024 | 12:58 | 0.06343 | 0.0004926 | 50 | 6438 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2735-E | Whatawhata | Network | WHACB5 | 13/09/2024 | 09:05 | 13/09/2024 | 11:42 | 0.081983 | 0.0005222 | 53 | 8321 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-177698-F | Weavers | Network | NGACB2 | 15/09/2024 | 03:30 | 15/09/2024 | 12:51 | 0.0013575 | 6.9e-05 | 7 | 137.78 | Unplanned interruptions on the network | Defective Equipment | Line break at twist joint
|  | INCD-177728-F | Hampton Downs | Network | HPTCB5 | 16/09/2024 | 09:23 | 16/09/2024 | 14:32 | 0.0030444 | 9.9e-06 | 1 | 309 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2752-E | Gordonton | Network | GORCB12 | 20/09/2024 | 09:04 | 20/09/2024 | 11:45 | 0.077293 | 0.000532 | 54 | 7845 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-177976-F | Chartwell | Network | HAMCB2902 | 23/09/2024 | 08:34 | 23/09/2024 | 15:02 | 0.0038228 | 9.9e-06 | 1 | 388 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-178083-F | Wallace | Network | WALCB6 | 25/09/2024 | 05:49 | 25/09/2024 | 07:11 | 0.0024237 | 2.96e-05 | 3 | 246 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-178099-F | Te Kauwhata | Network | TEKCB5 | 25/09/2024 | 09:20 | 25/09/2024 | 12:19 | 0.0070544 | 3.94e-05 | 4 | 716 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-178127-F | Gordonton | Network | GORCB12 | 26/09/2024 | 09:05 | 26/09/2024 | 15:05 | 0.20899 | 0.0005813 | 59 | 21212 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2724-E | Tasman | Network | TASCB3 | 26/09/2024 | 19:10 | 27/09/2024 | 00:59 | 0.013754 | 3.94e-05 | 4 | 1396 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2815-E | Hoeka | Network | HOECB3 | 04/10/2024 | 09:01 | 04/10/2024 | 12:43 | 0.076771 | 0.0003448 | 35 | 7792 | Planned interruptions on the network | Planned | Distribution Transformer Replacement
|  | INCD-17661-G | Wallace | Network | WALCB6 | 07/10/2024 | 20:10 | 08/10/2024 | 00:06 | 0.0093008 | 3.94e-05 | 4 | 944 | Unplanned interruptions on the network | Defective Equipment | Intnl insulation failure
|  | INCD-2802-E | Weavers | Network | WEACB3 | 08/10/2024 | 09:35 | 08/10/2024 | 15:42 | 0.064682 | 0.0009853 | 100 | 6565 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-178557-F | Hoeka | Network | HOECB4 | 08/10/2024 | 19:01 | 08/10/2024 | 19:02 | 0.0009163 | 0.0004828 | 49 | 93 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (IN Zone)
|  | INCD-2821-E | Te Uku | Network | TEUCB13 | 10/10/2024 | 08:31 | 10/10/2024 | 12:49 | 0.081372 | 0.0003153 | 32 | 8259 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-178719-F | Te Uku | Network | TEUCB2 | 13/10/2024 | 16:22 | 13/10/2024 | 17:28 | 0.0026031 | 3.94e-05 | 4 | 264.21 | Unplanned interruptions on the network | Vegetation | Tree blown ovr on line (OUT of Zone)
|  | INCD-178719-F | Te Uku | Network | TEUCB12 | 13/10/2024 | 16:22 | 13/10/2024 | 17:28 | 0.096316 | 0.0014582 | 148 | 9775.79 | Unplanned interruptions on the network | Vegetation | Tree blown ovr on line (OUT of Zone)
|  | INCD-178863-F | Wallace Rd | Network | AVACB1 | 17/10/2024 | 09:04 | 17/10/2024 | 09:11 | 0.0050346 | 0.0007192 | 73 | 511 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2817-E | Ngaruawahia | Network | NGACB3 | 20/10/2024 | 09:36 | 20/10/2024 | 14:29 | 0.049075 | 0.0001675 | 17 | 4981 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-179164-F | Weavers | Network | WEACB5 | 22/10/2024 | 09:35 | 27/10/2024 | 00:00 | 0.05143 | 0.0001478 | 15 | 5220 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2823-E | Weavers | Network | WEACB3 | 25/10/2024 | 09:36 | 25/10/2024 | 14:04 | 0.050169 | 0.0001872 | 19 | 5092 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-179136-F | Hoeka | Network | HOECB1 | 25/10/2024 | 06:54 | 25/10/2024 | 15:08 | 0.0097343 | 1.97e-05 | 2 | 988 | Unplanned interruptions on the network | Defective Equipment | Loose connection
|  | INCD-179244-F | Weavers | Network | WEACB6 | 27/10/2024 | 10:05 | 27/10/2024 | 15:36 | 0.0065224 | 1.97e-05 | 2 | 662 | Unplanned interruptions on the network | Vegetation | Tree blown ovr on line (OUT of Zone)
|  | INCD-17669-G | Chartwell | Network | CHACB9 | 30/10/2024 | 12:09 | 30/10/2024 | 19:47 | 0.013537 | 2.96e-05 | 3 | 1374 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-179306-F | Chartwell | Network | CHACB9 | 30/10/2024 | 12:00 | 30/10/2024 | 13:32 | 0.0072514 | 7.88e-05 | 8 | 736 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-2849-E | Avalon | Network | AVACB8 | 01/11/2024 | 10:05 | 01/11/2024 | 14:41 | 0.47085 | 0.0017833 | 181 | 47790 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-179426-F | Peacockes Rd | Network | PEACB12 | 04/11/2024 | 07:53 | 04/11/2024 | 18:31 | 0.779 | 0.0071431 | 725 | 79066 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-2766-E | Weavers | Network | WEACB6 | 05/11/2024 | 09:40 | 05/11/2024 | 15:17 | 0.096959 | 0.0002956 | 30 | 9841 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-179475-F | Glasgow | Network | GLACB2 | 05/11/2024 | 08:23 | 05/11/2024 | 10:09 | 0.0031331 | 2.96e-05 | 3 | 318 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-2890-E | Transpower Hamilton | Network | HAMCB2902 | 05/11/2024 | 17:00 | 05/11/2024 | 18:24 | 0.16094 | 0.0072909 | 740 | 16335 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2863-E | Wallace | Network | WALCB2 | 07/11/2024 | 09:06 | 07/11/2024 | 11:09 | 0.11391 | 0.0009261 | 94 | 11562 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-179584-F | Gordonton | Network | GORCB12 | 08/11/2024 | 08:57 | 08/11/2024 | 11:57 | 0.0070938 | 3.94e-05 | 4 | 720 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-179633-F | Gordonton | Network | GORCB13 | 10/11/2024 | 22:15 | 11/11/2024 | 00:42 | 0.0072416 | 4.93e-05 | 5 | 735 | Unplanned interruptions on the network | Defective Equipment | Insulator split
|  | INCD-179687-F | Hoeka | Network | HOECB2 | 12/11/2024 | 10:15 | 12/11/2024 | 10:18 | 0.0017045 | 0.0007882 | 80 | 173 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-179720-F | Hoeka | Network | HOECB3 | 13/11/2024 | 10:06 | 13/11/2024 | 14:58 | 0.020139 | 6.9e-05 | 7 | 2044 | Planned interruptions on the network | Planned | Distribution Transformer Replacement
|  | INCD-179757-F | Gordonton | Private | GORCB11 | 14/11/2024 | 08:55 | 14/11/2024 | 09:19 | 0.0009458 | 3.94e-05 | 4 | 96 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-179844-F | Whatawhata | Network | WHACB5 | 17/11/2024 | 07:26 | 17/11/2024 | 08:38 | 0.020996 | 0.0002956 | 30 | 2131 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-179987-F | Te Uku | Network | TEUCB2 | 21/11/2024 | 09:03 | 21/11/2024 | 14:45 | 0.010719 | 3.94e-05 | 4 | 1088 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-17677-G | Weavers | Private | WEACB5 | 21/11/2024 | 16:44 | 21/11/2024 | 16:59 | 0.002069 | 0.0001379 | 14 | 210 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-180010-F | Raglan | Network | RAGCB3 | 22/11/2024 | 01:00 | 22/11/2024 | 01:32 | 0.0043647 | 0.0007389 | 75 | 443 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2929-E | Avalon | Network | AVACB3 | 29/11/2024 | 08:36 | 29/11/2024 | 11:51 | 0.38756 | 0.0019804 | 201 | 39336 | Planned interruptions on the network | Planned | New Connections
|  | INCD-2845-E | Weavers | Network | WEACB4 | 01/12/2024 | 09:07 | 01/12/2024 | 14:03 | 0.020414 | 6.9e-05 | 7 | 2072 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-180347-F | Whatawhata | Network | WHACB2 | 03/12/2024 | 09:00 | 03/12/2024 | 14:13 | 0.33326 | 0.0010936 | 111 | 33825 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2936-E | Transpower Hamilton | Network | HAMCB2862 | 04/12/2024 | 08:35 | 04/12/2024 | 15:55 | 0.23034 | 0.0040297 | 409 | 23379 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-180424-F | Raglan | Network | RAGCB6 | 05/12/2024 | 09:35 | 05/12/2024 | 11:23 | 0.056396 | 0.0005222 | 53 | 5724 | Unplanned interruptions on the network | Defective Equipment | Rotten crossarm
|  | INCD-2933-E | Weavers | Network | WHACB5 | 06/12/2024 | 08:09 | 06/12/2024 | 15:05 | 0.12452 | 0.0003054 | 31 | 12638 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-2918-E | Silverdale | Network | SILCB1 | 06/12/2024 | 09:32 | 06/12/2024 | 15:25 | 0.18336 | 0.0005222 | 53 | 18610 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2940-E | Horotiu | Network | HORCB5 | 09/12/2024 | 09:03 | 09/12/2024 | 12:25 | 0.20087 | 0.0011232 | 114 | 20388 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2962-E | Weavers | Network | WEACB2 | 11/12/2024 | 09:04 | 11/12/2024 | 14:38 | 0.0065815 | 1.97e-05 | 2 | 668 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-180646-F | Finlayson Rd | Network | FINCB2 | 13/12/2024 | 11:56 | 13/12/2024 | 14:48 | 0.0016946 | 9.9e-06 | 1 | 172 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2964-E | Gordonton | Network | GORCB11 | 18/12/2024 | 09:05 | 18/12/2024 | 13:47 | 0.072426 | 0.000266 | 27 | 7351 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2949-E | Hampton Downs | Network | HPTCB5 | 20/12/2024 | 09:06 | 20/12/2024 | 11:30 | 0.005675 | 3.94e-05 | 4 | 576 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-17707-G | Transpower Hamilton | Network | HAMCB2742 | 23/12/2024 | 09:26 | 23/12/2024 | 11:10 | 0.059056 | 0.0006207 | 63 | 5994 | Unplanned interruptions on the network | Defective Equipment | Cracked /brkn insulator
|  | INCD-17711-G | Whatawhata | Network | WHACB5 | 23/12/2024 | 06:38 | 23/12/2024 | 19:15 | 0.014917 | 1.97e-05 | 2 | 1514 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-181244-F | Finlayson Rd | Network | FINCB2 | 08/01/2025 | 17:21 | 08/01/2025 | 17:52 | 0.0003054 | 9.9e-06 | 1 | 31 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-181470-F | Gordonton | Network | GORCB11 | 15/01/2025 | 14:53 | 15/01/2025 | 17:03 | 0.0012808 | 9.9e-06 | 1 | 130 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-181558-F | Avalon Dr | Network | AVACB8 | 18/01/2025 | 00:03 | 18/01/2025 | 05:13 | 0.2427 | 0.0035075 | 356 | 24633 | Unplanned interruptions on the network | Defective Equipment | Faulty joint/connection
|  | INCD-17724-G | Whatawhata | Network | WHACB2 | 21/01/2025 | 07:36 | 21/01/2025 | 07:48 | 0.0003547 | 2.96e-05 | 3 | 36 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-181706-F | Chartwell | Network | CHACB13 | 22/01/2025 | 16:24 | 22/01/2025 | 18:13 | 0.91991 | 0.011744 | 1192 | 93368 | Unplanned interruptions on the network | Defective Equipment | Installed Incorrectly
|  | INCD-182180-F | Chartwell | Network | CHACB10 | 23/01/2025 | 00:25 | 06/02/2025 | 23:16 | 0.021932 | 0.0018227 | 185 | 2226 | Unplanned interruptions on the network | Defective Equipment | Installed Incorrectly
|  | INCD-181765-F | Steele Park | Network | STECB3 | 24/01/2025 | 09:03 | 24/01/2025 | 09:11 | 0.015764 | 0.0019705 | 200 | 1600 | Planned interruptions on the network | Planned | New Connections
|  | INCD-3009-E | Horotiu | Network | HORCB6 | 29/01/2025 | 08:30 | 29/01/2025 | 16:57 | 0.81664 | 0.0016651 | 169 | 82887 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2983-E | Gordonton | Network | GORCB12 | 29/01/2025 | 09:08 | 29/01/2025 | 14:59 | 0.67048 | 0.0019508 | 198 | 68052 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-181944-F | Peachgrove Rd | Network | PCHCB1 | 30/01/2025 | 08:14 | 30/01/2025 | 09:38 | 0.05675 | 0.0014188 | 144 | 5760 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-3023-E | Te Uku | Network | TEUCB11 | 31/01/2025 | 09:06 | 31/01/2025 | 12:08 | 0.0035863 | 1.97e-05 | 2 | 364 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-182098-F | Whatawhata | Private | WHACB4 | 04/02/2025 | 09:14 | 04/02/2025 | 09:36 | 0.0002168 | 9.9e-06 | 1 | 22 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-182197-F | Hampton Downs | Network | HPTCB3 | 08/02/2025 | 03:33 | 08/02/2025 | 05:01 | 0.030976 | 0.0003547 | 36 | 3144 | Unplanned interruptions on the network | Unknown | Fire Risk Mitigation Patrol - Sucessfully reclosed
|  | INCD-182506-F | Hoeka | Network | HOECB6 | 17/02/2025 | 05:19 | 17/02/2025 | 08:31 | 0.01135 | 5.91e-05 | 6 | 1152 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (OUT of Zone)
|  | INCD-182666-F | Weavers | Network | WEACB3 | 17/02/2025 | 09:48 | 17/02/2025 | 12:37 | 0.0016651 | 9.9e-06 | 1 | 169 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-182551-F | Pukete | Network | PUKCB10 | 17/02/2025 | 18:13 | 17/02/2025 | 19:21 | 0.00067 | 9.9e-06 | 1 | 68 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-182704-F | Te Uku | Network | TEUCB11 | 21/02/2025 | 08:30 | 21/02/2025 | 11:34 | 0.22796 | 0.0013005 | 132 | 23137 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-3055-E | Raglan | Network | RAGCB5 | 24/02/2025 | 08:36 | 24/02/2025 | 12:20 | 0.011035 | 4.93e-05 | 5 | 1120 | Planned interruptions on the network | Planned | Transformer Upgrade
|  | INCD-3060-E | Ngaruawahia | Network | NGACB5 | 27/02/2025 | 09:00 | 27/02/2025 | 16:04 | 0.7932 | 0.0038523 | 391 | 80507 | Planned interruptions on the network | Planned | New Connections
|  | INCD-182935-F | Claudelands | Network | CLACB16 | 28/02/2025 | 00:30 | 28/02/2025 | 00:34 | 0.034179 | 0.0085815 | 871 | 3469.06 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-101-K | Latham | Network | LATCB2 | 12/03/2025 | 06:04 | 12/03/2025 | 07:13 | 0.10932 | 0.0034385 | 349 | 11096 | Planned interruptions on the network | Planned | New Connections
|  | INCD-176-K | Latham | Network | LATCB2 | 13/03/2025 | 17:01 | 13/03/2025 | 18:02 | 0.069115 | 0.001133 | 115 | 7015 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-287-K | Sandwich Rd | Network | SANCB5 | 18/03/2025 | 09:09 | 18/03/2025 | 09:16 | 0.013104 | 0.001872 | 190 | 1330 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-0-N | Te Uku | Network | TEUCB11 | 18/03/2025 | 13:40 | 18/03/2025 | 16:08 | 0.014493 | 9.85e-05 | 10 | 1471 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-361-K | Transpower Hamilton | Network | HAMCB2722 | 20/03/2025 | 06:05 | 20/03/2025 | 06:55 | 0.037932 | 0.0007586 | 77 | 3850 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-376-K | Weavers | Network | WEACB3 | 20/03/2025 | 10:11 | 20/03/2025 | 11:08 | 0.0005616 | 9.9e-06 | 1 | 57 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-3082-E | Whatawhata | Network | WHACB2 | 24/03/2025 | 09:01 | 24/03/2025 | 09:16 | 0.0005912 | 3.94e-05 | 4 | 60 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-646-K | Weavers | Network | WEACB3 | 27/03/2025 | 10:19 | 27/03/2025 | 16:27 | 0.0036257 | 9.9e-06 | 1 | 368 | Unplanned interruptions on the network | Wildlife | Bird betw line & pole
|  | INCD-3117-E | Weavers | Network | WEACB4 | 30/03/2025 | 10:36 | 30/03/2025 | 12:22 | 0.0010444 | 9.9e-06 | 1 | 106 | Planned interruptions on the network | Planned | New Connections
|  | INCD-171039-F | Horotiu | Network | HORCB5 | 03/04/2024 | 09:02 | 03/04/2024 | 15:42 | 0.26531 | 0.0017636 | 179 | 26928 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2276-E | Finlayson | Network | FINCB3 | 03/04/2024 | 09:42 | 03/04/2024 | 13:32 | 0.0045322 | 1.97e-05 | 2 | 460 | Planned interruptions on the network | Planned | Transformer Upgrade
|  | INCD-17570-G | Transpower Hamilton | Network | HAMCB2802 | 03/04/2024 | 14:00 | 03/04/2024 | 14:57 | 0.0011232 | 1.97e-05 | 2 | 114 | Planned interruptions on the network | Defective Equipment | Pole Replacement
|  | INCD-171090-F | Horotiu | Network | HORCB5 | 03/04/2024 | 15:27 | 03/04/2024 | 15:42 | 0.013104 | 0.0008473 | 86 | 1330 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-17574-G | Gordonton | Network | GORCB12 | 10/04/2024 | 23:35 | 11/04/2024 | 06:02 | 0.087343 | 0.000601 | 61 | 8865 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-2298-E | Weavers | Network | WEACB3 | 12/04/2024 | 09:05 | 12/04/2024 | 13:44 | 0.17196 | 0.0006897 | 70 | 17453 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2287-E | Hampton Downs | Network | HPTCB5 | 12/04/2024 | 09:11 | 12/04/2024 | 11:19 | 0.0088278 | 6.9e-05 | 7 | 896 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-171410-F | Tasman | Network | TASCB4 | 13/04/2024 | 07:05 | 13/04/2024 | 07:08 | 0.0001182 | 3.94e-05 | 4 | 12 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-171426-F | Tasman | Network | TASCB4 | 13/04/2024 | 16:01 | 13/04/2024 | 17:30 | 0.015547 | 0.0001773 | 18 | 1578 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-171437-F | Steele Park | Network | STECB2 | 15/04/2024 | 07:01 | 15/04/2024 | 07:38 | 0.035361 | 0.0009557 | 97 | 3589 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2314-E | Finlayson | Network | FINCB2 | 15/04/2024 | 09:05 | 15/04/2024 | 10:42 | 0.0076455 | 7.88e-05 | 8 | 776 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2311-E | Hoeka | Network | HOECB1 | 16/04/2024 | 08:48 | 16/04/2024 | 16:03 | 0.62294 | 0.0015468 | 157 | 63227 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2248-E | Weavers | Network | WEACB6 | 17/04/2024 | 09:05 | 17/04/2024 | 17:52 | 0.031016 | 5.91e-05 | 6 | 3148 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-171713-F | Borman Rd | Network | BORCB2 | 24/04/2024 | 17:45 | 24/04/2024 | 19:00 | 0.044336 | 0.0005912 | 60 | 4500 | Unplanned interruptions on the network | Third_party | Hit by vehicle
|  | INCD-171760-F | Claudelands | Network | CLACB3 | 29/04/2024 | 08:22 | 29/04/2024 | 10:32 | 0.12168 | 0.000936 | 95 | 12350 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-171767-F | Transpower Hamilton | Network | HAMCB2802 | 29/04/2024 | 09:40 | 29/04/2024 | 10:40 | 0.0005912 | 9.9e-06 | 1 | 60 | Unplanned interruptions on the network | Wildlife | Rodent on HV terminals
|  | INCD-171788-F | Kent St | Network | KENCB9 | 30/04/2024 | 05:01 | 02/05/2024 | 20:25 | 0.0027587 | 9.85e-05 | 10 | 280 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2357-E | Sandwich | Network | SANCB3 | 01/05/2024 | 20:09 | 02/05/2024 | 02:59 | 0.18574 | 0.0004828 | 49 | 18852 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-172045-F | Claudelands | Network | CLACB3 | 07/05/2024 | 08:08 | 07/05/2024 | 11:59 | 0.21621 | 0.000936 | 95 | 21945 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2180-E | Te Kauwhata | Network | WEACB3 | 07/05/2024 | 09:05 | 07/05/2024 | 16:47 | 0.051075 | 0.0001182 | 12 | 5184 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-172140-F | Peacockes Rd | Network | PEACB12 | 08/05/2024 | 14:05 | 08/05/2024 | 22:34 | 0.86089 | 0.0076948 | 781 | 87378 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-172228-F | Transpower Hamilton | Network | HAMCB2862 | 10/05/2024 | 09:06 | 10/05/2024 | 12:30 | 0.31154 | 0.0015271 | 155 | 31620 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-172293-F | Raglan | Network | RAGCB6 | 12/05/2024 | 14:35 | 12/05/2024 | 15:59 | 0.079451 | 0.0009458 | 96 | 8064 | Unplanned interruptions on the network | Defective Equipment | Faulty joint/connection
|  | INCD-172297-F | Finlayson Rd | Network | FINCB2 | 12/05/2024 | 17:58 | 12/05/2024 | 21:31 | 0.058504 | 0.0002759 | 28 | 5938 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2382-E | Finlayson | Network | FINCB2 | 13/05/2024 | 08:55 | 13/05/2024 | 11:41 | 0.064908 | 0.000404 | 41 | 6588 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2422-E | Te Uku | Network | TEUCB13 | 16/05/2024 | 09:00 | 16/05/2024 | 16:41 | 0.12549 | 0.0002759 | 28 | 12737 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-172520-F | Hampton Downs | Network | HPTCB4 | 17/05/2024 | 11:00 | 17/05/2024 | 15:13 | 0.0024927 | 9.9e-06 | 1 | 253 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-172544-F | Silverdale | Network | SILCB4 | 18/05/2024 | 11:39 | 18/05/2024 | 16:23 | 0.25218 | 0.0027686 | 281 | 25596 | Unplanned interruptions on the network | Third_party | Tree felled into line (Third Party)
|  | INCD-2412-E | Hoeka | Network | HOECB1 | 21/05/2024 | 09:36 | 21/05/2024 | 15:35 | 0.0035371 | 9.9e-06 | 1 | 359 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-172675-F | Whatawhata | Network | WHACB3 | 21/05/2024 | 17:04 | 21/05/2024 | 18:04 | 0.0053204 | 8.87e-05 | 9 | 540 | Unplanned interruptions on the network | Defective Equipment | Pin stem corroded
|  | INCD-172690-F | Avalon Dr | Network | AVACB3 | 22/05/2024 | 01:23 | 22/05/2024 | 05:35 | 0.60777 | 0.0026208 | 266 | 61687 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-172915-F | Transpower Hamilton | Network | HAMCB2902 | 22/05/2024 | 11:02 | 22/05/2024 | 11:40 | 0.018345 | 0.0004828 | 49 | 1862 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2415-E | Chartwell | Network | CHACB9 | 23/05/2024 | 09:47 | 23/05/2024 | 15:43 | 0.16788 | 0.000532 | 54 | 17039 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-171724-F | Te Uku | Network | TEUCB11 | 24/05/2024 | 09:07 | 24/05/2024 | 12:13 | 0.023823 | 0.0001281 | 13 | 2418 | Planned interruptions on the network | Planned | New Connections
|  | INCD-172824-F | Te Kauwhata | Network | TEKCB5 | 24/05/2024 | 14:31 | 24/05/2024 | 18:02 | 0.0062366 | 2.96e-05 | 3 | 633 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-172913-F | Horotiu | Network | HORCB6 | 26/05/2024 | 14:44 | 26/05/2024 | 14:46 | 0.018573 | 0.010414 | 1057 | 1885.11 | Unplanned interruptions on the network | Adverse weather | High wind lne break
|  | INCD-17593-G | Transpower Hamilton | Network | HAMCB2902 | 27/05/2024 | 16:02 | 27/05/2024 | 16:35 | 0.014956 | 0.0004532 | 46 | 1518 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-172966-F | Transpower Hamilton | Network | HAMCB2902 | 28/05/2024 | 11:02 | 28/05/2024 | 11:48 | 0.022208 | 0.0004828 | 49 | 2254 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-173013-F | Horotiu | Network | HORCB4 | 29/05/2024 | 09:37 | 29/05/2024 | 23:13 | 0.73634 | 0.0046898 | 476 | 74736 | Unplanned interruptions on the network | Vegetation | Tree blown ovr on line (OUT of Zone)
|  | INCD-173067-F | Gordonton | Network | GORCB11 | 29/05/2024 | 13:35 | 29/05/2024 | 14:45 | 0.21805 | 0.0046996 | 477 | 22131 | Unplanned interruptions on the network | Adverse weather | Line clash high wind
|  | INCD-173091-F | Transpower Hamilton | Network | CHACB5 | 29/05/2024 | 14:31 | 29/05/2024 | 19:03 | 0.87625 | 0.018306 | 1858 | 88937 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (IN Zone)
|  | INCD-173091-F | Transpower Hamilton | Network | CHACB9 | 29/05/2024 | 14:31 | 29/05/2024 | 19:03 | 2.4715 | 0.024661 | 2503 | 250850.04 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (IN Zone)
|  | INCD-173101-F | Te Uku Wind Farm | Network | RAGCB2 | 29/05/2024 | 14:42 | 30/05/2024 | 21:19 | 11.052 | 0.0077047 | 782 | 1121741 | Unplanned interruptions on the network | Lightning | Lightning strike surge
|  | INCD-173096-F | Transpower Hamilton | Network | HAMCB2822 | 29/05/2024 | 14:42 | 29/05/2024 | 21:38 | 0.55666 | 0.013409 | 1361 | 56499 | Unplanned interruptions on the network | Defective Equipment | Insulator split
|  | INCD-173102-F | Te Uku | Network | TEUCB13 | 29/05/2024 | 14:50 | 31/05/2024 | 17:05 | 0.07313 | 0.0007291 | 74 | 7422.5 | Unplanned interruptions on the network | Vegetation | Tree blown ovr on line (OUT of Zone)
|  | INCD-173108-F | Weavers | Network | NGACB2 | 29/05/2024 | 15:01 | 29/05/2024 | 15:06 | 0.027883 | 0.0061283 | 622 | 2830 | Unplanned interruptions on the network | Adverse weather | Wind line clash
|  | INCD-173108-F | Weavers | Network | NGACB6 | 29/05/2024 | 15:01 | 29/05/2024 | 15:06 | 0.0043034 | 0.0009458 | 96 | 436.78 | Unplanned interruptions on the network | Adverse weather | Wind line clash
|  | INCD-173108-F | Weavers | Network | NGACB36 | 29/05/2024 | 15:01 | 29/05/2024 | 15:06 | 0.0013896 | 0.0003054 | 31 | 141.04 | Unplanned interruptions on the network | Adverse weather | Wind line clash
|  | INCD-173110-F | Gordonton | Network | GORCB13 | 29/05/2024 | 15:06 | 31/05/2024 | 06:39 | 1.465 | 0.0061283 | 622 | 148695 | Unplanned interruptions on the network | Adverse weather | Pole blown over
|  | INCD-17598-G | Glasgow St | Network | GLACB2 | 30/05/2024 | 00:54 | 30/05/2024 | 09:35 | 0.015399 | 2.96e-05 | 3 | 1563 | Unplanned interruptions on the network | Defective Equipment | Nut or bolt loose
|  | INCD-173278-F | Whatawhata | Network | WHACB2 | 30/05/2024 | 08:44 | 30/05/2024 | 11:01 | 0.0013498 | 9.9e-06 | 1 | 137 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-173418-F | Raglan | Network | RAGCB6 | 31/05/2024 | 00:25 | 31/05/2024 | 00:44 | 0.0001872 | 9.9e-06 | 1 | 19 | Unplanned interruptions on the network | Adverse weather | Line clash high wind
|  | INCD-173390-F | Finlayson | Network | FINCB2 | 31/05/2024 | 10:22 | 31/05/2024 | 12:38 | 0.073894 | 0.0005912 | 60 | 7500 | Unplanned interruptions on the network | Defective Equipment | Faulty joint/connection
|  | INCD-173393-F | Hampton Downs | Network | HPTCB5 | 31/05/2024 | 10:28 | 31/05/2024 | 11:00 | 0.0028375 | 8.87e-05 | 9 | 288 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-173448-F | Weavers | Network | WEACB6 | 01/06/2024 | 09:15 | 01/06/2024 | 16:35 | 0.0043351 | 9.9e-06 | 1 | 440 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-173536-F | Peacockes Rd | Network | PEACB12 | 04/06/2024 | 09:48 | 08/06/2024 | 12:40 | 0.058445 | 9.9e-06 | 1 | 5932 | Unplanned interruptions on the network | Defective Equipment | Faulty line spacer
|  | INCD-173542-F | Peacockes Rd | Network | PEACB12 | 04/06/2024 | 10:07 | 04/06/2024 | 10:18 | 0.014414 | 0.0013596 | 138 | 1463 | Unplanned interruptions on the network | Defective Equipment | Faulty line spacer
|  | INCD-173568-F | Whitiora School | Network | WHICB4 | 04/06/2024 | 16:29 | 04/06/2024 | 16:30 | 0.0014582 | 0.0014582 | 148 | 148 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-2187-E | Te Kauwhata | Network | TEKCB5 | 09/06/2024 | 08:34 | 09/06/2024 | 16:40 | 0.11474 | 0.0002463 | 25 | 11646 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-2463-E | Weavers | Network | WEACB3 | 14/06/2024 | 09:17 | 14/06/2024 | 15:06 | 0.070012 | 0.0002562 | 26 | 7106 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-173985-F | Hoeka | Network | HOECB1 | 14/06/2024 | 13:58 | 15/06/2024 | 14:55 | 0.07145 | 0.0001379 | 14 | 7252 | Unplanned interruptions on the network | Vegetation | Tree blown ovr on line (OUT of Zone)
|  | INCD-2470-E | Glasgow | Network | GLACB5 | 16/06/2024 | 09:02 | 16/06/2024 | 10:08 | 0.061125 | 0.0009261 | 94 | 6204 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-174042-F | Raglan | Network | RAGCB4 | 16/06/2024 | 23:11 | 17/06/2024 | 05:21 | 0.91598 | 0.0065027 | 660 | 92969.38 | Unplanned interruptions on the network | Defective Equipment | Burning frm prev flt
|  | INCD-17609-G | Hoeka | Network | HOECB1 | 19/06/2024 | 20:28 | 19/06/2024 | 20:36 | 0.0031528 | 0.0003941 | 40 | 320 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2497-E | Glasgow | Network | GLACB6 | 20/06/2024 | 09:09 | 20/06/2024 | 13:43 | 0.05547 | 0.0002562 | 26 | 5630 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-174324-F | Sandwich | Network | SANCB2 | 24/06/2024 | 09:42 | 24/06/2024 | 10:55 | 0.053942 | 0.0007389 | 75 | 5475 | Unplanned interruptions on the network | Defective Equipment | Connect/jumper loose
|  | INCD-174426-F | Tasman | Network | TASCB1 | 26/06/2024 | 19:03 | 26/06/2024 | 19:34 | 0.0039706 | 0.0001281 | 13 | 403 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-174639-F | Horotiu | Network | HORCB5 | 03/07/2024 | 08:26 | 03/07/2024 | 11:33 | 0.0018424 | 9.9e-06 | 1 | 187 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-174659-F | Whatawhata | Network | WHACB4 | 03/07/2024 | 17:47 | 03/07/2024 | 20:13 | 0.0086308 | 5.91e-05 | 6 | 876 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-17619-G | Te Kauwhata | Network | TEKCB5 | 04/07/2024 | 17:11 | 04/07/2024 | 18:53 | 0.0040198 | 3.94e-05 | 4 | 408 | Unplanned interruptions on the network | Wildlife | Bird betw line & pole
|  | INCD-2524-E | Glasgow | Network | GLACB2 | 05/07/2024 | 08:59 | 05/07/2024 | 14:41 | 0.18154 | 0.0005517 | 56 | 18426 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-174711-F | Finlayson | Network | FINCB1 | 05/07/2024 | 09:20 | 05/07/2024 | 09:22 | 0.0067588 | 0.0040986 | 416 | 686 | Unplanned interruptions on the network | Defective Equipment | Line break at twist joint
|  | INCD-174757-F | Weavers | Network | WEACB2 | 06/07/2024 | 11:51 | 06/07/2024 | 13:41 | 0.0010838 | 9.9e-06 | 1 | 110 | Unplanned interruptions on the network | Wildlife | Bird betw line & pole
|  | INCD-2535-E | Finlayson | Network | FINCB1 | 09/07/2024 | 09:16 | 09/07/2024 | 11:32 | 0.071017 | 0.0005222 | 53 | 7208 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2555-E | Weavers | Network | WEACB4 | 10/07/2024 | 09:13 | 10/07/2024 | 12:30 | 0.02135 | 0.0001084 | 11 | 2167 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-175073-F | Pukete | Network | PUKCB8 | 13/07/2024 | 12:50 | 13/07/2024 | 18:29 | 0.04009 | 0.0002956 | 30 | 4069 | Unplanned interruptions on the network | Defective Equipment | Cable termination fails
|  | INCD-2550-E | Te Uku | Network | TEUCB11 | 15/07/2024 | 09:30 | 15/07/2024 | 12:02 | 0.0044927 | 2.96e-05 | 3 | 456 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-175162-F | Horotiu | Private | HORCB5 | 15/07/2024 | 18:22 | 15/07/2024 | 19:21 | 0.0034878 | 5.91e-05 | 6 | 354 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-175180-F | Claudelands | Network | CLACB16 | 16/07/2024 | 08:42 | 16/07/2024 | 11:55 | 0.0019015 | 9.9e-06 | 1 | 193 | Planned interruptions on the network | Planned | New Connections
|  | INCD-2547-E | Transpower Hamilton | Network | HAMCB2802 | 17/07/2024 | 09:18 | 17/07/2024 | 12:49 | 0.05613 | 0.000266 | 27 | 5697 | Planned interruptions on the network | Planned | New Connections
|  | INCD-2549-E | Finlayson | Network | FINCB2 | 17/07/2024 | 10:11 | 17/07/2024 | 13:51 | 0.0086702 | 3.94e-05 | 4 | 880 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-175327-F | Latham Court | Network | LATCB3 | 18/07/2024 | 17:56 | 18/07/2024 | 23:27 | 0.26371 | 0.0067687 | 687 | 26766 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-17630-G | Hoeka | Private | HOECB2 | 20/07/2024 | 08:33 | 20/07/2024 | 08:53 | 0.0001971 | 9.9e-06 | 1 | 20 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-2486-E | Whatawhata | Network | WHACB3 | 23/07/2024 | 09:01 | 23/07/2024 | 15:56 | 0.20698 | 0.0007094 | 72 | 21008 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-4607-H | Foreman Rd | Network | TASCB3 | 24/07/2024 | 09:01 | 24/07/2024 | 12:38 | 0.006414 | 2.96e-05 | 3 | 651 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-175641-F | Gordonton | Network | GORCB11 | 30/07/2024 | 15:42 | 30/07/2024 | 17:20 | 0.0028966 | 2.96e-05 | 3 | 294 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2494-E | Te Kauwhata | Network | TEKCB5 | 31/07/2024 | 09:03 | 31/07/2024 | 14:51 | 0.079096 | 0.0002365 | 24 | 8028 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-175702-F | Avalon Dr | Network | AVACB3 | 01/08/2024 | 09:04 | 01/08/2024 | 12:52 | 0.13928 | 0.0006109 | 62 | 14136 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-2507-E | Te Kauwhata | Network | TEKCB5 | 02/08/2024 | 09:06 | 02/08/2024 | 16:48 | 0.054071 | 0.0003448 | 35 | 5488 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-2661-E | Ngaruawahia | Network | NGACB2 | 08/08/2024 | 09:09 | 08/08/2024 | 14:39 | 0.09286 | 0.0002956 | 30 | 9425 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-176225-F | Claudelands | Network | CLACB10 | 13/08/2024 | 08:31 | 14/08/2024 | 08:22 | 0.24286 | 0.0005714 | 58 | 24650 | Planned interruptions on the network | Planned | Distribution Transformer Replacement
|  | INCD-176274-F | Latham Court | Network | LATCB3 | 14/08/2024 | 00:14 | 14/08/2024 | 03:04 | 0.1983 | 0.016779 | 1703 | 20127 | Unplanned interruptions on the network | Defective Equipment | LV Panel fire
|  | INCD-2674-E | Glasgow | Network | GLACB2 | 14/08/2024 | 11:20 | 14/08/2024 | 13:14 | 0.020217 | 0.0001773 | 18 | 2052 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2671-E | Glasgow | Network | GLACB2 | 14/08/2024 | 11:32 | 14/08/2024 | 13:01 | 0.01403 | 0.0001576 | 16 | 1424 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-176341-F | Weavers | Network | WEACB4 | 14/08/2024 | 20:13 | 14/08/2024 | 22:46 | 0.031794 | 0.0002168 | 22 | 3227 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-2632-E | Borman | Network | BORCB5 | 15/08/2024 | 09:41 | 15/08/2024 | 15:53 | 0.084298 | 0.0002266 | 23 | 8556 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-176450-F | Te Uku | Network | TEUCB11 | 17/08/2024 | 15:38 | 17/08/2024 | 16:23 | 0.005074 | 0.008217 | 834 | 515 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2692-E | Horotiu | Network | HORCB7 | 18/08/2024 | 08:10 | 18/08/2024 | 11:31 | 0.0019804 | 9.9e-06 | 1 | 201 | Planned interruptions on the network | Planned | New Connections
|  | INCD-17642-G | Chartwell | Network | CHACB9 | 18/08/2024 | 09:31 | 18/08/2024 | 13:06 | 0.0042366 | 1.97e-05 | 2 | 430 | Unplanned interruptions on the network | Vegetation | Tree blown ovr on line (OUT of Zone)
|  | INCD-17643-G | Gordonton | Network | GORCB13 | 18/08/2024 | 11:36 | 18/08/2024 | 11:57 | 0.0004138 | 1.97e-05 | 2 | 42 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (OUT of Zone)
|  | INCD-176497-F | Whatawhata | Network | TEUCB11 | 19/08/2024 | 02:55 | 19/08/2024 | 03:13 | 0.13009 | 0.0074978 | 761 | 13203.61 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-176637-F | Gordonton | Network | GORCB12 | 19/08/2024 | 22:59 | 20/08/2024 | 01:10 | 0.086919 | 0.0027193 | 276 | 8822 | Unplanned interruptions on the network | Defective Equipment | Loose connection
|  | INCD-176759-F | Steele Park | Network | STECB3 | 21/08/2024 | 15:16 | 21/08/2024 | 15:19 | 0.0026306 | 0.0008769 | 89 | 267 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-176764-F | Weavers | Network | WEACB3 | 21/08/2024 | 12:18 | 21/08/2024 | 17:23 | 0.003005 | 9.9e-06 | 1 | 305 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-2574-E | Weavers | Network | WEACB6 | 22/08/2024 | 09:41 | 22/08/2024 | 16:40 | 0.66464 | 0.0015863 | 161 | 67459 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-176835-F | Claudelands | Network | CLACB16 | 23/08/2024 | 00:07 | 23/08/2024 | 07:06 | 0.0074485 | 0.0003547 | 36 | 756 | Unplanned interruptions on the network | Defective Equipment | Intnl insulation failure
|  | INCD-2657-E | Cobham | Network | COBCB11 | 24/08/2024 | 08:02 | 24/08/2024 | 13:47 | 0.0067982 | 1.97e-05 | 2 | 690 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-177069-F | Weavers | Network | WEACB2 | 29/08/2024 | 09:05 | 29/08/2024 | 10:07 | 0.051933 | 0.0008473 | 86 | 5271 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-177108-F | Wallace | Network | WALCB5 | 29/08/2024 | 22:53 | 30/08/2024 | 05:16 | 0.19245 | 0.0005025 | 51 | 19533 | Unplanned interruptions on the network | Defective Equipment | Intnl insulation failure
|  | INCD-177209-F | Transpower Hamilton | Network | HAMCB2802 | 01/09/2024 | 08:19 | 01/09/2024 | 16:38 | 0.019666 | 3.94e-05 | 4 | 1996 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-177233-F | Borman Rd | Network | CHACB13 | 02/09/2024 | 04:03 | 02/09/2024 | 05:01 | 0.12923 | 0.0022562 | 229 | 13116 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-177283-F | Tasman | Network | TASCB2 | 02/09/2024 | 19:59 | 02/09/2024 | 21:32 | 0.001005 | 1.97e-05 | 2 | 102 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2740-E | Whatawhata | Network | WHACB3 | 05/09/2024 | 09:04 | 05/09/2024 | 14:20 | 0.01868 | 5.91e-05 | 6 | 1896 | Planned interruptions on the network | Planned | Transformer Upgrade
|  | INCD-2626-E | Chartwell | Network | CHACB9 | 05/09/2024 | 09:05 | 05/09/2024 | 13:22 | 0.18279 | 0.0007291 | 74 | 18553 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-177539-F | Pukete | Private | PUKCB10 | 09/09/2024 | 16:14 | 09/09/2024 | 16:34 | 0.0013794 | 6.9e-05 | 7 | 140 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-2783-E | Whatawhata | Private | WHACB3 | 10/09/2024 | 10:20 | 10/09/2024 | 10:56 | 0.0010641 | 2.96e-05 | 3 | 108 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-177614-F | Pukete | Network | PUKCB10 | 12/09/2024 | 06:14 | 12/09/2024 | 07:13 | 0.016227 | 0.0002759 | 28 | 1647 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-177621-F | Te Kauwhata | Network | TEKCB5 | 12/09/2024 | 09:00 | 12/09/2024 | 15:51 | 0.28049 | 0.0007094 | 72 | 28469 | Planned interruptions on the network | Planned | New Connections
|  | INCD-2746-E | Finlayson | Network | FINCB1 | 12/09/2024 | 09:11 | 12/09/2024 | 14:00 | 0.01139 | 3.94e-05 | 4 | 1156 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-177834-F | Te Uku | Network | TEUCB11 | 18/09/2024 | 12:13 | 18/09/2024 | 17:33 | 0.0031528 | 9.9e-06 | 1 | 320 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-177901-F | Weavers | Network | WEACB3 | 20/09/2024 | 08:48 | 20/09/2024 | 10:09 | 0.0007981 | 9.9e-06 | 1 | 81 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-177935-F | Ngaruawahia | Network | NGACB6 | 20/09/2024 | 17:03 | 20/09/2024 | 23:15 | 0.01466 | 3.94e-05 | 4 | 1488 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-178040-F | Gordonton | Network | GORCB11 | 24/09/2024 | 02:20 | 24/09/2024 | 10:25 | 0.81429 | 0.0018523 | 188 | 82648 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-2769-E | Wallace | Network | WALCB6 | 04/10/2024 | 10:13 | 04/10/2024 | 13:42 | 0.1116 | 0.0005714 | 58 | 11327 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-178564-F | Massey St | Network | MASCB12 | 09/10/2024 | 08:05 | 09/10/2024 | 15:22 | 0.18083 | 0.0004138 | 42 | 18354 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-178596-F | Sandwich | Network | SANCB4 | 10/10/2024 | 08:00 | 10/10/2024 | 08:02 | 0.021449 | 0.01139 | 1156 | 2177 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2808-E | Wallace | Network | WALCB6 | 11/10/2024 | 09:53 | 11/10/2024 | 15:07 | 0.21965 | 0.0006995 | 71 | 22294 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-178789-F | Whatawhata | Network | WHACB4 | 15/10/2024 | 09:10 | 15/10/2024 | 09:47 | 0.0014582 | 3.94e-05 | 4 | 148 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-178815-F | Chartwell | Network | CHACB9 | 16/10/2024 | 06:57 | 16/10/2024 | 07:20 | 0.0002266 | 9.9e-06 | 1 | 23 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-178910-F | Pukete | Network | PUKCB10 | 18/10/2024 | 09:07 | 18/10/2024 | 14:55 | 0.08753 | 0.0002562 | 26 | 8884 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-2822-E | Sandwich | Network | SANCB3 | 24/10/2024 | 09:01 | 24/10/2024 | 13:19 | 0.19319 | 0.0007488 | 76 | 19608 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-179112-F | Weavers | Network | WEACB3 | 24/10/2024 | 07:03 | 24/10/2024 | 12:50 | 0.0034188 | 9.9e-06 | 1 | 347 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2843-E | Te Uku | Network | TEUCB11 | 25/10/2024 | 08:31 | 25/10/2024 | 16:26 | 0.68551 | 0.001606 | 163 | 69577 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-179251-F | Horotiu | Network | HORCB5 | 28/10/2024 | 06:00 | 28/10/2024 | 10:42 | 0.10253 | 0.0003645 | 37 | 10406 | Unplanned interruptions on the network | Defective Equipment | Jumpers come off
|  | INCD-179246-F | Horotiu | Network | HORCB5 | 28/10/2024 | 06:00 | 28/10/2024 | 07:27 | 0.014444 | 0.0001675 | 17 | 1466 | Unplanned interruptions on the network | Defective Equipment | Jumpers come off
|  | INCD-2872-E | Whatawhata | Network | WHACB2 | 04/11/2024 | 09:37 | 04/11/2024 | 11:24 | 0.0021084 | 1.97e-05 | 2 | 214 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-179487-F | Whatawhata | Private | WHACB4 | 05/11/2024 | 12:18 | 05/11/2024 | 12:38 | 0.0011823 | 5.91e-05 | 6 | 120 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-2866-E | Weavers | Network | WEACB6 | 08/11/2024 | 10:08 | 08/11/2024 | 14:18 | 0.0049263 | 1.97e-05 | 2 | 500 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-179625-F | Glasgow | Network | GLACB2 | 10/11/2024 | 11:22 | 10/11/2024 | 12:40 | 0.0023055 | 2.96e-05 | 3 | 234 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-179627-F | Avalon Dr | Network | AVACB8 | 10/11/2024 | 12:33 | 10/11/2024 | 12:38 | 0.0094584 | 0.0018917 | 192 | 960 | Unplanned interruptions on the network | Defective Equipment | Overheated connections
|  | INCD-179829-F | Glasgow | Network | GLACB2 | 16/11/2024 | 06:28 | 16/11/2024 | 09:28 | 0.0017735 | 9.9e-06 | 1 | 180 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-180010-F | Raglan | Network | RAGCB4 | 22/11/2024 | 01:00 | 22/11/2024 | 01:32 | 0.092342 | 0.0065125 | 661 | 9372.45 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-180075-F | Weavers | Network | WEACB3 | 25/11/2024 | 08:31 | 25/11/2024 | 12:14 | 0.095983 | 0.0004532 | 46 | 9742 | Unplanned interruptions on the network | Defective Equipment | Nut or bolt loose
|  | INCD-2883-E | Borman | Network | BORCB2 | 26/11/2024 | 09:34 | 26/11/2024 | 13:25 | 0.035873 | 0.0001675 | 17 | 3641 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-2898-E | Weavers | Network | NGACB2 | 28/11/2024 | 09:31 | 28/11/2024 | 17:32 | 0.014621 | 3.94e-05 | 4 | 1484 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2912-E | Chartwell | Network | CHACB9 | 01/12/2024 | 08:58 | 01/12/2024 | 17:40 | 0.23144 | 0.0004434 | 45 | 23490 | Planned interruptions on the network | Planned | Transformer Upgrade
|  | INCD-180338-F | Te Kauwhata | Network | TEKCB5 | 03/12/2024 | 05:58 | 03/12/2024 | 12:09 | 0.20656 | 0.0005714 | 58 | 20965 | Unplanned interruptions on the network | Defective Equipment | Line break at twist joint
|  | INCD-2916-E | Whatawhata | Network | WHACB5 | 03/12/2024 | 09:06 | 03/12/2024 | 12:20 | 0.045873 | 0.0002365 | 24 | 4656 | Planned interruptions on the network | Planned | Transformer Upgrade
|  | INCD-2900-E | Borman | Network | BORCB6 | 06/12/2024 | 09:07 | 06/12/2024 | 12:30 | 0.26653 | 0.0014089 | 143 | 27052 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-17689-G | Te Uku | Network | TEUCB12 | 06/12/2024 | 17:18 | 06/12/2024 | 18:06 | 0.0028375 | 5.91e-05 | 6 | 288 | Unplanned interruptions on the network | Defective Equipment | Contact problem
|  | INCD-17690-G | Transpower Hamilton | Network | HAMCB2762 | 07/12/2024 | 09:28 | 07/12/2024 | 15:42 | 0.10686 | 0.0002857 | 29 | 10846 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-17691-G | Peacockes | Network | PEACB12 | 07/12/2024 | 06:53 | 07/12/2024 | 10:40 | 0.004473 | 1.97e-05 | 2 | 454 | Unplanned interruptions on the network | Defective Equipment | Mal adjusted from wear
|  | INCD-2884-E | Borman | Network | BORCB2 | 12/12/2024 | 09:33 | 12/12/2024 | 15:55 | 0.28511 | 0.0007685 | 78 | 28938 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-180637-F | Latham Court | Network | LATCB1 | 13/12/2024 | 10:03 | 13/12/2024 | 12:33 | 0.20469 | 0.0013695 | 139 | 20775 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-17698-G | Glasgow St | Network | GLACB6 | 14/12/2024 | 08:08 | 14/12/2024 | 12:30 | 0.068179 | 0.000266 | 27 | 6920 | Unplanned interruptions on the network | Defective Equipment | Faulty joint/connection
|  | INCD-17700-G | Weavers | Network | WEACB2 | 15/12/2024 | 10:36 | 15/12/2024 | 12:45 | 0.001271 | 9.9e-06 | 1 | 129 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-2951-E | Hoeka | Network | HOECB1 | 18/12/2024 | 09:04 | 18/12/2024 | 12:25 | 0.30723 | 0.001606 | 163 | 31183 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-180872-F | Weavers | Network | WEACB3 | 20/12/2024 | 12:11 | 20/12/2024 | 16:36 | 0.0052218 | 1.97e-05 | 2 | 530 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-17708-G | Weavers | Network | WEACB2 | 23/12/2024 | 07:09 | 23/12/2024 | 10:42 | 0.012592 | 5.91e-05 | 6 | 1278 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-180969-F | Whatawhata | Private | WHACB2 | 24/12/2024 | 13:38 | 24/12/2024 | 14:04 | 0.0043548 | 0.0001675 | 17 | 442 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-17713-G | Glasgow St | Network | GLACB6 | 25/12/2024 | 04:20 | 25/12/2024 | 05:53 | 0.010079 | 0.0001084 | 11 | 1023 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-181095-F | Weavers | Network | FINCB2 | 02/01/2025 | 03:59 | 02/01/2025 | 04:00 | 0.0060244 | 0.005478 | 556 | 611.46 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-181125-F | Te Kauwhata | Network | TEKCB3 | 03/01/2025 | 21:40 | 04/01/2025 | 15:13 | 0.031124 | 2.96e-05 | 3 | 3159 | Unplanned interruptions on the network | Third_party | Damaged by extr impact
|  | INCD-181148-F | Weavers | Network | WEACB6 | 05/01/2025 | 14:44 | 06/01/2025 | 00:51 | 0.023922 | 3.94e-05 | 4 | 2428 | Unplanned interruptions on the network | Defective Equipment | Intnl insulation failure
|  | INCD-181169-F | Avalon | Network | AVACB8 | 06/01/2025 | 12:19 | 06/01/2025 | 13:24 | 0.0057637 | 8.87e-05 | 9 | 585 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-181522-F | Te Uku | Network | TEUCB11 | 16/01/2025 | 22:40 | 17/01/2025 | 18:03 | 0.4397 | 0.0065421 | 664 | 44628 | Unplanned interruptions on the network | Defective Equipment | Insulator split
|  | INCD-181607-F | Te Uku | Network | TEUCB11 | 17/01/2025 | 09:16 | 17/01/2025 | 09:35 | 0.031715 | 0.0016651 | 169 | 3219 | Unplanned interruptions on the network | Defective Equipment | Insulator split
|  | INCD-181608-F | Te Uku | Network | TEUCB11 | 17/01/2025 | 09:16 | 17/01/2025 | 09:37 | 0.052504 | 0.0024533 | 249 | 5329 | Unplanned interruptions on the network | Defective Equipment | Insulator split
|  | INCD-181651-F | Glasgow St | Network | GLACB2 | 21/01/2025 | 08:46 | 21/01/2025 | 11:15 | 0.03804 | 0.0002562 | 26 | 3861 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2886-E | Borman | Network | BORCB2 | 21/01/2025 | 09:32 | 21/01/2025 | 15:33 | 0.056524 | 0.0001576 | 16 | 5737 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-181678-F | Gordonton | Network | GORCB11 | 21/01/2025 | 22:38 | 22/01/2025 | 00:05 | 0.12176 | 0.0047391 | 481 | 12358 | Unplanned interruptions on the network | Unknown | Fire Risk Mitigation Patrol - Sucessfully reclosed
|  | INCD-181706-F | Chartwell | Network | CHACB5 | 22/01/2025 | 16:24 | 22/01/2025 | 18:13 | 0.15454 | 0.009153 | 929 | 15685 | Unplanned interruptions on the network | Defective Equipment | Installed Incorrectly
|  | INCD-181706-F | Chartwell | Network | CHACB6 | 22/01/2025 | 16:24 | 22/01/2025 | 18:13 | 0.092426 | 0.0009951 | 101 | 9381 | Unplanned interruptions on the network | Defective Equipment | Installed Incorrectly
|  | INCD-181706-F | Chartwell | Network | CHACB15 | 22/01/2025 | 16:24 | 22/01/2025 | 18:13 | 1.2061 | 0.012178 | 1236 | 122411 | Unplanned interruptions on the network | Defective Equipment | Installed Incorrectly
|  | INCD-182179-F | Chartwell | Network | CHACB9 | 23/01/2025 | 00:33 | 23/01/2025 | 03:38 | 0.091215 | 0.010788 | 1095 | 9258 | Unplanned interruptions on the network | Defective Equipment | Installed Incorrectly
|  | INCD-181740-F | Chartwell | Network | CHACB13 | 23/01/2025 | 10:02 | 23/01/2025 | 12:41 | 0.084594 | 0.000532 | 54 | 8586 | Planned interruptions on the network | Planned | Distribution Transformer Replacement
|  | INCD-2978-E | Te Uku | Network | TEUCB12 | 23/01/2025 | 10:14 | 23/01/2025 | 15:45 | 0.1174 | 0.0003547 | 36 | 11916 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-181930-F | Glasgow St | Network | GLACB2 | 29/01/2025 | 16:56 | 29/01/2025 | 18:27 | 0.014266 | 0.0001576 | 16 | 1448 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2819-E | Avalon Substation | Network | AVACB8 | 30/01/2025 | 09:02 | 30/01/2025 | 16:02 | 0.26428 | 0.0006306 | 64 | 26823.45 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-3007-E | Chartwell | Network | CHACB15 | 03/02/2025 | 08:32 | 03/02/2025 | 10:41 | 0.37887 | 0.0030149 | 306 | 38454 | Planned interruptions on the network | Planned | New Connections
|  | INCD-182184-F | Chartwell | Network | CHACB15 | 04/02/2025 | 15:08 | 04/02/2025 | 16:02 | 0.078209 | 0.0014483 | 147 | 7938 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-2990-E | Sandwich | Network | SANCB7 | 05/02/2025 | 09:15 | 05/02/2025 | 15:03 | 0.017143 | 4.93e-05 | 5 | 1740 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-182196-F | Weavers | Network | WEACB6 | 08/02/2025 | 00:21 | 08/02/2025 | 03:03 | 0.0015961 | 9.9e-06 | 1 | 162 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-182263-F | Chartwell | Network | CHACB5 | 11/02/2025 | 06:14 | 11/02/2025 | 12:17 | 0.47591 | 0.0013498 | 137 | 48303 | Unplanned interruptions on the network | Defective Equipment | Cable joint fails
|  | INCD-3001-E | Gordonton | Network | GORCB12 | 12/02/2025 | 08:15 | 12/02/2025 | 13:23 | 0.0091037 | 2.96e-05 | 3 | 924 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-182398-F | Te Uku | Private | TEUCB12 | 13/02/2025 | 12:41 | 13/02/2025 | 13:05 | 0.0014188 | 5.91e-05 | 6 | 144 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-182467-F | Weavers | Private | WEACB3 | 15/02/2025 | 09:56 | 27/02/2025 | 10:30 | 0.17059 | 9.9e-06 | 1 | 17314 | Unplanned interruptions on the network | Third_party | Temp Disconnect / safety isolation
|  | INCD-182479-F | MAF | Network | MAFCB3 | 16/02/2025 | 09:00 | 16/02/2025 | 15:07 | 0.014109 | 3.94e-05 | 4 | 1432 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-182496-F | Raglan | Network | RAGCB2 | 16/02/2025 | 16:25 | 16/02/2025 | 22:43 | 0.36498 | 0.0009655 | 98 | 37044 | Unplanned interruptions on the network | Defective Equipment | Cable termination fails
|  | INCD-182534-F | Whatawhata | Network | WHACB3 | 17/02/2025 | 13:46 | 17/02/2025 | 19:30 | 0.21003 | 0.0006109 | 62 | 21317 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (OUT of Zone)
|  | INCD-182648-F | Whatawhata | Private | WHACB3 | 19/02/2025 | 22:30 | 19/02/2025 | 23:03 | 0.0032513 | 9.85e-05 | 10 | 330 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-3041-E | Weavers | Network | WEACB6 | 21/02/2025 | 09:19 | 21/02/2025 | 11:12 | 0.0022267 | 1.97e-05 | 2 | 226 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-3059-E | Latham | Network | LATCB3 | 24/02/2025 | 09:01 | 24/02/2025 | 18:21 | 1.0873 | 0.0052317 | 531 | 110358 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-182810-F | Pukete | Network | PUKCB2 | 25/02/2025 | 08:21 | 25/02/2025 | 17:31 | 0.0054189 | 9.9e-06 | 1 | 550 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-3037-E | Hampton Downs | Network | HPTCB5 | 26/02/2025 | 09:08 | 26/02/2025 | 13:28 | 0.017932 | 6.9e-05 | 7 | 1820 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-182880-F | Claudelands | Network | CLACB3 | 26/02/2025 | 23:52 | 27/02/2025 | 00:01 | 0.0058846 | 0.0006109 | 62 | 597.27 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-3061-E | Horotiu | Network | HORCB5 | 05/03/2025 | 08:40 | 05/03/2025 | 11:35 | 0.0034484 | 1.97e-05 | 2 | 350 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-3118-E | Transpower Hamilton | Network | CLACB16 | 06/03/2025 | 10:02 | 06/03/2025 | 14:35 | 0.21752 | 0.0008178 | 83 | 22078 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-100-K | Wallace Rd | Network | WALCB6 | 11/03/2025 | 20:29 | 12/03/2025 | 00:45 | 0.01872 | 0.0001281 | 13 | 1900 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-3053-E | Whatawhata | Network | WHACB4 | 12/03/2025 | 09:05 | 12/03/2025 | 15:50 | 0.025971 | 6.9e-05 | 7 | 2636 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-141-K | Te Uku | Network | TEUCB11 | 12/03/2025 | 21:44 | 12/03/2025 | 22:53 | 0.051085 | 0.0012119 | 123 | 5185 | Unplanned interruptions on the network | Unknown | Fire Risk Mitigation Patrol - Sucessfully reclosed
|  | INCD-142-K | Weavers | Network | WEACB3 | 12/03/2025 | 22:35 | 13/03/2025 | 00:05 | 0.14168 | 0.0021873 | 222 | 14380 | Unplanned interruptions on the network | Vegetation | Tree growns in line
|  | INCD-181-K | Silverdale | Network | HOECB3 | 13/03/2025 | 23:59 | 14/03/2025 | 00:06 | 0.039406 | 0.0085815 | 871 | 3999.54 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-181-K | Silverdale | Network | HOECB6 | 13/03/2025 | 23:59 | 14/03/2025 | 00:06 | 0.032685 | 0.0058721 | 596 | 3317.43 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-3057-E | Gordonton | Network | GORCB13 | 14/03/2025 | 09:04 | 14/03/2025 | 10:48 | 0.0051233 | 4.93e-05 | 5 | 520 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-226-K | Weavers | Network | WEACB6 | 15/03/2025 | 22:08 | 16/03/2025 | 00:46 | 0.0077835 | 4.93e-05 | 5 | 790 | Unplanned interruptions on the network | Defective Equipment | Line break at twist joint
|  | INCD-231-K | Weavers | Network | WEACB3 | 16/03/2025 | 08:28 | 16/03/2025 | 09:59 | 0.0071726 | 7.88e-05 | 8 | 728 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-255-K | Whatawhata | Network | WHACB3 | 17/03/2025 | 09:58 | 17/03/2025 | 11:04 | 0.15047 | 0.0023646 | 240 | 15272 | Unplanned interruptions on the network | Unknown | Fire Risk Mitigation Patrol - Sucessfully reclosed
|  | INCD-281-K | Gordonton | Network | GORCB11 | 17/03/2025 | 19:01 | 18/03/2025 | 00:42 | 0.59377 | 0.0018129 | 184 | 60266 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-3076-E | Weavers | Network | WEACB4 | 18/03/2025 | 09:05 | 18/03/2025 | 12:36 | 0.022237 | 0.0001084 | 11 | 2257 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-412-K | Hoeka | Private | HOECB3 | 20/03/2025 | 16:58 | 20/03/2025 | 17:29 | 0.0018326 | 5.91e-05 | 6 | 186 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-494-K | Te Kauwhata | Network | TEKCB3 | 23/03/2025 | 14:11 | 23/03/2025 | 16:12 | 0.08414 | 0.0007882 | 80 | 8540 | Unplanned interruptions on the network | Defective Equipment | Faulty joint/connection
|  | INCD-585-K | Ngaruawahia | Network | NGACB2 | 26/03/2025 | 06:31 | 26/03/2025 | 15:13 | 0.27875 | 0.0008867 | 90 | 28292 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (IN Zone)
|  | INCD-3070-E | Gordonton | Network | GORCB12 | 26/03/2025 | 10:00 | 26/03/2025 | 16:24 | 0.19497 | 0.000532 | 54 | 19789 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2268-E | Gordonton | Network | GORCB11 | 02/04/2024 | 09:46 | 02/04/2024 | 14:29 | 0.040563 | 0.0001478 | 15 | 4117 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2267-E | Gordonton | Network | GORCB11 | 04/04/2024 | 10:08 | 04/04/2024 | 17:05 | 0.05209 | 0.0001478 | 15 | 5287 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-171264-F | Te Uku | Network | TEUCB13 | 09/04/2024 | 21:52 | 09/04/2024 | 23:59 | 0.086443 | 0.0007291 | 74 | 8773.73 | Unplanned interruptions on the network | Wildlife | Possum contacts line
|  | INCD-171452-F | Silverdale | Network | SILCB4 | 12/04/2024 | 22:28 | 12/04/2024 | 22:29 | 0.0010936 | 0.0008375 | 85 | 111 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-171409-F | Whatawhata | Network | WHACB3 | 13/04/2024 | 03:22 | 13/04/2024 | 18:24 | 0.73271 | 0.00334 | 339 | 74368 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-171622-F | Gordonton | Network | GORCB11 | 19/04/2024 | 15:56 | 19/04/2024 | 16:27 | 0.0003054 | 9.9e-06 | 1 | 31 | Unplanned interruptions on the network | Defective Equipment | Fuse blown on overload
|  | INCD-171836-F | Transpower Hamilton | Network | HAMCB2802 | 01/05/2024 | 08:31 | 01/05/2024 | 08:53 | 0.0002168 | 9.9e-06 | 1 | 22 | Unplanned interruptions on the network | Wildlife | Rodent on HV terminals
|  | INCD-2347-E | Glasgow | Network | GLACB2 | 03/05/2024 | 09:01 | 03/05/2024 | 12:50 | 0.036701 | 0.0001675 | 17 | 3725 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-171993-F | Weavers | Network | WEACB3 | 05/05/2024 | 05:39 | 05/05/2024 | 07:02 | 0.0024533 | 2.96e-05 | 3 | 249 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2361-E | Finlayson | Network | FINCB3 | 05/05/2024 | 10:20 | 05/05/2024 | 13:11 | 0.013744 | 9.85e-05 | 10 | 1395 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-172088-F | Transpower Hamilton | Network | HAMCB2802 | 08/05/2024 | 00:05 | 08/05/2024 | 00:08 | 0.0044632 | 0.0014877 | 151 | 453 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-172089-F | Transpower Hamilton | Network | HAMCB2902 | 08/05/2024 | 00:35 | 08/05/2024 | 00:48 | 0.071982 | 0.0055371 | 562 | 7306 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-17575-G | Transpower Hamilton | Network | HAMCB2742 | 08/05/2024 | 15:17 | 08/05/2024 | 16:21 | 0.048553 | 0.0007586 | 77 | 4928 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-172446-F | Te Kauwhata | Network | TEKCB5 | 15/05/2024 | 11:00 | 15/05/2024 | 16:11 | 0.0091924 | 2.96e-05 | 3 | 933 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-17588-G | Latham Court | Network | LATCB3 | 19/05/2024 | 09:42 | 19/05/2024 | 15:06 | 0.022346 | 6.9e-05 | 7 | 2268 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-172622-F | Ngaruawahia | Network | NGACB5 | 20/05/2024 | 19:38 | 20/05/2024 | 21:03 | 0.14661 | 0.0057834 | 587 | 14880.28 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-172630-F | Transpower Hamilton | Network | HAMCB2902 | 21/05/2024 | 07:03 | 21/05/2024 | 16:06 | 0.34861 | 0.0014188 | 144 | 35383 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2414-E | Hoeka | Network | HOECB1 | 22/05/2024 | 09:17 | 22/05/2024 | 14:17 | 0.017735 | 5.91e-05 | 6 | 1800 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2429-E | Chartwell | Network | CHACB9 | 25/05/2024 | 09:04 | 25/05/2024 | 14:20 | 0.093678 | 0.0003054 | 31 | 9508 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-172967-F | Wallace Rd | Network | WALCB2 | 28/05/2024 | 11:04 | 28/05/2024 | 11:26 | 0.19269 | 0.011685 | 1186 | 19557.3 | Unplanned interruptions on the network | Human error | Unintentionally Disabled
|  | INCD-2426-E | Te Kauwhata | Network | TEKCB3 | 29/05/2024 | 09:03 | 29/05/2024 | 11:04 | 0.027419 | 0.0002266 | 23 | 2783 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-173012-F | Horotiu | Network | NGACB2 | 29/05/2024 | 09:35 | 29/05/2024 | 15:57 | 0.1965 | 0.0020394 | 207 | 19944.29 | Unplanned interruptions on the network | Vegetation | Tree blown ovr on line (IN Zone)
|  | INCD-173079-F | Whatawhata | Network | RAGCB3 | 29/05/2024 | 14:19 | 29/05/2024 | 14:38 | 0.014133 | 0.0007192 | 73 | 1434.44 | Unplanned interruptions on the network | Adverse weather | Wind line clash
|  | INCD-173079-F | Whatawhata | Network | RAGCB5 | 29/05/2024 | 14:19 | 29/05/2024 | 14:38 | 0.029815 | 0.0015173 | 154 | 3026.09 | Unplanned interruptions on the network | Adverse weather | Wind line clash
|  | INCD-173102-F | Te Uku | Network | RAGCB2 | 29/05/2024 | 14:50 | 31/05/2024 | 17:05 | 0.046149 | 0.0071923 | 730 | 4684 | Unplanned interruptions on the network | Vegetation | Tree blown ovr on line (OUT of Zone)
|  | INCD-173414-F | Raglan | Network | RAGCB4 | 30/05/2024 | 16:34 | 30/05/2024 | 21:24 | 0.43716 | 0.0015074 | 153 | 44370 | Unplanned interruptions on the network | Defective Equipment | Cable termination fails
|  | INCD-173415-F | Raglan | Network | RAGCB4 | 30/05/2024 | 23:02 | 30/05/2024 | 23:54 | 0.075313 | 0.0014483 | 147 | 7644 | Unplanned interruptions on the network | Adverse weather | Line clash high wind
|  | INCD-173499-F | Te Uku | Network | RAGCB2 | 03/06/2024 | 05:28 | 03/06/2024 | 07:00 | 0.70921 | 0.0077047 | 782 | 71983 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-173499-F | Te Uku | Network | RAGCB5 | 03/06/2024 | 05:28 | 03/06/2024 | 07:00 | 0.14098 | 0.0015173 | 154 | 14309 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-173507-F | Tasman | Network | TASCB1 | 03/06/2024 | 11:08 | 03/06/2024 | 12:33 | 0.060632 | 0.0010247 | 104 | 6154 | Unplanned interruptions on the network | Defective Equipment | Flashovr on cable bush
|  | INCD-2457-E | Te Uku | Network | TEUCB11 | 05/06/2024 | 09:13 | 05/06/2024 | 11:25 | 0.0039016 | 2.96e-05 | 3 | 396 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-173649-F | Tasman | Network | TASCB1 | 05/06/2024 | 22:09 | 06/06/2024 | 03:59 | 0.077933 | 0.0002266 | 23 | 7910 | Unplanned interruptions on the network | Defective Equipment | Flashovr on cable bush
|  | INCD-173726-F | Sandwich Rd | Network | SANCB3 | 07/06/2024 | 08:45 | 07/06/2024 | 17:06 | 0.16284 | 0.0003251 | 33 | 16528 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-173729-F | Glasgow | Network | GLACB2 | 07/06/2024 | 09:31 | 07/06/2024 | 14:25 | 0.0028966 | 9.9e-06 | 1 | 294 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2468-E | Te Kauwhata | Network | TEKCB3 | 11/06/2024 | 09:08 | 11/06/2024 | 14:56 | 0.013715 | 3.94e-05 | 4 | 1392 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2448-E | Te Kauwhata | Network | TEKCB5 | 11/06/2024 | 09:23 | 11/06/2024 | 14:02 | 0.010995 | 3.94e-05 | 4 | 1116 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2452-E | Whatawhata | Network | WHACB4 | 12/06/2024 | 09:13 | 12/06/2024 | 14:38 | 0.0064041 | 1.97e-05 | 2 | 650 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-174146-F | Te Kauwhata | Network | TEKCB3 | 19/06/2024 | 09:05 | 19/06/2024 | 12:43 | 0.24884 | 0.0011724 | 119 | 25257 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-17610-G | Weavers | Network | WEACB4 | 20/06/2024 | 19:50 | 20/06/2024 | 21:01 | 0.0083943 | 0.0001182 | 12 | 852 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-2499-E | Te Kauwhata | Network | TEKCB5 | 21/06/2024 | 09:14 | 21/06/2024 | 10:18 | 0.0018917 | 2.96e-05 | 3 | 192 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2500-E | Chartwell | Network | CHACB9 | 22/06/2024 | 09:00 | 22/06/2024 | 12:53 | 0.018365 | 7.88e-05 | 8 | 1864 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2509-E | Horotiu | Network | HORCB5 | 24/06/2024 | 09:08 | 24/06/2024 | 14:25 | 0.018739 | 5.91e-05 | 6 | 1902 | Planned interruptions on the network | Planned | Transformer Upgrade
|  | INCD-2519-E | Whatawhata | Network | WHACB3 | 26/06/2024 | 09:02 | 26/06/2024 | 15:44 | 0.20922 | 0.0007488 | 76 | 21235 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-174513-F | Weavers | Network | WEACB3 | 30/06/2024 | 22:18 | 01/07/2024 | 00:14 | 0.32666 | 0.0012907 | 131 | 33155 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-2516-E | Avalon | Network | AVACB6 | 04/07/2024 | 09:04 | 04/07/2024 | 17:31 | 0.29971 | 0.0005912 | 60 | 30420 | Planned interruptions on the network | Planned | Distribution Transformer Replacement
|  | INCD-2531-E | Weavers | Network | WEACB2 | 04/07/2024 | 09:40 | 04/07/2024 | 14:31 | 0.0028671 | 9.9e-06 | 1 | 291 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-174847-F | Gordonton | Network | GORCB11 | 09/07/2024 | 01:36 | 09/07/2024 | 10:36 | 0.28737 | 0.001803 | 183 | 29167 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-174880-F | Gordonton | Network | GORCB11 | 09/07/2024 | 09:01 | 09/07/2024 | 14:54 | 0.12047 | 0.0003547 | 36 | 12227 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-174958-F | Weavers | Network | WEACB3 | 10/07/2024 | 15:08 | 10/07/2024 | 16:48 | 0.003941 | 3.94e-05 | 4 | 400 | Unplanned interruptions on the network | Defective Equipment | Loss or failure of oil
|  | INCD-17622-G | Finlayson Rd | Network | FINCB3 | 11/07/2024 | 12:12 | 11/07/2024 | 12:12 | 0.0012316 | 4.93e-05 | 5 | 125 | Unplanned interruptions on the network | Defective Equipment | Stay wire/ line clash
|  | INCD-17623-G | Avalon Dr | Network | AVACB6 | 11/07/2024 | 13:43 | 11/07/2024 | 13:53 | 0.01005 | 0.001005 | 102 | 1020 | Unplanned interruptions on the network | Defective Equipment | Overheated connections
|  | INCD-17624-G | Gordonton | Network | GORCB13 | 11/07/2024 | 17:46 | 11/07/2024 | 22:08 | 0.0025814 | 9.9e-06 | 1 | 262 | Unplanned interruptions on the network | Defective Equipment | Split crossarm
|  | INCD-175096-F | Wallace Rd | Network | WALCB2 | 14/07/2024 | 10:18 | 15/07/2024 | 12:02 | 1.4785 | 0.003606 | 366 | 150060 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-175230-F | Transpower Hamilton | Network | HAMCB2902 | 16/07/2024 | 21:06 | 16/07/2024 | 21:25 | 0.10883 | 0.0055667 | 565 | 11046 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-175252-F | Hoeka | Private | HOECB4 | 17/07/2024 | 09:09 | 17/07/2024 | 09:24 | 0.0007389 | 4.93e-05 | 5 | 75 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-175324-F | Latham | Network | LATCB3 | 18/07/2024 | 17:06 | 21/07/2024 | 17:20 | 0.95273 | 0.0042169 | 428 | 96699 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-175345-F | Whatawhata | Network | WHACB4 | 19/07/2024 | 09:04 | 19/07/2024 | 12:03 | 0.10177 | 0.0006109 | 62 | 10329 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2572-E | Te Uku | Network | TEUCB11 | 19/07/2024 | 09:45 | 19/07/2024 | 12:54 | 0.038464 | 0.0002168 | 22 | 3904 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-2542-E | Latham | Network | LATCB5 | 21/07/2024 | 09:03 | 21/07/2024 | 13:30 | 0.11278 | 0.0004237 | 43 | 11447 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-2589-E | Te Uku | Network | TEUCB11 | 23/07/2024 | 09:30 | 23/07/2024 | 10:22 | 0.012296 | 0.0002365 | 24 | 1248 | Unplanned interruptions on the network | Defective Equipment | Rotten crossarm
|  | INCD-175616-F | Transpower Hamilton | Network | HAMCB2762 | 29/07/2024 | 09:10 | 29/07/2024 | 10:48 | 0.060829 | 0.0006207 | 63 | 6174 | Planned interruptions on the network | Planned | Distribution Transformer Replacement
|  | INCD-17633-G | Avalon Dr | Network | AVACB6 | 30/07/2024 | 06:35 | 30/07/2024 | 07:52 | 0.098624 | 0.0012808 | 130 | 10010 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2595-E | MAF | Network | MAFCB3 | 31/07/2024 | 08:31 | 31/07/2024 | 16:09 | 0.012936 | 2.96e-05 | 3 | 1313 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2621-E | Wallace | Network | WALCB6 | 06/08/2024 | 10:05 | 06/08/2024 | 15:24 | 0.029558 | 9.85e-05 | 10 | 3000 | Planned interruptions on the network | Planned | New Connections
|  | INCD-175996-F | Peacockes | Network | PEACB12 | 07/08/2024 | 08:45 | 07/08/2024 | 14:38 | 0.01739 | 4.93e-05 | 5 | 1765 | Unplanned interruptions on the network | Defective Equipment | Mechanism seized
|  | INCD-176441-F | Te Uku | Network | TEUCB11 | 16/08/2024 | 03:05 | 17/08/2024 | 15:38 | 0.043321 | 0.0064534 | 655 | 4397 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-176497-F | Whatawhata | Network | RAGCB2 | 19/08/2024 | 02:55 | 19/08/2024 | 03:13 | 0.11446 | 0.007015 | 712 | 11617.38 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-176497-F | Whatawhata | Network | RAGCB4 | 19/08/2024 | 02:55 | 19/08/2024 | 03:13 | 0.1061 | 0.0065027 | 660 | 10768.92 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-176497-F | Whatawhata | Network | TEUCB13 | 19/08/2024 | 02:55 | 19/08/2024 | 03:13 | 0.0091958 | 0.0007389 | 75 | 933.35 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-176643-F | Gordonton | Network | GORCB13 | 20/08/2024 | 05:42 | 20/08/2024 | 07:25 | 0.0010148 | 9.9e-06 | 1 | 103 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-176832-F | Claudelands | Network | CLACB16 | 21/08/2024 | 21:53 | 23/08/2024 | 00:39 | 0.15506 | 0.001271 | 129 | 15738 | Unplanned interruptions on the network | Defective Equipment | Intnl insulation failure
|  | INCD-2712-E | Finlayson | Network | FINCB1 | 23/08/2024 | 09:10 | 23/08/2024 | 15:46 | 0.032464 | 8.87e-05 | 9 | 3295 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-176853-F | Hoeka | Network | HOECB4 | 23/08/2024 | 18:42 | 23/08/2024 | 21:50 | 0.029617 | 0.0001576 | 16 | 3006 | Unplanned interruptions on the network | Defective Equipment | Faulty joint/connection
|  | INCD-177084-F | Weavers | Network | WEACB3 | 29/08/2024 | 08:55 | 29/08/2024 | 12:06 | 0.0018818 | 9.9e-06 | 1 | 191 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-177090-F | Weavers | Network | WEACB3 | 29/08/2024 | 14:26 | 29/08/2024 | 14:38 | 0.0002365 | 1.97e-05 | 2 | 24 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-177100-F | Gordonton | Network | GORCB12 | 29/08/2024 | 21:23 | 30/08/2024 | 04:31 | 0.41777 | 0.0021478 | 218 | 42402 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-177136-F | Claudelands | Network | CLACB16 | 30/08/2024 | 09:03 | 30/08/2024 | 14:30 | 0.28828 | 0.001872 | 190 | 29260 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-177171-F | Foreman Rd | Network | FORCB5 | 31/08/2024 | 08:05 | 31/08/2024 | 10:06 | 0.0023843 | 1.97e-05 | 2 | 242 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-177188-F | Bryce St | Network | BRYCB3 | 31/08/2024 | 22:22 | 01/09/2024 | 01:52 | 0.0050445 | 2.96e-05 | 3 | 512 | Unplanned interruptions on the network | Defective Equipment | Cable termination fails
|  | INCD-177191-F | Te Uku | Network | TEUCB11 | 01/09/2024 | 00:21 | 01/09/2024 | 15:05 | 0.25092 | 0.0024927 | 253 | 25468 | Unplanned interruptions on the network | Lightning | Lightning breaks cond
|  | INCD-177217-F | Transpower Hamilton | Network | HAMCB2802 | 01/09/2024 | 11:54 | 01/09/2024 | 12:12 | 0.05144 | 0.0028769 | 292 | 5221 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-2715-E | Ngaruawahia | Network | NGACB2 | 03/09/2024 | 09:11 | 03/09/2024 | 15:02 | 0.024208 | 6.9e-05 | 7 | 2457 | Planned interruptions on the network | Planned | Distribution Transformer Replacement
|  | INCD-177310-F | Te Kauwhata | Network | TEKCB3 | 03/09/2024 | 10:36 | 03/09/2024 | 13:05 | 0.0088081 | 5.91e-05 | 6 | 894 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-177327-F | MAF | Private | MAFCB3 | 03/09/2024 | 18:32 | 03/09/2024 | 23:49 | 0.0080297 | 3.95e-05 | 4 | 815 | Unplanned interruptions on the network | Third_party | Discon of premise
|  | INCD-177451-F | Kent St | Network | KENCB3 | 05/09/2024 | 08:04 | 05/09/2024 | 10:35 | 0.0029558 | 1.97e-05 | 2 | 300 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2726-E | Weavers | Network | WEACB4 | 05/09/2024 | 09:26 | 05/09/2024 | 12:09 | 0.062632 | 0.0003842 | 39 | 6357 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-177399-F | Hoeka | Network | HOECB1 | 05/09/2024 | 10:05 | 05/09/2024 | 13:29 | 0.056278 | 0.0002759 | 28 | 5712 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-177583-F | Te Kauwhata | Network | TEKCB5 | 11/09/2024 | 08:11 | 11/09/2024 | 11:02 | 0.0067096 | 3.94e-05 | 4 | 681 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-177664-F | Raglan | Network | RAGCB6 | 13/09/2024 | 10:15 | 13/09/2024 | 12:49 | 0.10773 | 0.0006995 | 71 | 10934 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-177690-F | MAF | Network | MAFCB3 | 14/09/2024 | 09:03 | 14/09/2024 | 09:46 | 0.0016946 | 3.94e-05 | 4 | 172 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-177691-F | Hampton Downs | Network | HPTCB5 | 14/09/2024 | 08:23 | 14/09/2024 | 09:59 | 0.0085126 | 8.87e-05 | 9 | 864 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-177698-F | Weavers | Network | WEACB6 | 15/09/2024 | 03:30 | 15/09/2024 | 12:51 | 0.32684 | 0.0065913 | 669 | 33173.22 | Unplanned interruptions on the network | Defective Equipment | Line break at twist joint
|  | INCD-177763-F | Hampton Downs | Network | HPTCB2 | 17/09/2024 | 06:33 | 17/09/2024 | 07:04 | 0.0003054 | 9.9e-06 | 1 | 31 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2760-E | Te Uku | Network | TEUCB11 | 17/09/2024 | 09:16 | 17/09/2024 | 13:51 | 0.0081283 | 2.96e-05 | 3 | 825 | Planned interruptions on the network | Planned | Transformer Upgrade
|  | INCD-177805-F | Rural Bank | Network | RURCB1 | 17/09/2024 | 21:31 | 17/09/2024 | 21:36 | 0.0012808 | 0.0002562 | 26 | 130 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2750-E | Gordonton | Network | GORCB11 | 18/09/2024 | 09:06 | 18/09/2024 | 14:28 | 0.10532 | 0.0003645 | 37 | 10690 | Planned interruptions on the network | Planned | Distribution Transformer Replacement
|  | INCD-2759-E | Te Uku | Network | TEUCB11 | 19/09/2024 | 09:00 | 19/09/2024 | 16:21 | 0.16076 | 0.0003645 | 37 | 16317 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2755-E | Wallace | Network | WALCB3 | 19/09/2024 | 09:42 | 19/09/2024 | 18:09 | 0.2114 | 0.0004729 | 48 | 21456 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2749-E | Horotiu | Network | HORCB6 | 20/09/2024 | 09:02 | 20/09/2024 | 14:58 | 0.010523 | 2.96e-05 | 3 | 1068 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-178019-F | Weavers | Network | WEACB3 | 23/09/2024 | 07:19 | 23/09/2024 | 20:02 | 0.03007 | 3.94e-05 | 4 | 3052 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-178093-F | Gordonton | Network | GORCB12 | 25/09/2024 | 09:03 | 25/09/2024 | 16:26 | 0.25044 | 0.0005912 | 60 | 25419 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-178178-F | Weavers | Network | WEACB2 | 27/09/2024 | 09:18 | 27/09/2024 | 15:50 | 0.023833 | 6.9e-05 | 7 | 2419 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-178180-F | Peacockes Rd | Network | PEACB12 | 27/09/2024 | 09:43 | 27/09/2024 | 13:05 | 0.0079608 | 3.94e-05 | 4 | 808 | Unplanned interruptions on the network | Defective Equipment | Loose Connection
|  | INCD-178184-F | Horotiu | Network | HORCB4 | 27/09/2024 | 10:03 | 27/09/2024 | 12:47 | 0.070682 | 0.0004335 | 44 | 7174 | Unplanned interruptions on the network | Defective Equipment | Split crossarm
|  | INCD-178221-F | Peacockes | Network | PEACB12 | 28/09/2024 | 19:26 | 28/09/2024 | 20:54 | 0.10678 | 0.0012217 | 124 | 10838 | Unplanned interruptions on the network | Defective Equipment | Insulator split
|  | INCD-2811-E | Horotiu | Network | HORCB4 | 08/10/2024 | 09:09 | 08/10/2024 | 14:54 | 0.12063 | 0.0018818 | 191 | 12244 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2803-E | Transpower Hamilton | Network | HAMCB2762 | 10/10/2024 | 08:03 | 10/10/2024 | 15:34 | 0.29327 | 0.0006503 | 66 | 29766 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-178688-F | Hoeka | Network | HOECB4 | 13/10/2024 | 04:54 | 13/10/2024 | 12:47 | 0.17979 | 0.0010444 | 106 | 18248 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-178720-F | Te Uku | Network | TEUCB12 | 13/10/2024 | 16:22 | 13/10/2024 | 17:29 | 0.03807 | 0.0005714 | 58 | 3864 | Unplanned interruptions on the network | Vegetation | Tree blown ovr on line (OUT of Zone)
|  | INCD-178746-F | Finlayson Rd | Network | FINCB2 | 14/10/2024 | 12:00 | 14/10/2024 | 20:13 | 4.17e-05 | 9.9e-06 | 1 | 4.23 | Unplanned interruptions on the network | Defective Equipment | Contact problem
|  | INCD-178768-F | Glasgow St | Network | GLACB5 | 14/10/2024 | 18:46 | 15/10/2024 | 02:44 | 0.57609 | 0.0027587 | 280 | 58471 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-178788-F | Avalon | Network | AVACB8 | 15/10/2024 | 09:33 | 15/10/2024 | 15:22 | 0.2292 | 0.00067 | 68 | 23263 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-2840-E | Weavers | Network | WEACB5 | 22/10/2024 | 10:24 | 22/10/2024 | 15:58 | 0.1092 | 0.0003645 | 37 | 11083 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-179138-F | Sandwich Rd | Private | SANCB2 | 25/10/2024 | 10:37 | 25/10/2024 | 12:48 | 0.1252 | 0.0009557 | 97 | 12707 | Unplanned interruptions on the network | Third_party | Temp Disconnect / safety isolation
|  | INCD-179165-F | Weavers | Network | NGACB5 | 26/10/2024 | 23:59 | 27/10/2024 | 00:35 | 0.28356 | 0.0095865 | 973 | 28780 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-179250-F | Horotiu | Network | HORCB5 | 28/10/2024 | 06:00 | 28/10/2024 | 07:59 | 0.059411 | 0.0005025 | 51 | 6030 | Unplanned interruptions on the network | Defective Equipment | Jumpers come off
|  | INCD-2877-E | Hoeka | Network | HOECB3 | 29/10/2024 | 09:05 | 29/10/2024 | 13:56 | 0.44369 | 0.0016454 | 167 | 45033 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-179400-F | Wallace Rd | Network | WALCB6 | 02/11/2024 | 07:04 | 02/11/2024 | 08:50 | 0.0041775 | 3.94e-05 | 4 | 424 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (OUT of Zone)
|  | INCD-2897-E | Weavers | Network | WEACB6 | 07/11/2024 | 09:31 | 07/11/2024 | 15:16 | 0.29066 | 0.000867 | 88 | 29501 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-179766-F | Avalon Dr | Network | AVACB3 | 14/11/2024 | 09:24 | 14/11/2024 | 13:06 | 0.0035469 | 0.0003547 | 36 | 360 | Unplanned interruptions on the network | Third_party | Cable hit by digger
|  | INCD-2907-E | Hampton Downs | Network | HPTCB5 | 14/11/2024 | 09:55 | 14/11/2024 | 13:41 | 0.0022267 | 9.9e-06 | 1 | 226 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2913-E | Horotiu | Network | HORCB7 | 16/11/2024 | 08:10 | 16/11/2024 | 09:28 | 0.0007685 | 9.9e-06 | 1 | 78 | Planned interruptions on the network | Planned | 11kV Fuse Replacement
|  | INCD-17675-G | Te Uku | Network | TEUCB11 | 20/11/2024 | 08:32 | 20/11/2024 | 15:54 | 0.029725 | 6.9e-05 | 7 | 3017 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-179987-F | Te Uku | Network | TEUCB12 | 21/11/2024 | 09:03 | 21/11/2024 | 14:45 | 0.75135 | 0.0026799 | 272 | 76260 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-180008-F | Te Uku | Network | TEUCB12 | 21/11/2024 | 23:59 | 22/11/2024 | 00:09 | 0.023536 | 0.0026799 | 272 | 2388.87 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-180010-F | Raglan | Network | RAGCB6 | 22/11/2024 | 01:00 | 22/11/2024 | 01:32 | 0.048691 | 0.0098032 | 995 | 4942 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2888-E | Finlayson | Network | FINCB2 | 24/11/2024 | 08:30 | 24/11/2024 | 15:15 | 0.020523 | 0.0006207 | 63 | 2083 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2915-E | Transpower Hamilton | Network | HAMCB2802 | 27/11/2024 | 09:08 | 27/11/2024 | 12:00 | 0.086426 | 0.0005025 | 51 | 8772 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2919-E | Weavers | Network | WEACB3 | 27/11/2024 | 09:34 | 27/11/2024 | 12:58 | 0.14133 | 0.0007094 | 72 | 14345 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-2898-E | Weavers | Network | WEACB6 | 28/11/2024 | 09:31 | 28/11/2024 | 17:32 | 1.7143 | 0.0041183 | 418 | 173999 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-180340-F | Te Kauwhata | Network | TEKCB5 | 03/12/2024 | 05:58 | 03/12/2024 | 06:02 | 0.0005813 | 0.0001478 | 15 | 59 | Unplanned interruptions on the network | Defective Equipment | Line break at twist joint
|  | INCD-180554-F | Whatawhata | Private | WHACB5 | 10/12/2024 | 09:41 | 10/12/2024 | 09:47 | 0.0001182 | 1.97e-05 | 2 | 12 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-2865-E | Peacockes | Network | PEACB12 | 18/12/2024 | 08:34 | 18/12/2024 | 17:48 | 0.77577 | 0.0014483 | 147 | 78738 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-180882-F | Weavers | Network | WEACB6 | 21/12/2024 | 08:37 | 21/12/2024 | 12:51 | 0.02003 | 7.88e-05 | 8 | 2033 | Unplanned interruptions on the network | Vegetation | Tree blown ovr on line (OUT of Zone)
|  | INCD-17710-G | Weavers | Network | WEACB2 | 23/12/2024 | 12:15 | 23/12/2024 | 15:44 | 0.012355 | 5.91e-05 | 6 | 1254 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-180990-F | Peacockes | Network | PEACB16 | 26/12/2024 | 22:04 | 26/12/2024 | 23:53 | 0.042957 | 0.0003941 | 40 | 4360 | Unplanned interruptions on the network | Defective Equipment | Leaning pole
|  | INCD-181131-F | Hoeka | Network | HOECB6 | 04/01/2025 | 09:31 | 04/01/2025 | 10:47 | 0.0044927 | 5.91e-05 | 6 | 456 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (OUT of Zone)
|  | INCD-181255-F | Gordonton | Network | GORCB12 | 09/01/2025 | 09:01 | 09/01/2025 | 14:16 | 0.16772 | 0.000532 | 54 | 17023 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-17714-G | Te Kauwhata | Network | TEKCB3 | 09/01/2025 | 08:31 | 09/01/2025 | 09:52 | 0.0015961 | 1.97e-05 | 2 | 162 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-2967-E | Weavers | Network | WEACB6 | 10/01/2025 | 09:31 | 10/01/2025 | 13:38 | 0.041371 | 0.0001675 | 17 | 4199 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-181333-F | Finlayson Rd | Network | FINCB2 | 12/01/2025 | 13:48 | 12/01/2025 | 15:49 | 0.0011922 | 9.9e-06 | 1 | 121 | Unplanned interruptions on the network | Wildlife | Bird betw line & pole
|  | INCD-181434-F | Transpower Hamilton | Network | HAMCB2802 | 15/01/2025 | 00:02 | 15/01/2025 | 00:11 | 0.013478 | 0.0014976 | 152 | 1368 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-17721-G | Transpower Hamilton | Network | HAMCB2802 | 16/01/2025 | 00:02 | 16/01/2025 | 00:12 | 0.014976 | 0.0014976 | 152 | 1520 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-2754-E | Wallace | Network | WALCB6 | 16/01/2025 | 09:02 | 16/01/2025 | 14:20 | 0.15543 | 0.0005123 | 52 | 15776 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-181499-F | Te Uku | Network | TEUCB11 | 16/01/2025 | 12:57 | 16/01/2025 | 15:35 | 0.46361 | 0.0052908 | 537 | 47055 | Unplanned interruptions on the network | Unknown | Fire Risk Mitigation Patrol - Sucessfully reclosed
|  | INCD-2997-E | Sandwich | Network | SANCB7 | 16/01/2025 | 19:17 | 17/01/2025 | 01:12 | 0.07683 | 0.0002168 | 22 | 7798 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-181515-F | Te Uku | Network | TEUCB11 | 16/01/2025 | 21:23 | 17/01/2025 | 00:02 | 0.60617 | 0.0052908 | 537 | 61524 | Unplanned interruptions on the network | Defective Equipment | Insulator split
|  | INCD-17723-G | Weavers | Network | WEACB6 | 16/01/2025 | 22:21 | 17/01/2025 | 18:48 | 0.012089 | 9.9e-06 | 1 | 1227 | Unplanned interruptions on the network | Defective Equipment | Intnl insulation failure
|  | INCD-2992-E | Latham | Network | LATCB3 | 19/01/2025 | 09:29 | 19/01/2025 | 18:20 | 0.16543 | 0.0003448 | 35 | 16791 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-181587-F | Weavers | Network | WEACB3 | 19/01/2025 | 09:54 | 19/01/2025 | 15:15 | 0.22437 | 0.0006995 | 71 | 22773 | Unplanned interruptions on the network | Defective Equipment | Faulty joint/connection
|  | INCD-181681-F | Chartwell | Network | CHACB9 | 22/01/2025 | 02:09 | 22/01/2025 | 02:41 | 0.040267 | 0.001271 | 129 | 4087 | Unplanned interruptions on the network | Unknown | Fire Risk Mitigation Patrol - Sucessfully reclosed
|  | INCD-181706-F | Chartwell | Network | CHACB10 | 22/01/2025 | 16:24 | 22/01/2025 | 18:13 | 0.28778 | 0.010424 | 1058 | 29209 | Unplanned interruptions on the network | Defective Equipment | Installed Incorrectly
|  | INCD-181944-F | Peachgrove Rd | Network | PCHCB6 | 30/01/2025 | 08:14 | 30/01/2025 | 09:38 | 0.011823 | 0.0003941 | 40 | 1200 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-17730-G | Chartwell | Network | CHACB7 | 30/01/2025 | 11:03 | 30/01/2025 | 14:06 | 0.47542 | 0.0028572 | 290 | 48254 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-181274-F | Whatawhata | Network | WHACB2 | 04/02/2025 | 08:01 | 04/02/2025 | 10:47 | 0.003271 | 1.97e-05 | 2 | 332 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-182162-F | Ngaruawahia | Network | NGACB2 | 06/02/2025 | 06:02 | 06/02/2025 | 06:19 | 0.015074 | 0.0008867 | 90 | 1530 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-182281-F | Finlayson Rd | Network | FINCB1 | 11/02/2025 | 05:17 | 11/02/2025 | 10:06 | 0.0028474 | 9.9e-06 | 1 | 289 | Unplanned interruptions on the network | Wildlife | Bird causes flashover
|  | INCD-182436-F | Gordonton | Network | GORCB13 | 14/02/2025 | 09:20 | 14/02/2025 | 12:28 | 0.0055568 | 2.96e-05 | 3 | 564 | Unplanned interruptions on the network | Defective Equipment | Split crossarm
|  | INCD-17741-G | Raglan | Network | RAGCB2 | 17/02/2025 | 19:52 | 17/02/2025 | 20:14 | 0.021242 | 0.0009655 | 98 | 2156 | Unplanned interruptions on the network | Defective Equipment | Cable termination fails
|  | INCD-182555-F | Horotiu | Network | GORCB11 | 18/02/2025 | 07:35 | 18/02/2025 | 17:07 | 0.022759 | 0.0056652 | 575 | 2310 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-182635-F | Horotiu | Network | HORCB4 | 18/02/2025 | 22:29 | 18/02/2025 | 22:37 | 0.0079116 | 0.0010641 | 108 | 803 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-182695-F | Whatawhata | Private | WHACB4 | 20/02/2025 | 17:24 | 20/02/2025 | 17:53 | 0.0005714 | 1.97e-05 | 2 | 58 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-182880-F | Claudelands | Network | CLACB16 | 26/02/2025 | 23:52 | 27/02/2025 | 00:01 | 0.08267 | 0.0085815 | 871 | 8390.73 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-182935-F | Claudelands | Network | CLACB3 | 28/02/2025 | 00:30 | 28/02/2025 | 00:34 | 0.002433 | 0.0006109 | 62 | 246.94 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-182975-F | Galsgow | Network | GLACB1 | 01/03/2025 | 09:18 | 01/03/2025 | 10:54 | 0.030267 | 0.0025222 | 256 | 3072 | Unplanned interruptions on the network | Defective Equipment | Broken Neutral
|  | INCD-25-K | Whatawhata | Network | WHACB4 | 07/03/2025 | 10:54 | 10/03/2025 | 04:25 | 0.14815 | 0.0043055 | 437 | 15036.98 | Unplanned interruptions on the network | Unknown | Fire Risk Mitigation Patrol - Sucessfully reclosed
|  | INCD-24-K | Chartwell | Network | CHACB10 | 10/03/2025 | 00:11 | 10/03/2025 | 03:21 | 0.001872 | 9.9e-06 | 1 | 190 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-144-K | Hoeka | Network | HOECB1 | 12/03/2025 | 23:59 | 13/03/2025 | 00:11 | 0.071661 | 0.0062859 | 638 | 7273.34 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-3088-E | Ngaruawahia | Network | NGACB5 | 14/03/2025 | 08:54 | 14/03/2025 | 15:18 | 0.30975 | 0.0008079 | 82 | 31439 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-374-K | Transpower Hamilton | Network | HAMCB2722 | 20/03/2025 | 10:05 | 20/03/2025 | 15:09 | 0.59304 | 0.0019508 | 198 | 60192 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-417-K | Claudelands | Network | HAMCB2722 | 21/03/2025 | 00:04 | 21/03/2025 | 00:25 | 0.048829 | 0.0023252 | 236 | 4956 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-448-K | Te Kauwhata | Network | TEKCB5 | 21/03/2025 | 10:51 | 21/03/2025 | 12:31 | 0.0009853 | 9.9e-06 | 1 | 100 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-502-K | Horotiu | Network | HORCB4 | 24/03/2025 | 00:28 | 24/03/2025 | 01:07 | 0.0038425 | 9.85e-05 | 10 | 390 | Unplanned interruptions on the network | Defective Equipment | Connect/jumper loose
|  | INCD-3078-E | Claudeland | Network | CLACB13 | 27/03/2025 | 09:04 | 27/03/2025 | 12:28 | 0.22913 | 0.0011232 | 114 | 23256 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-651-K | Peacockes | Network | PEACB12 | 28/03/2025 | 03:38 | 28/03/2025 | 04:49 | 0.0034976 | 4.93e-05 | 5 | 355 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-3115-E | Pukete | Network | PUKCB10 | 29/03/2025 | 09:31 | 29/03/2025 | 10:50 | 0.0026503 | 0.0001971 | 20 | 269 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-171018-F | Whatawhata | Network | WHACB2 | 02/04/2024 | 17:19 | 02/04/2024 | 18:59 | 0.007882 | 7.88e-05 | 8 | 800 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-171029-F | Horotiu | Network | HORCB5 | 03/04/2024 | 06:11 | 03/04/2024 | 07:11 | 0.031922 | 0.000532 | 54 | 3240 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2277-E | Glasgow | Network | GLACB2 | 05/04/2024 | 10:05 | 05/04/2024 | 14:30 | 0.042169 | 0.0001675 | 17 | 4280 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2296-E | Silverdale | Network | SILCB1 | 10/04/2024 | 09:34 | 10/04/2024 | 14:42 | 0.18074 | 0.0005912 | 60 | 18345 | Planned interruptions on the network | Planned | Undergrounding
|  | INCD-171390-F | Te Kauwhata | Network | FINCB2 | 11/04/2024 | 14:46 | 12/04/2024 | 14:06 | 0.088967 | 0.0054386 | 552 | 9029.91 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-171423-F | Weavers | Network | WEACB2 | 13/04/2024 | 12:44 | 13/04/2024 | 15:34 | 0.045085 | 0.000266 | 27 | 4576 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2305-E | Glasgow | Network | GLACB2 | 17/04/2024 | 10:16 | 17/04/2024 | 13:10 | 0.0034287 | 1.97e-05 | 2 | 348 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2310-E | Hoeka | Network | HOECB1 | 18/04/2024 | 09:22 | 18/04/2024 | 15:07 | 0.016996 | 4.93e-05 | 5 | 1725 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-171673-F | MAF | Network | MAFCB6 | 23/04/2024 | 09:49 | 23/04/2024 | 11:21 | 0.0041307 | 6.9e-05 | 7 | 419.25 | Unplanned interruptions on the network | Defective Equipment | faulty line connection
|  | INCD-171682-F | Weavers | Network | WEACB5 | 23/04/2024 | 20:28 | 24/04/2024 | 01:03 | 0.024355 | 8.87e-05 | 9 | 2472 | Unplanned interruptions on the network | Defective Equipment | Fuse blown on overload
|  | INCD-171752-F | Transpower Hamilton | Network | HAMCB2902 | 29/04/2024 | 00:07 | 29/04/2024 | 00:12 | 0.027685 | 0.0055371 | 562 | 2810 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-171762-F | Transpower Hamilton | Network | HAMCB2902 | 29/04/2024 | 09:02 | 29/04/2024 | 16:30 | 0.30184 | 0.0012316 | 125 | 30636 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-171924-F | Horotiu | Network | HORCB5 | 02/05/2024 | 20:50 | 02/05/2024 | 22:35 | 0.0010345 | 9.9e-06 | 1 | 105 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2363-E | Peacockes | Network | PEACB18 | 03/05/2024 | 09:22 | 03/05/2024 | 15:26 | 0.010759 | 2.96e-05 | 3 | 1092 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-171981-F | Transpower Hamilton | Network | HAMCB2902 | 04/05/2024 | 16:10 | 04/05/2024 | 16:38 | 0.034484 | 0.0012316 | 125 | 3500 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-2360-E | Finlayson | Network | FINCB2 | 05/05/2024 | 10:00 | 05/05/2024 | 15:35 | 0.018217 | 0.0006207 | 63 | 1849 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-172128-F | Horotiu | Network | HORCB5 | 08/05/2024 | 11:32 | 08/05/2024 | 12:26 | 0.000532 | 9.9e-06 | 1 | 54 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-172165-F | Latham Court | Network | LATCB2 | 09/05/2024 | 05:10 | 09/05/2024 | 07:30 | 0.36645 | 0.013429 | 1363 | 37194 | Unplanned interruptions on the network | Defective Equipment | Faulty joint/connection
|  | INCD-2407-E | Weavers | Network | WEACB3 | 10/05/2024 | 09:09 | 10/05/2024 | 11:57 | 0.0033104 | 1.97e-05 | 2 | 336 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-172314-F | Horotiu | Network | HORCB6 | 13/05/2024 | 09:40 | 13/05/2024 | 11:41 | 0.051913 | 0.0013202 | 134 | 5269 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-172404-F | Horotiu | Network | HORCB4 | 15/05/2024 | 06:47 | 15/05/2024 | 08:22 | 0.0046799 | 4.93e-05 | 5 | 475 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-2384-E | Hoeka | Network | HOECB1 | 16/05/2024 | 09:15 | 16/05/2024 | 13:47 | 0.016079 | 5.91e-05 | 6 | 1632 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-172466-F | Borman Rd | Network | BORCB3 | 16/05/2024 | 09:45 | 16/05/2024 | 13:33 | 0.81332 | 0.01138 | 1155 | 82549.71 | Unplanned interruptions on the network | Defective Equipment | Flashovr on cable bush
|  | INCD-172582-F | Te Uku | Network | TEUCB11 | 20/05/2024 | 08:36 | 20/05/2024 | 10:31 | 0.0541 | 0.000601 | 61 | 5491 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-17591-G | Te Kauwhata | Network | TEKCB2 | 21/05/2024 | 19:41 | 21/05/2024 | 22:39 | 0.007015 | 3.94e-05 | 4 | 712 | Unplanned interruptions on the network | Wildlife | Possum across structure
|  | INCD-2440-E | Gordonton | Network | GORCB12 | 23/05/2024 | 09:12 | 23/05/2024 | 12:55 | 0.017577 | 7.88e-05 | 8 | 1784 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2445-E | Transpower Hamilton | Network | HAMCB2722 | 24/05/2024 | 09:04 | 24/05/2024 | 15:08 | 0.37656 | 0.0010345 | 105 | 38220 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-2413-E | Hoeka | Network | HOECB1 | 24/05/2024 | 09:05 | 24/05/2024 | 12:20 | 0.04611 | 0.0002365 | 24 | 4680 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-173032-F | Finlayson Rd | Network | FINCB1 | 29/05/2024 | 10:14 | 29/05/2024 | 19:41 | 0.2952 | 0.0005222 | 53 | 29962 | Unplanned interruptions on the network | Adverse weather | High wind lne break
|  | INCD-173060-F | Te Uku | Network | TEUCB11 | 29/05/2024 | 13:19 | 31/05/2024 | 12:59 | 0.53107 | 0.0004729 | 48 | 53902 | Unplanned interruptions on the network | Third_party | Tree felled into line (Third Party)
|  | INCD-173079-F | Whatawhata | Network | TEUCB11 | 29/05/2024 | 14:19 | 29/05/2024 | 14:38 | 0.13552 | 0.0068968 | 700 | 13754.93 | Unplanned interruptions on the network | Adverse weather | Wind line clash
|  | INCD-173079-F | Whatawhata | Network | TEUCB12 | 29/05/2024 | 14:19 | 29/05/2024 | 14:38 | 0.041431 | 0.0021084 | 214 | 4205.08 | Unplanned interruptions on the network | Adverse weather | Wind line clash
|  | INCD-173081-F | Whatawhata | Network | WHACB2 | 29/05/2024 | 14:24 | 31/05/2024 | 05:09 | 2.7321 | 0.0046208 | 469 | 277301 | Unplanned interruptions on the network | Vegetation | Tree blown ovr on line (OUT of Zone)
|  | INCD-173091-F | Transpower Hamilton | Network | BORCB6 | 29/05/2024 | 14:31 | 29/05/2024 | 19:03 | 1.3745 | 0.01405 | 1426 | 139510.33 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (IN Zone)
|  | INCD-173091-F | Transpower Hamilton | Network | BORCB7 | 29/05/2024 | 14:31 | 29/05/2024 | 19:03 | 1.6418 | 0.013301 | 1350 | 166634.94 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (IN Zone)
|  | INCD-173102-F | Te Uku | Network | TEUCB12 | 29/05/2024 | 14:50 | 31/05/2024 | 17:05 | 4.1761 | 0.0021084 | 214 | 423861.91 | Unplanned interruptions on the network | Vegetation | Tree blown ovr on line (OUT of Zone)
|  | INCD-173146-F | Weavers | Network | WEACB2 | 29/05/2024 | 15:49 | 29/05/2024 | 17:54 | 0.0086111 | 6.9e-05 | 7 | 874 | Unplanned interruptions on the network | Adverse weather | Line clash high wind
|  | INCD-17597-G | Gordonton | Network | GORCB11 | 29/05/2024 | 20:04 | 29/05/2024 | 20:23 | 0.0016848 | 8.87e-05 | 9 | 171 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-17601-G | Glasgow St | Network | GLACB2 | 30/05/2024 | 02:45 | 30/05/2024 | 02:54 | 0.0004434 | 4.93e-05 | 5 | 45 | Unplanned interruptions on the network | Adverse weather | Line clash high wind
|  | INCD-173263-F | Ngaruawahia | Network | NGACB6 | 30/05/2024 | 09:28 | 30/05/2024 | 10:54 | 0.0033893 | 3.94e-05 | 4 | 344 | Unplanned interruptions on the network | Adverse weather | Line clash high wind
|  | INCD-173329-F | Weavers | Network | WEACB6 | 30/05/2024 | 15:22 | 31/05/2024 | 14:43 | 0.013803 | 9.9e-06 | 1 | 1401 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-173417-F | Raglan | Network | RAGCB2 | 31/05/2024 | 00:06 | 31/05/2024 | 00:13 | 0.0035863 | 0.0005123 | 52 | 364 | Unplanned interruptions on the network | Adverse weather | Line clash high wind
|  | INCD-173416-F | Raglan | Network | RAGCB4 | 31/05/2024 | 00:45 | 31/05/2024 | 00:51 | 0.0060297 | 0.001005 | 102 | 612 | Unplanned interruptions on the network | Adverse weather | Line clash high wind
|  | INCD-173411-F | Gordonton | Network | GORCB13 | 31/05/2024 | 13:48 | 31/05/2024 | 15:06 | 0.057099 | 0.0007291 | 74 | 5795.38 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (OUT of Zone)
|  | INCD-173431-F | Te Uku | Network | TEUCB12 | 31/05/2024 | 14:15 | 31/05/2024 | 19:05 | 0.025715 | 0.0004335 | 44 | 2610 | Unplanned interruptions on the network | Defective Equipment | Corr on cable term flash
|  | INCD-173499-F | Te Uku | Network | RAGCB3 | 03/06/2024 | 05:28 | 03/06/2024 | 07:00 | 0.064731 | 0.0007192 | 73 | 6570 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-173647-F | Weavers | Network | WEACB6 | 05/06/2024 | 20:38 | 05/06/2024 | 20:54 | 0.0003153 | 1.97e-05 | 2 | 32 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-173761-F | Peacockes Rd | Network | PEACB12 | 08/06/2024 | 09:01 | 08/06/2024 | 12:12 | 0.016789 | 8.87e-05 | 9 | 1704 | Unplanned interruptions on the network | Defective Equipment | Faulty line spacer
|  | INCD-2451-E | Weavers | Network | WEACB5 | 09/06/2024 | 09:37 | 09/06/2024 | 16:50 | 0.31159 | 0.0007586 | 77 | 31625 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-173781-F | Gordonton | Network | GORCB11 | 10/06/2024 | 01:44 | 10/06/2024 | 05:03 | 0.40042 | 0.0072514 | 736 | 40641 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (OUT of Zone)
|  | INCD-173887-F | Te Kauwhata | Network | TEKCB5 | 12/06/2024 | 09:16 | 12/06/2024 | 11:04 | 0.0031922 | 2.96e-05 | 3 | 324 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-173933-F | Pukete | Network | PUKCB10 | 13/06/2024 | 09:00 | 13/06/2024 | 16:09 | 0.17881 | 0.0008473 | 86 | 18149 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-174026-F | Raglan | Network | RAGCB4 | 16/06/2024 | 05:59 | 16/06/2024 | 06:16 | 0.10941 | 0.0065125 | 661 | 11104.96 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-174093-F | Te Kauwhata | Network | TEKCB3 | 18/06/2024 | 08:29 | 18/06/2024 | 08:59 | 0.0005912 | 1.97e-05 | 2 | 60 | Unplanned interruptions on the network | Wildlife | Bird betw line & pole
|  | INCD-174137-F | Transpower Hamilton | Network | HAMCB2902 | 19/06/2024 | 08:14 | 19/06/2024 | 08:39 | 0.012808 | 0.0005123 | 52 | 1300 | Planned interruptions on the network | Planned | New Connections
|  | INCD-174286-F | Te Kauwhata | Network | TEKCB5 | 23/06/2024 | 08:49 | 23/06/2024 | 14:55 | 0.003606 | 9.9e-06 | 1 | 366 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-174539-F | Weavers | Network | WEACB2 | 01/07/2024 | 12:58 | 01/07/2024 | 14:34 | 0.23117 | 0.004542 | 461 | 23463 | Unplanned interruptions on the network | Third_party | Cable hit by digger
|  | INCD-174581-F | Latham | Network | LATCB2 | 02/07/2024 | 02:47 | 02/07/2024 | 14:13 | 1.0497 | 0.002207 | 224 | 106544 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-174644-F | Finlayson Rd | Network | FINCB2 | 03/07/2024 | 10:59 | 03/07/2024 | 12:15 | 0.0007488 | 9.9e-06 | 1 | 76 | Unplanned interruptions on the network | Wildlife | Bird betw line & pole
|  | INCD-2478-E | Pukete | Network | PUKCB10 | 04/07/2024 | 09:07 | 04/07/2024 | 12:24 | 0.025232 | 0.0001281 | 13 | 2561 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-174755-F | Gordonton | Network | GORCB13 | 06/07/2024 | 12:56 | 06/07/2024 | 14:02 | 0.046425 | 0.0025025 | 254 | 4712 | Unplanned interruptions on the network | Wildlife | Bird nest cause flashovr
|  | INCD-2533-E | Glasgow | Network | GLACB2 | 08/07/2024 | 09:40 | 08/07/2024 | 12:26 | 0.013084 | 7.88e-05 | 8 | 1328 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-174882-F | Gordonton | Network | GORCB11 | 09/07/2024 | 09:01 | 09/07/2024 | 09:06 | 0.0012316 | 0.0002463 | 25 | 125 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2559-E | Weavers | Network | WEACB3 | 12/07/2024 | 09:16 | 12/07/2024 | 11:23 | 0.027735 | 0.0002365 | 24 | 2815 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-175074-F | Pukete | Network | PUKCB10 | 13/07/2024 | 12:50 | 13/07/2024 | 14:27 | 0.24179 | 0.0037045 | 376 | 24541 | Unplanned interruptions on the network | Defective Equipment | Cable termination fails
|  | INCD-2560-E | Finlayson | Network | FINCB3 | 14/07/2024 | 09:00 | 14/07/2024 | 11:00 | 0.021616 | 0.0001872 | 19 | 2194 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2552-E | Glasgow | Network | GLACB6 | 17/07/2024 | 10:15 | 17/07/2024 | 12:29 | 0.014523 | 0.0001084 | 11 | 1474 | Planned interruptions on the network | Planned | 11kV Fuse Replacement
|  | INCD-175299-F | Gordonton | Network | GORCB13 | 18/07/2024 | 09:03 | 18/07/2024 | 15:11 | 0.21043 | 0.000601 | 61 | 21358 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-175325-F | Weavers | Network | WEACB4 | 18/07/2024 | 16:55 | 18/07/2024 | 17:52 | 0.0067391 | 0.0001182 | 12 | 684 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-2586-E | Finlayson | Network | FINCB3 | 19/07/2024 | 13:04 | 19/07/2024 | 13:56 | 0.02203 | 0.0004237 | 43 | 2236 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-175375-F | Glasgow St | Network | GLACB6 | 19/07/2024 | 22:02 | 20/07/2024 | 00:11 | 0.22969 | 0.001803 | 183 | 23313 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-2571-E | Chartwell | Network | CHACB12 | 29/07/2024 | 08:44 | 29/07/2024 | 13:05 | 0.090003 | 0.0003448 | 35 | 9135 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-2658-E | Te Uku | Network | TEUCB11 | 01/08/2024 | 09:24 | 01/08/2024 | 12:05 | 0.03807 | 0.0002365 | 24 | 3864 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2622-E | Glasgow | Network | GLACB2 | 01/08/2024 | 09:27 | 01/08/2024 | 13:59 | 0.013399 | 4.93e-05 | 5 | 1360 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-175864-F | Peacockes Rd | Network | PEACB12 | 01/08/2024 | 19:35 | 02/08/2024 | 04:56 | 0.21553 | 0.0003842 | 39 | 21876 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-175760-F | Weavers | Network | WEACB6 | 02/08/2024 | 09:24 | 02/08/2024 | 14:49 | 0.0064041 | 1.97e-05 | 2 | 650 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2638-E | Weavers | Network | WEACB3 | 07/08/2024 | 09:37 | 07/08/2024 | 15:12 | 0.093057 | 0.0007586 | 77 | 9445 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-176020-F | Glasgow | Network | GLACB2 | 07/08/2024 | 19:42 | 07/08/2024 | 22:15 | 0.066327 | 0.0004335 | 44 | 6732 | Unplanned interruptions on the network | Defective Equipment | Twist crossarm
|  | INCD-176022-F | Hampton Downs | Network | HPTCB5 | 07/08/2024 | 19:22 | 07/08/2024 | 21:41 | 0.012325 | 8.87e-05 | 9 | 1251 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-176044-F | Finlayson | Network | FINCB2 | 08/08/2024 | 08:51 | 08/08/2024 | 12:11 | 0.0059115 | 2.96e-05 | 3 | 600 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-176066-F | Finlayson Rd | Network | FINCB2 | 08/08/2024 | 15:26 | 08/08/2024 | 18:27 | 0.0017833 | 9.9e-06 | 1 | 181 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-2654-E | Weavers | Network | WEACB3 | 13/08/2024 | 09:08 | 13/08/2024 | 12:07 | 0.0035272 | 1.97e-05 | 2 | 358 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2670-E | Glasgow | Network | GLACB2 | 14/08/2024 | 09:00 | 14/08/2024 | 10:32 | 0.011695 | 0.0001281 | 13 | 1187 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2599-E | Wallace | Network | WALCB4 | 14/08/2024 | 09:04 | 14/08/2024 | 14:56 | 0.079766 | 0.0002266 | 23 | 8096 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2679-E | Glasgow | Network | GLACB2 | 14/08/2024 | 12:30 | 14/08/2024 | 15:54 | 0.01005 | 4.93e-05 | 5 | 1020 | Planned interruptions on the network | Planned | Distribution Transformer Replacement
|  | INCD-2672-E | Glasgow | Network | GLACB2 | 14/08/2024 | 14:08 | 14/08/2024 | 14:43 | 0.0037932 | 0.0001084 | 11 | 385 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-176384-F | Te Kauwhata | Network | TEKCB3 | 16/08/2024 | 03:36 | 16/08/2024 | 04:17 | 0.0008079 | 1.97e-05 | 2 | 82 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-176401-F | Weavers | Network | WEACB3 | 16/08/2024 | 10:43 | 16/08/2024 | 10:54 | 0.0001084 | 9.9e-06 | 1 | 11 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-176495-F | Te Kauwhata | Network | TEKCB5 | 19/08/2024 | 00:22 | 19/08/2024 | 01:03 | 0.000404 | 9.9e-06 | 1 | 41 | Unplanned interruptions on the network | Defective Equipment | LV Panel fire
|  | INCD-176533-F | Whatawhata | Network | RAGCB2 | 19/08/2024 | 06:57 | 19/08/2024 | 16:19 | 3.5873 | 0.0077047 | 782 | 364103 | Unplanned interruptions on the network | Defective Equipment | Cable termination fails
|  | INCD-176533-F | Whatawhata | Network | RAGCB6 | 19/08/2024 | 06:57 | 19/08/2024 | 16:19 | 4.5478 | 0.0097343 | 988 | 461583 | Unplanned interruptions on the network | Defective Equipment | Cable termination fails
|  | INCD-176574-F | Glasgow St | Network | GLACB1 | 19/08/2024 | 11:47 | 19/08/2024 | 15:08 | 1.0836 | 0.0093205 | 946 | 109982 | Unplanned interruptions on the network | Defective Equipment | Broken binder
|  | INCD-176624-F | Gordonton | Network | GORCB12 | 19/08/2024 | 18:52 | 19/08/2024 | 19:09 | 0.077411 | 0.0047391 | 481 | 7857 | Unplanned interruptions on the network | Defective Equipment | Loose connection
|  | INCD-176731-F | Whatawhata | Network | WHACB5 | 21/08/2024 | 09:19 | 21/08/2024 | 14:23 | 0.10364 | 0.0003645 | 37 | 10519 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-176845-F | Weavers | Network | WEACB2 | 23/08/2024 | 09:54 | 23/08/2024 | 14:59 | 0.003005 | 9.9e-06 | 1 | 305 | Unplanned interruptions on the network | Wildlife | Bird betw line & pole
|  | INCD-2708-E | Te Uku | Network | TEUCB11 | 27/08/2024 | 09:39 | 27/08/2024 | 13:31 | 0.026562 | 0.0001281 | 13 | 2696 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-177077-F | Weavers | Network | WEACB3 | 29/08/2024 | 09:49 | 29/08/2024 | 10:01 | 0.0011823 | 9.85e-05 | 10 | 120 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-177104-F | Gordonton | Network | GORCB12 | 29/08/2024 | 22:14 | 29/08/2024 | 22:32 | 0.0027488 | 0.0001478 | 15 | 279 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-177185-F | Hoeka | Network | HOECB4 | 31/08/2024 | 21:12 | 31/08/2024 | 22:17 | 0.0019212 | 2.96e-05 | 3 | 195 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-2680-E | Weavers | Network | WEACB3 | 03/09/2024 | 09:48 | 03/09/2024 | 11:47 | 0.016414 | 0.0001379 | 14 | 1666 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-177490-F | Whatawhata | Network | WHACB5 | 07/09/2024 | 23:56 | 08/09/2024 | 04:27 | 0.30472 | 0.0065716 | 667 | 30928 | Unplanned interruptions on the network | Defective Equipment | Broken binder
|  | INCD-177542-F | Tasman | Network | TASCB2 | 09/09/2024 | 20:05 | 09/09/2024 | 20:10 | 4.93e-05 | 9.9e-06 | 1 | 5 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2753-E | Finlayson | Network | FINCB3 | 15/09/2024 | 09:10 | 15/09/2024 | 12:58 | 0.022464 | 9.85e-05 | 10 | 2280 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2757-E | Gordonton | Network | GORCB11 | 16/09/2024 | 09:07 | 16/09/2024 | 13:06 | 0.24725 | 0.0010345 | 105 | 25095 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-177729-F | Ngaruawahia | Network | NGACB2 | 16/09/2024 | 09:35 | 16/09/2024 | 09:59 | 0.0009458 | 3.94e-05 | 4 | 96 | Unplanned interruptions on the network | Human error | Cable isolated- saftey reasons
|  | INCD-177746-F | Te Kauwhata | Network | TEKCB5 | 16/09/2024 | 10:17 | 16/09/2024 | 13:18 | 0.0071332 | 3.94e-05 | 4 | 724 | Unplanned interruptions on the network | Adverse weather | Line clash high wind
|  | INCD-177788-F | Ngaruawahia | Network | NGACB2 | 17/09/2024 | 13:57 | 17/09/2024 | 14:36 | 0.001537 | 3.94e-05 | 4 | 156 | Unplanned interruptions on the network | Human error | Cable isolated- saftey reasons
|  | INCD-177800-F | Gordonton | Network | GORCB11 | 17/09/2024 | 16:52 | 17/09/2024 | 17:54 | 0.0018326 | 2.96e-05 | 3 | 186 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-2748-E | Weavers | Network | WEACB2 | 18/09/2024 | 09:06 | 18/09/2024 | 14:34 | 0.066741 | 0.0002069 | 21 | 6774 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2755-E | Wallace | Network | WALCB2 | 19/09/2024 | 09:42 | 19/09/2024 | 18:09 | 0.18559 | 0.0003842 | 39 | 18837 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2744-E | Tasman | Network | TASCB3 | 19/09/2024 | 18:43 | 20/09/2024 | 00:46 | 0.0035765 | 9.9e-06 | 1 | 363 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2756-E | Weavers | Network | WEACB4 | 23/09/2024 | 09:13 | 23/09/2024 | 13:24 | 0.039568 | 0.0001576 | 16 | 4016 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-178042-F | Glasgow St | Network | GORCB11 | 24/09/2024 | 02:20 | 24/09/2024 | 03:49 | 0.14088 | 0.0015764 | 160 | 14299 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-178257-F | Raglan | Network | RAGCB6 | 30/09/2024 | 09:38 | 30/09/2024 | 13:45 | 0.12857 | 0.0005222 | 53 | 13049 | Unplanned interruptions on the network | Defective Equipment | Connect/jumper loose
|  | INCD-2778-E | Horotiu | Network | HORCB6 | 01/10/2024 | 09:34 | 01/10/2024 | 14:35 | 0.20691 | 0.0007094 | 72 | 21001 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-178337-F | Hoeka | Network | HOECB3 | 02/10/2024 | 09:00 | 02/10/2024 | 15:21 | 0.46009 | 0.0013202 | 134 | 46698 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-178434-F | Finlayson | Network | FINCB2 | 04/10/2024 | 15:49 | 04/10/2024 | 17:45 | 0.0057145 | 4.93e-05 | 5 | 580 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2809-E | Weavers | Network | WEACB6 | 07/10/2024 | 10:20 | 07/10/2024 | 12:18 | 0.0046504 | 3.94e-05 | 4 | 472 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2812-E | Whatawhata | Network | WHACB5 | 10/10/2024 | 22:44 | 11/10/2024 | 01:30 | 0.081776 | 0.0004926 | 50 | 8300 | Planned interruptions on the network | Planned | Distribution Transformer Replacement
|  | INCD-178642-F | Transpower Hamilton | Network | HAMCB2802 | 11/10/2024 | 06:34 | 11/10/2024 | 07:34 | 0.0017735 | 2.96e-05 | 3 | 180 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-178721-F | Te Uku | Network | TEUCB12 | 13/10/2024 | 16:22 | 13/10/2024 | 20:01 | 0.14194 | 0.0006503 | 66 | 14406 | Unplanned interruptions on the network | Vegetation | Tree blown ovr on line (OUT of Zone)
|  | INCD-17666-G | Whatawhata | Network | WHACB5 | 16/10/2024 | 04:47 | 16/10/2024 | 06:29 | 0.0020099 | 1.97e-05 | 2 | 204 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-178850-F | Horotiu | Network | HORCB5 | 16/10/2024 | 15:47 | 16/10/2024 | 18:55 | 0.0018523 | 9.9e-06 | 1 | 188 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-17654-G | Weavers | Network | WEACB3 | 17/10/2024 | 07:03 | 17/10/2024 | 16:48 | 0.20542 | 0.0006601 | 67 | 20850 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-179040-F | Bryce | Network | BRYCB12 | 22/10/2024 | 13:32 | 22/10/2024 | 14:00 | 0.027587 | 0.0009853 | 100 | 2800 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-179061-F | Hoeka | Network | HOECB1 | 23/10/2024 | 08:15 | 23/10/2024 | 10:24 | 0.0025419 | 1.97e-05 | 2 | 258 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2831-E | Avalon | Network | AVACB6 | 24/10/2024 | 09:05 | 24/10/2024 | 11:40 | 0.070248 | 0.0004532 | 46 | 7130 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-179130-F | Sandwich Rd | Network | SANCB2 | 25/10/2024 | 09:00 | 25/10/2024 | 09:13 | 0.012424 | 0.0009557 | 97 | 1261 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-179165-F | Weavers | Network | NGACB2 | 26/10/2024 | 23:59 | 27/10/2024 | 00:35 | 0.20767 | 0.0061677 | 626 | 21078 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-179245-F | Horotiu | Network | HORCB5 | 28/10/2024 | 06:00 | 28/10/2024 | 07:01 | 0.090801 | 0.0015074 | 153 | 9216 | Unplanned interruptions on the network | Defective Equipment | Jumpers come off
|  | INCD-179219-F | Whatawhata | Private | WHACB3 | 29/10/2024 | 04:20 | 29/10/2024 | 04:42 | 0.0010838 | 4.93e-05 | 5 | 110 | Unplanned interruptions on the network | Third_party | High Load Request
|  | INCD-179307-F | Chartwell | Network | CHACB9 | 30/10/2024 | 11:47 | 30/10/2024 | 13:45 | 0.0093008 | 7.88e-05 | 8 | 944 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-2880-E | Borman | Network | BORCB2 | 05/11/2024 | 09:31 | 05/11/2024 | 15:27 | 0.052583 | 0.0001478 | 15 | 5337 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-179541-F | Transpower Hamilton | Private | HAMCB2802 | 06/11/2024 | 17:08 | 06/11/2024 | 17:26 | 0.0007094 | 3.94e-05 | 4 | 72 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-2908-E | Raglan | Network | RAGCB6 | 09/11/2024 | 01:01 | 09/11/2024 | 01:26 | 0.10715 | 0.0042858 | 435 | 10875 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-179671-F | Transpower Hamilton | Network | HAMCB2802 | 11/11/2024 | 16:13 | 11/11/2024 | 21:04 | 0.0028671 | 9.9e-06 | 1 | 291 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-179694-F | Finlayson Rd | Network | FINCB1 | 12/11/2024 | 11:01 | 12/11/2024 | 13:35 | 0.0015173 | 9.9e-06 | 1 | 154 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-179761-F | Avalon Dr | Network | AVACB3 | 14/11/2024 | 08:59 | 14/11/2024 | 14:05 | 0.40154 | 0.0016257 | 165 | 40755 | Unplanned interruptions on the network | Third_party | Cable hit by digger
|  | INCD-179787-F | Te Kauwhata | Network | TEKCB2 | 14/11/2024 | 13:30 | 14/11/2024 | 19:49 | 0.049519 | 0.0005616 | 57 | 5026 | Unplanned interruptions on the network | Defective Equipment | Faulty joint/connection
|  | INCD-180008-F | Te Uku | Network | TEUCB11 | 21/11/2024 | 23:59 | 22/11/2024 | 00:09 | 0.071982 | 0.0074978 | 761 | 7306 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2914-E | Weavers | Network | WEACB3 | 22/11/2024 | 09:30 | 22/11/2024 | 12:43 | 0.0079116 | 4.93e-05 | 5 | 803 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-180024-F | Finlayson Rd | Network | FINCB1 | 22/11/2024 | 08:10 | 22/11/2024 | 10:02 | 0.0033104 | 2.96e-05 | 3 | 336 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2851-E | Te Uku | Network | TEUCB11 | 27/11/2024 | 08:37 | 27/11/2024 | 15:54 | 0.15111 | 0.0003744 | 38 | 15337 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-180176-F | Hoeka | Private | HOECB3 | 27/11/2024 | 18:58 | 27/11/2024 | 19:43 | 0.0026602 | 5.91e-05 | 6 | 270 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-2934-E | Wallace | Network | WALCB6 | 03/12/2024 | 12:28 | 03/12/2024 | 14:54 | 0.0057539 | 3.94e-05 | 4 | 584 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-180408-F | Ngaruawahia | Network | NGACB2 | 05/12/2024 | 01:38 | 05/12/2024 | 02:27 | 0.0062662 | 0.0001281 | 13 | 636 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-180411-F | Weavers | Network | WEACB3 | 05/12/2024 | 05:47 | 05/12/2024 | 07:24 | 0.013242 | 0.0001379 | 14 | 1344 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-2947-E | Wallace | Network | WALCB2 | 05/12/2024 | 08:30 | 05/12/2024 | 15:29 | 0.75625 | 0.0041085 | 417 | 76757 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2938-E | Peacockes | Network | PEACB18 | 06/12/2024 | 08:33 | 06/12/2024 | 13:35 | 0.026621 | 8.87e-05 | 9 | 2702 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2937-E | Chartwell | Network | CHACB9 | 06/12/2024 | 10:03 | 06/12/2024 | 11:39 | 0.048238 | 0.0005025 | 51 | 4896 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2942-E | Whatawhata | Network | WHACB4 | 11/12/2024 | 09:05 | 11/12/2024 | 12:52 | 0.011183 | 4.93e-05 | 5 | 1135 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2941-E | Horotiu | Network | HORCB4 | 11/12/2024 | 09:19 | 11/12/2024 | 09:33 | 0.013695 | 0.0009557 | 97 | 1390 | Planned interruptions on the network | Planned | New Connections
|  | INCD-2950-E | Finlayson | Network | FINCB2 | 11/12/2024 | 09:35 | 11/12/2024 | 13:16 | 0.12269 | 0.0005616 | 57 | 12453 | Planned interruptions on the network | Planned | 11kV Fuse Replacement
|  | INCD-2970-E | Chartwell | Network | CHACB9 | 13/12/2024 | 09:17 | 13/12/2024 | 17:44 | 0.0099904 | 1.97e-05 | 2 | 1014 | Planned interruptions on the network | Planned | Distribution Transformer Replacement
|  | INCD-2959-E | Te Uku | Network | TEUCB12 | 13/12/2024 | 10:15 | 13/12/2024 | 14:02 | 0.0067096 | 2.96e-05 | 3 | 681 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2969-E | Finlayson | Network | FINCB2 | 17/12/2024 | 09:46 | 17/12/2024 | 13:33 | 0.0067096 | 2.96e-05 | 3 | 681 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-180759-F | Wallace Rd | Network | WALCB1 | 17/12/2024 | 12:52 | 17/12/2024 | 14:27 | 0.034632 | 0.0003645 | 37 | 3515 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-17709-G | Weavers | Network | WEACB2 | 23/12/2024 | 08:46 | 23/12/2024 | 11:40 | 0.0017143 | 9.9e-06 | 1 | 174 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-181095-F | Weavers | Network | FINCB1 | 02/01/2025 | 03:59 | 02/01/2025 | 04:00 | 0.0045075 | 0.0040986 | 416 | 457.5 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-181186-F | Weavers | Private | WEACB4 | 07/01/2025 | 06:23 | 07/01/2025 | 06:40 | 0.0018424 | 0.0001084 | 11 | 187 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2979-E | Latham | Network | LATCB1 | 09/01/2025 | 20:06 | 10/01/2025 | 03:54 | 0.018444 | 3.94e-05 | 4 | 1872 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-181382-F | Horotiu | Network | HORCB6 | 13/01/2025 | 16:58 | 13/01/2025 | 19:20 | 0.025183 | 0.0001773 | 18 | 2556 | Unplanned interruptions on the network | Vegetation | Tree falls and hits Tx
|  | INCD-181389-F | Weavers | Network | WEACB3 | 14/01/2025 | 03:24 | 14/01/2025 | 05:24 | 0.15148 | 0.0021873 | 222 | 15375.18 | Unplanned interruptions on the network | Wildlife | Possum contacts line
|  | INCD-181439-F | Horotiu | Network | HORCB4 | 15/01/2025 | 08:40 | 15/01/2025 | 11:28 | 0.16056 | 0.0009557 | 97 | 16296 | Unplanned interruptions on the network | Vegetation | Tree known grows in line
|  | INCD-181464-F | Wallace Rd | Network | WALCB6 | 15/01/2025 | 14:47 | 15/01/2025 | 15:02 | 0.0008867 | 5.91e-05 | 6 | 90 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-3008-E | Peacockes | Network | PEACB12 | 17/01/2025 | 08:36 | 17/01/2025 | 13:22 | 0.027961 | 9.85e-05 | 10 | 2838 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2986-E | Wallace | Network | WALCB5 | 17/01/2025 | 09:03 | 17/01/2025 | 14:36 | 0.60925 | 0.0020395 | 207 | 61837 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-181570-F | Finlayson Rd | Network | FINCB2 | 18/01/2025 | 10:49 | 18/01/2025 | 11:18 | 0.0002857 | 9.9e-06 | 1 | 29 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-181573-F | Finlayson Rd | Network | FINCB1 | 18/01/2025 | 11:02 | 18/01/2025 | 13:30 | 0.0062563 | 5.91e-05 | 6 | 635 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-181577-F | Peacockes | Network | PEACB12 | 18/01/2025 | 16:08 | 18/01/2025 | 17:46 | 0.0048277 | 4.93e-05 | 5 | 490 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-182177-F | Chartwell | Network | CHACB13 | 23/01/2025 | 09:02 | 23/01/2025 | 09:29 | 0.0031922 | 0.0001182 | 12 | 324 | Planned interruptions on the network | Planned | Distribution Transformer Replacement
|  | INCD-2976-E | Peacockes | Network | PEACB16 | 23/01/2025 | 09:09 | 23/01/2025 | 16:11 | 0.1533 | 0.0003941 | 40 | 15560 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-3012-E | Weavers | Network | WEACB6 | 24/01/2025 | 09:38 | 24/01/2025 | 12:25 | 0.016454 | 9.85e-05 | 10 | 1670 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-182181-F | Latham Court | Network | LATCB1 | 30/01/2025 | 20:41 | 01/02/2025 | 11:02 | 0.28333 | 0.0023646 | 240 | 28757 | Unplanned interruptions on the network | Defective Equipment | Cable termination fails
|  | INCD-3014-E | Weavers | Network | WEACB2 | 31/01/2025 | 09:02 | 31/01/2025 | 13:48 | 0.078899 | 0.0002759 | 28 | 8008 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-182034-F | Wallace Rd | Network | WALCB6 | 01/02/2025 | 10:38 | 01/02/2025 | 15:18 | 0.02207 | 7.88e-05 | 8 | 2240 | Unplanned interruptions on the network | Defective Equipment | Faulty joint/connection
|  | INCD-17735-G | Weavers | Network | WEACB6 | 07/02/2025 | 07:27 | 07/02/2025 | 09:31 | 0.0036651 | 2.96e-05 | 3 | 372 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-182299-F | Gordonton | Network | GORCB11 | 11/02/2025 | 12:01 | 11/02/2025 | 14:38 | 0.0030937 | 1.97e-05 | 2 | 314 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-182314-F | Te Uku | Network | TEUCB11 | 11/02/2025 | 08:18 | 11/02/2025 | 18:29 | 0.01806 | 2.96e-05 | 3 | 1833 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-182318-F | Avalon Dr | Network | AVACB6 | 12/02/2025 | 06:32 | 12/02/2025 | 07:48 | 0.68184 | 0.023814 | 2417 | 69205 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-3032-E | Whatawhata | Network | WHACB4 | 15/02/2025 | 08:39 | 15/02/2025 | 11:30 | 0.0016848 | 9.9e-06 | 1 | 171 | Planned interruptions on the network | Planned | New Connections
|  | INCD-182507-F | Pukete | Network | PUKCB10 | 17/02/2025 | 06:39 | 17/02/2025 | 07:28 | 0.0004828 | 9.9e-06 | 1 | 49 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-182555-F | Horotiu | Network | GORCB12 | 18/02/2025 | 07:35 | 18/02/2025 | 17:07 | 0.020927 | 0.0047391 | 481 | 2124 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-3027-E | Gordonton | Network | GORCB13 | 19/02/2025 | 09:04 | 19/02/2025 | 13:49 | 0.13753 | 0.000532 | 54 | 13959 | Planned interruptions on the network | Planned | Distribution Transformer Replacement
|  | INCD-3036-E | Weavers | Network | WEACB3 | 25/02/2025 | 10:07 | 25/02/2025 | 13:58 | 0.010316 | 4.93e-05 | 5 | 1047 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-3029-E | Finlayson | Network | FINCB2 | 26/02/2025 | 10:05 | 26/02/2025 | 14:44 | 0.07147 | 0.0002857 | 29 | 7254 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-182868-F | Wallace Rd | Network | WALCB6 | 26/02/2025 | 11:42 | 26/02/2025 | 12:32 | 0.003941 | 7.88e-05 | 8 | 400 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-182891-F | Transpower Hamilton | Private | HAMCB2722 | 27/02/2025 | 06:09 | 27/02/2025 | 06:47 | 0.028828 | 0.0007586 | 77 | 2926 | Planned interruptions on the network | Third_party | Mixed Asset Replacement
|  | INCD-182904-F | Transpower Hamilton | Network | HAMCB2722 | 27/02/2025 | 10:02 | 27/02/2025 | 16:47 | 0.71757 | 0.0027094 | 275 | 72831 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-0-L | Peacockes | Network | PEACB13 | 09/03/2025 | 01:37 | 09/03/2025 | 07:18 | 0.12095 | 0.0003547 | 36 | 12276 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-23-K | Silverdale | Network | SILCB4 | 09/03/2025 | 17:11 | 09/03/2025 | 17:53 | 0.11092 | 0.0026405 | 268 | 11258 | Unplanned interruptions on the network | Unknown | Fire Risk Mitigation Patrol - Sucessfully reclosed
|  | INCD-104-K | Weavers | Network | WEACB3 | 12/03/2025 | 07:11 | 12/03/2025 | 08:44 | 0.11196 | 0.0021873 | 222 | 11364 | Unplanned interruptions on the network | Unknown | Fire Risk Mitigation Patrol - Sucessfully reclosed
|  | INCD-145-K | Hoeka | Network | HOECB2 | 12/03/2025 | 23:59 | 13/03/2025 | 00:01 | 0.0016722 | 0.0007488 | 76 | 169.72 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-177-K | Te Kauwhata | Network | TEKCB5 | 13/03/2025 | 16:26 | 13/03/2025 | 18:21 | 0.0045322 | 3.94e-05 | 4 | 460 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-182-K | Transpower Hamilton | Network | HOECB4 | 14/03/2025 | 00:03 | 14/03/2025 | 00:05 | 0.004948 | 0.0024533 | 249 | 502.21 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-214-K | Weavers | Network | WEACB4 | 15/03/2025 | 05:13 | 15/03/2025 | 06:32 | 0.016345 | 0.0002069 | 21 | 1659 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-245-K | Te Kauwhata | Network | TEKCB5 | 17/03/2025 | 04:31 | 17/03/2025 | 05:20 | 0.021134 | 0.0015764 | 160 | 2145 | Unplanned interruptions on the network | Wildlife | Bird betw line & pole
|  | INCD-324-K | Transpower Hamilton | Network | HAMCB2802 | 18/03/2025 | 19:06 | 18/03/2025 | 20:23 | 0.024917 | 0.0003251 | 33 | 2529 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (OUT of Zone)
|  | INCD-410-K | Te Uku | Private | TEUCB11 | 20/03/2025 | 16:14 | 20/03/2025 | 16:43 | 0.0008572 | 2.96e-05 | 3 | 87 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-501-K | Chartwell | Network | CHACB9 | 24/03/2025 | 00:01 | 24/03/2025 | 00:02 | 0.0022365 | 0.0022365 | 227 | 227 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-582-K | Weavers | Network | WEACB6 | 25/03/2025 | 17:25 | 25/03/2025 | 18:43 | 0.0053795 | 6.9e-05 | 7 | 546 | Unplanned interruptions on the network | Defective Equipment | Connect/jumper loose
|  | INCD-600-K | Te Kauwhata | Private | TEKCB2 | 26/03/2025 | 10:04 | 26/03/2025 | 10:50 | 0.03872 | 0.0008276 | 84 | 3930 | Unplanned interruptions on the network | Third_party | Temp Disconnect / safety isolation
|  | INCD-3110-E | Latham | Network | LATCB3 | 27/03/2025 | 08:33 | 27/03/2025 | 14:13 | 0.33094 | 0.0014582 | 148 | 33589 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-662-K | Horotiu | Private | HORCB6 | 28/03/2025 | 09:23 | 28/03/2025 | 15:43 | 0.003744 | 9.9e-06 | 1 | 380 | Unplanned interruptions on the network | Third_party | Temp Disconnect / safety isolation
|  | INCD-694-K | Pukete | Network | PUKCB10 | 28/03/2025 | 14:30 | 28/03/2025 | 18:22 | 0.0068573 | 2.96e-05 | 3 | 696 | Unplanned interruptions on the network | Defective Equipment | Split crossarm
|  | INCD-171048-F | Whatawhata | Network | WHACB2 | 02/04/2024 | 21:08 | 03/04/2024 | 00:48 | 0.14359 | 0.0006503 | 66 | 14574 | Unplanned interruptions on the network | Defective Equipment | Faulty joint/connection
|  | INCD-171071-F | Horotiu | Network | HORCB5 | 03/04/2024 | 19:06 | 03/04/2024 | 19:52 | 0.027725 | 0.0008276 | 84 | 2814 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-171082-F | Ngaruawahia | Network | NGACB2 | 04/04/2024 | 08:32 | 04/04/2024 | 18:01 | 0.28194 | 0.0008276 | 84 | 28616 | Unplanned interruptions on the network | Defective Equipment | Split crossarm
|  | INCD-2295-E | Gordonton | Network | GORCB11 | 04/04/2024 | 10:09 | 04/04/2024 | 14:05 | 0.020927 | 8.87e-05 | 9 | 2124 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2294-E | Weavers | Network | WEACB4 | 10/04/2024 | 09:18 | 10/04/2024 | 13:09 | 0.025035 | 0.0001084 | 11 | 2541 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2317-E | Transpower Hamilton | Network | HAMCB2822 | 11/04/2024 | 06:28 | 11/04/2024 | 20:55 | 0.59322 | 0.0040986 | 416 | 60210 | Planned interruptions on the network | Planned | New Connections
|  | INCD-171349-F | Finlayson Rd | Network | FINCB1 | 11/04/2024 | 13:43 | 11/04/2024 | 20:04 | 0.28324 | 0.0059312 | 602 | 28748 | Unplanned interruptions on the network | Defective Equipment | Corros causes lne brk
|  | INCD-171390-F | Te Kauwhata | Network | FINCB3 | 11/04/2024 | 14:46 | 12/04/2024 | 14:06 | 0.040032 | 0.0024336 | 247 | 4063.13 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-171390-F | Te Kauwhata | Network | FINCB4 | 11/04/2024 | 14:46 | 12/04/2024 | 14:06 | 0.0001621 | 9.9e-06 | 1 | 16.45 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-171390-F | Te Kauwhata | Network | HPTCB2 | 11/04/2024 | 14:46 | 12/04/2024 | 14:06 | 0.0003182 | 2.96e-05 | 3 | 32.3 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2349-E | Ngaruawahia | Network | NGACB3 | 16/04/2024 | 09:04 | 16/04/2024 | 15:15 | 0.085126 | 0.0002365 | 24 | 8640 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2308-E | Wallace | Network | WALCB6 | 18/04/2024 | 09:35 | 18/04/2024 | 15:53 | 0.13791 | 0.0003842 | 39 | 13997 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-171620-F | Steele Park | Network | STECB2 | 19/04/2024 | 14:34 | 19/04/2024 | 15:42 | 0.064987 | 0.0009557 | 97 | 6596 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2304-E | Silverdale | Network | SILCB4 | 23/04/2024 | 09:40 | 23/04/2024 | 15:31 | 0.2497 | 0.0007192 | 73 | 25344 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2237-E | Silverdale | Network | SILCB1 | 23/04/2024 | 09:46 | 23/04/2024 | 15:19 | 0.10162 | 0.0003054 | 31 | 10314 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-2362-E | Latham | Network | LATCB2 | 24/04/2024 | 05:05 | 24/04/2024 | 23:16 | 0.48801 | 0.0025222 | 256 | 49532 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2354-E | Chartwell | Network | CHACB9 | 24/04/2024 | 10:06 | 24/04/2024 | 12:35 | 0.02202 | 0.0001478 | 15 | 2235 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-171771-F | Chartwell | Network | CHACB12 | 29/04/2024 | 10:00 | 29/04/2024 | 12:47 | 0.19744 | 0.0011823 | 120 | 20040 | Unplanned interruptions on the network | Defective Equipment | Cable insulation failure
|  | INCD-2367-E | Silverdale | Network | SILCB5 | 01/05/2024 | 05:38 | 01/05/2024 | 16:52 | 1.046 | 0.0069362 | 704 | 106164 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-2345-E | Te Kauwhata | Network | TEKCB2 | 03/05/2024 | 09:09 | 03/05/2024 | 10:44 | 0.002808 | 2.96e-05 | 3 | 285 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2352-E | Glasgow | Network | GLACB2 | 07/05/2024 | 09:00 | 07/05/2024 | 14:21 | 0.052967 | 0.0003251 | 33 | 5376 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2358-E | Te Kauwhata | Network | TEKCB3 | 09/05/2024 | 09:17 | 09/05/2024 | 14:46 | 0.012966 | 3.94e-05 | 4 | 1316 | Planned interruptions on the network | Planned | Transformer Upgrade
|  | INCD-2409-E | Whatawhata | Network | WHACB3 | 14/05/2024 | 09:10 | 14/05/2024 | 15:09 | 0.19454 | 0.0005419 | 55 | 19745 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-172640-F | Glasgow | Network | GLACB2 | 21/05/2024 | 08:07 | 21/05/2024 | 09:19 | 0.0028375 | 3.94e-05 | 4 | 288 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-172657-F | Whatawhata | Network | WHACB4 | 21/05/2024 | 10:54 | 21/05/2024 | 15:07 | 0.049785 | 0.0001971 | 20 | 5053 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2182-E | Te Kauwhata | Network | TEKCB5 | 23/05/2024 | 09:06 | 23/05/2024 | 15:31 | 0.053105 | 0.0001379 | 14 | 5390 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-172798-F | Horotiu | Network | HORCB6 | 24/05/2024 | 09:18 | 24/05/2024 | 14:01 | 0.23143 | 0.0008178 | 83 | 23489 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-172852-F | Te Kauwhata | Network | TEKCB3 | 25/05/2024 | 20:41 | 25/05/2024 | 22:45 | 0.02808 | 0.0002266 | 23 | 2850 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-172876-F | Horotiu | Network | HORCB6 | 26/05/2024 | 14:17 | 26/05/2024 | 14:44 | 0.022562 | 0.0008276 | 84 | 2290 | Unplanned interruptions on the network | Adverse weather | High wind lne break
|  | INCD-172921-F | Horotiu | Network | HORCB6 | 26/05/2024 | 14:44 | 26/05/2024 | 16:36 | 0.0010936 | 9.9e-06 | 1 | 111 | Unplanned interruptions on the network | Adverse weather | High wind lne break
|  | INCD-173004-F | Te Uku | Network | TEUCB11 | 29/05/2024 | 08:57 | 30/05/2024 | 20:41 | 0.7676 | 0.00267 | 271 | 77909 | Unplanned interruptions on the network | Adverse weather | High wind lne break
|  | INCD-173052-F | Hoeka | Network | HOECB3 | 29/05/2024 | 09:38 | 29/05/2024 | 14:15 | 0.019104 | 6.9e-05 | 7 | 1939 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (IN Zone)
|  | INCD-173079-F | Whatawhata | Network | RAGCB2 | 29/05/2024 | 14:19 | 29/05/2024 | 14:38 | 0.13765 | 0.0070051 | 711 | 13971.08 | Unplanned interruptions on the network | Adverse weather | Wind line clash
|  | INCD-173082-F | Pukete | Network | HORCB5 | 29/05/2024 | 14:25 | 29/05/2024 | 14:28 | 0.0010323 | 2.96e-05 | 3 | 104.78 | Unplanned interruptions on the network | Adverse weather | High wind lne break
|  | INCD-173091-F | Transpower Hamilton | Network | CHACB12 | 29/05/2024 | 14:31 | 29/05/2024 | 19:03 | 1.6681 | 0.02074 | 2105 | 169306.8 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (IN Zone)
|  | INCD-173091-F | Transpower Hamilton | Network | CHACB15 | 29/05/2024 | 14:31 | 29/05/2024 | 19:03 | 1.125 | 0.012158 | 1234 | 114186 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (IN Zone)
|  | INCD-173091-F | Transpower Hamilton | Network | HAMCB2902 | 29/05/2024 | 14:31 | 29/05/2024 | 19:03 | 0.0009396 | 9.9e-06 | 1 | 95.37 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (IN Zone)
|  | INCD-173108-F | Weavers | Network | HORCB6 | 29/05/2024 | 15:01 | 29/05/2024 | 15:06 | 0.021114 | 0.0046405 | 471 | 2142.97 | Unplanned interruptions on the network | Adverse weather | Wind line clash
|  | INCD-2488-E | Finlayson | Network | FINCB3 | 29/05/2024 | 16:45 | 31/05/2024 | 13:43 | 0.10631 | 3.94e-05 | 4 | 10790 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-173259-F | Weavers | Network | WEACB3 | 30/05/2024 | 09:18 | 30/05/2024 | 09:55 | 0.0003645 | 9.9e-06 | 1 | 37 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-173271-F | Weavers | Network | WEACB3 | 29/05/2024 | 16:40 | 30/05/2024 | 10:44 | 0.042721 | 3.94e-05 | 4 | 4336 | Unplanned interruptions on the network | Adverse weather | Line clash high wind
|  | INCD-173444-F | Hampton Downs | Network | HPTCB5 | 01/06/2024 | 08:40 | 01/06/2024 | 16:13 | 0.11134 | 0.0002463 | 25 | 11301 | Unplanned interruptions on the network | Defective Equipment | Fuse blown on overload
|  | INCD-173458-F | Hampton Downs | Network | HPTCB5 | 01/06/2024 | 13:15 | 01/06/2024 | 15:14 | 0.010552 | 8.87e-05 | 9 | 1071 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-2186-E | Te Kauwhata | Network | TEKCB5 | 05/06/2024 | 09:45 | 05/06/2024 | 15:43 | 0.069106 | 0.0002266 | 23 | 7014 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-173682-F | Te Uku | Network | TEUCB12 | 06/06/2024 | 12:12 | 06/06/2024 | 14:36 | 0.062426 | 0.0004335 | 44 | 6336 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-173760-F | Finlayson Rd | Network | FINCB2 | 08/06/2024 | 06:42 | 08/06/2024 | 07:30 | 0.0038326 | 7.88e-05 | 8 | 389 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-174043-F | Ngaruawahia | Network | NGACB6 | 17/06/2024 | 01:09 | 17/06/2024 | 15:50 | 0.5072 | 0.0014188 | 144 | 51479 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-17607-G | Weavers | Network | WEACB6 | 18/06/2024 | 13:01 | 18/06/2024 | 16:00 | 0.0017636 | 9.9e-06 | 1 | 179 | Planned interruptions on the network | Planned | 11kV Fuse Replacement
|  | INCD-2469-E | Peacockes | Network | PEACB11 | 24/06/2024 | 07:04 | 24/06/2024 | 07:53 | 0.0061874 | 0.0001379 | 14 | 628 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-174321-F | Te Uku | Network | TEUCB11 | 24/06/2024 | 06:58 | 24/06/2024 | 09:36 | 0.0015567 | 9.9e-06 | 1 | 158 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-174491-F | Hoeka | Network | HOECB6 | 29/06/2024 | 12:09 | 29/06/2024 | 18:43 | 0.023291 | 5.91e-05 | 6 | 2364 | Unplanned interruptions on the network | Defective Equipment | Intnl insulation failure
|  | INCD-174590-F | Te Kauwhata | Network | TEKCB5 | 02/07/2024 | 06:45 | 02/07/2024 | 09:20 | 0.0030543 | 1.97e-05 | 2 | 310 | Unplanned interruptions on the network | Defective Equipment | Connect/jumper loose
|  | INCD-2501-E | Hampton Downs | Network | HPTCB5 | 02/07/2024 | 09:53 | 02/07/2024 | 13:15 | 0.0079608 | 3.94e-05 | 4 | 808 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-174772-F | Whatawhata | Network | WHACB3 | 07/07/2024 | 14:38 | 07/07/2024 | 19:12 | 0.39814 | 0.0015468 | 157 | 40410 | Unplanned interruptions on the network | Defective Equipment | Hairline crack
|  | INCD-174784-F | Raglan | Network | RAGCB6 | 07/07/2024 | 21:43 | 08/07/2024 | 00:49 | 0.0788 | 0.0004237 | 43 | 7998 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-174788-F | Horotiu | Network | NGACB2 | 08/07/2024 | 05:07 | 08/07/2024 | 06:01 | 0.010641 | 0.0001971 | 20 | 1080 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-174953-F | Weavers | Network | WEACB2 | 10/07/2024 | 14:11 | 10/07/2024 | 15:10 | 0.0005813 | 9.9e-06 | 1 | 59 | Unplanned interruptions on the network | Wildlife | Bird betw line & pole
|  | INCD-17627-G | Peacockes Rd | Network | PEACB18 | 12/07/2024 | 12:22 | 12/07/2024 | 15:38 | 0.0096555 | 4.93e-05 | 5 | 980 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-175283-F | Te Uku | Network | TEUCB11 | 17/07/2024 | 18:42 | 17/07/2024 | 19:06 | 0.027942 | 0.0011724 | 119 | 2836 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-175332-F | Transpower Hamilton | Network | HAMCB2902 | 18/07/2024 | 21:01 | 18/07/2024 | 21:05 | 0.021528 | 0.0055667 | 565 | 2185 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-2553-E | Glasgow | Network | GLACB1 | 19/07/2024 | 09:11 | 19/07/2024 | 10:48 | 0.0038228 | 3.94e-05 | 4 | 388 | Planned interruptions on the network | Planned | 11kV Fuse Replacement
|  | INCD-175542-F | Ngaruawahia | Network | NGACB2 | 25/07/2024 | 09:04 | 25/07/2024 | 16:34 | 0.22326 | 0.0005222 | 53 | 22660 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-175639-F | Peacockes | Private | PEACB18 | 30/07/2024 | 14:09 | 30/07/2024 | 14:35 | 0.0010247 | 3.94e-05 | 4 | 104 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-2625-E | Hampton Downs | Network | HPTCB5 | 31/07/2024 | 08:33 | 31/07/2024 | 15:25 | 0.24691 | 0.001468 | 149 | 25061 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-175663-F | Weavers | Network | TEKCB5 | 31/07/2024 | 10:27 | 31/07/2024 | 15:44 | 0.15603 | 0.0005912 | 60 | 15837 | Unplanned interruptions on the network | Defective Equipment | Line break at twist joint
|  | INCD-175701-F | Horotiu | Network | HORCB6 | 01/08/2024 | 09:03 | 01/08/2024 | 14:00 | 0.14061 | 0.0004926 | 50 | 14271 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2613-E | Gordonton | Network | GORCB12 | 02/08/2024 | 09:13 | 02/08/2024 | 15:06 | 0.0069559 | 1.97e-05 | 2 | 706 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-175799-F | Peacockes Rd | Network | PEACB14 | 03/08/2024 | 00:25 | 03/08/2024 | 10:57 | 0.40474 | 0.0006404 | 65 | 41080 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-175921-F | Te Uku | Network | TEUCB11 | 06/08/2024 | 00:25 | 06/08/2024 | 04:07 | 0.21179 | 0.0033203 | 337 | 21496 | Unplanned interruptions on the network | Wildlife | Possum contacts line
|  | INCD-2642-E | Transpower Hamilton | Network | HAMCB2902 | 06/08/2024 | 08:02 | 06/08/2024 | 15:25 | 0.48448 | 0.0010936 | 111 | 49173 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-175979-F | Peacockes Rd | Network | PEACB17 | 07/08/2024 | 06:04 | 07/08/2024 | 07:21 | 0.10123 | 0.0021084 | 214 | 10275 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-175990-F | Peacockes Rd | Network | PEACB17 | 07/08/2024 | 09:39 | 07/08/2024 | 18:04 | 0.42645 | 0.0021084 | 214 | 43283 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-176035-F | Hampton Downs | Network | HPTCB5 | 08/08/2024 | 07:55 | 08/08/2024 | 09:44 | 0.0042957 | 3.94e-05 | 4 | 436 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-176173-F | Pukete | Network | PUKCB5 | 11/08/2024 | 02:25 | 11/08/2024 | 05:39 | 0.13571 | 0.0006995 | 71 | 13774 | Unplanned interruptions on the network | Wildlife | Caused by rat
|  | INCD-176265-F | Whatawhata | Network | WHACB2 | 13/08/2024 | 17:11 | 14/08/2024 | 00:22 | 0.47071 | 0.0010936 | 111 | 47776 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-176268-F | Whatawhata | Network | WHACB2 | 13/08/2024 | 20:20 | 13/08/2024 | 20:22 | 0.0068771 | 0.0035272 | 358 | 698 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-176347-F | Ngaruawahia | Network | NGACB2 | 15/08/2024 | 04:24 | 15/08/2024 | 12:00 | 0.45303 | 0.0024631 | 250 | 45981 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-176555-F | Gordonton | Network | GORCB13 | 15/08/2024 | 19:31 | 15/08/2024 | 21:13 | 0.0020099 | 1.97e-05 | 2 | 204 | Unplanned interruptions on the network | Defective Equipment | Loss or failure of oil
|  | INCD-2652-E | Whatawhata | Network | WHACB4 | 16/08/2024 | 09:11 | 16/08/2024 | 11:16 | 0.012316 | 9.85e-05 | 10 | 1250 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-176533-F | Whatawhata | Network | TEUCB11 | 19/08/2024 | 06:57 | 19/08/2024 | 16:19 | 3.7466 | 0.012779 | 1297 | 380273 | Unplanned interruptions on the network | Defective Equipment | Cable termination fails
|  | INCD-176533-F | Whatawhata | Network | TEUCB12 | 19/08/2024 | 06:57 | 19/08/2024 | 16:19 | 1.2434 | 0.0026799 | 272 | 126200.27 | Unplanned interruptions on the network | Defective Equipment | Cable termination fails
|  | INCD-176600-F | Te Uku | Network | TEUCB11 | 19/08/2024 | 15:26 | 19/08/2024 | 15:31 | 0.0065716 | 0.0013005 | 132 | 667 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-176735-F | Steele Park | Network | STECB3 | 21/08/2024 | 09:25 | 21/08/2024 | 09:29 | 0.0035075 | 0.0008769 | 89 | 356 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-176804-F | Borman | Network | BORCB5 | 22/08/2024 | 17:03 | 22/08/2024 | 18:21 | 0.0007685 | 9.9e-06 | 1 | 78 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-176810-F | Ngaruawahia | Network | NGACB5 | 22/08/2024 | 19:33 | 23/08/2024 | 04:36 | 0.40498 | 0.0011035 | 112 | 41104 | Unplanned interruptions on the network | Defective Equipment | Intnl insulation failure
|  | INCD-176892-F | Borman Rd | Network | CHACB13 | 26/08/2024 | 04:06 | 26/08/2024 | 05:07 | 0.083727 | 0.0015567 | 158 | 8498 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-176916-F | Weavers | Network | WEACB2 | 26/08/2024 | 08:53 | 26/08/2024 | 13:02 | 0.0024533 | 9.9e-06 | 1 | 249 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-177014-F | Chartwell | Network | CHACB13 | 28/08/2024 | 09:20 | 28/08/2024 | 10:24 | 0.040356 | 0.0006306 | 64 | 4096 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-177015-F | Ngaruawahia | Network | NGACB2 | 28/08/2024 | 09:43 | 28/08/2024 | 15:01 | 0.13925 | 0.0004729 | 48 | 14133 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-177080-F | Weavers | Network | WEACB3 | 29/08/2024 | 11:10 | 29/08/2024 | 11:26 | 0.0001576 | 9.9e-06 | 1 | 16 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-177095-F | Weavers | Network | WEACB3 | 29/08/2024 | 15:40 | 29/08/2024 | 15:54 | 0.0001379 | 9.9e-06 | 1 | 14 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-177262-F | Gordonton | Network | GORCB12 | 29/08/2024 | 23:14 | 29/08/2024 | 23:38 | 0.004542 | 0.0013991 | 142 | 461 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-177140-F | Te Kauwhata | Network | TEKCB5 | 30/08/2024 | 10:01 | 30/08/2024 | 10:23 | 0.0006503 | 2.96e-05 | 3 | 66 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-177230-F | Hampton Downs | Network | HPTCB5 | 01/09/2024 | 10:23 | 01/09/2024 | 21:04 | 0.025262 | 3.94e-05 | 4 | 2564 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-177296-F | Whatawhata | Network | WHACB4 | 03/09/2024 | 09:04 | 03/09/2024 | 14:17 | 0.15791 | 0.0005222 | 53 | 16027 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2718-E | Te Uku | Network | TEUCB11 | 03/09/2024 | 09:13 | 03/09/2024 | 14:56 | 0.04275 | 0.0001281 | 13 | 4339 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-177344-F | Chartwell | Network | CHACB13 | 04/09/2024 | 09:07 | 04/09/2024 | 10:19 | 0.15128 | 0.0022562 | 229 | 15354 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-2728-E | Weavers | Network | WEACB3 | 06/09/2024 | 10:04 | 06/09/2024 | 14:52 | 0.12414 | 0.0004729 | 48 | 12600 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-177623-F | Weavers | Network | WEACB3 | 12/09/2024 | 09:34 | 12/09/2024 | 15:03 | 0.14748 | 0.0004631 | 47 | 14969 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-177666-F | Weavers | Network | WEACB2 | 13/09/2024 | 09:30 | 13/09/2024 | 11:07 | 0.0009557 | 9.9e-06 | 1 | 97 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-177871-F | Gordonton | Network | GORCB13 | 19/09/2024 | 14:02 | 19/09/2024 | 18:55 | 0.11388 | 0.0019606 | 199 | 11558 | Unplanned interruptions on the network | Defective Equipment | Broken binder
|  | INCD-177888-F | Chartwell | Network | CHACB9 | 20/09/2024 | 07:10 | 20/09/2024 | 08:02 | 0.0005123 | 9.9e-06 | 1 | 52 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-177976-F | Chartwell | Network | CHACB10 | 23/09/2024 | 08:34 | 23/09/2024 | 15:02 | 0.27012 | 0.0009064 | 92 | 27416 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2637-E | Borman | Network | BORCB5 | 24/09/2024 | 06:34 | 24/09/2024 | 16:37 | 0.029213 | 0.0001084 | 11 | 2965 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-2771-E | Rural Bank | Network | RURCB1 | 24/09/2024 | 06:45 | 24/09/2024 | 07:01 | 0.0040986 | 0.0002562 | 26 | 416 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-178174-F | Weavers | Network | WEACB6 | 27/09/2024 | 09:00 | 27/09/2024 | 11:58 | 0.051332 | 0.0003054 | 31 | 5210 | Planned interruptions on the network | Planned | New Connections
|  | INCD-178342-F | Avalon | Network | AVACB8 | 02/10/2024 | 09:31 | 02/10/2024 | 14:02 | 0.17623 | 0.00067 | 68 | 17887 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-17658-G | Peacockes | Network | PEACB13 | 06/10/2024 | 07:10 | 06/10/2024 | 07:56 | 0.064219 | 0.0017636 | 179 | 6518 | Planned interruptions on the network | Planned | 11kV Fuse Replacement
|  | INCD-17659-G | Peacockes | Network | PEACB13 | 06/10/2024 | 16:10 | 06/10/2024 | 16:20 | 0.0049263 | 0.0004926 | 50 | 500 | Planned interruptions on the network | Planned | 11kV Fuse Replacement
|  | INCD-2747-E | Hoeka | Network | HOECB6 | 08/10/2024 | 09:31 | 08/10/2024 | 15:03 | 0.028848 | 0.0055371 | 562 | 2928 | Planned interruptions on the network | Planned | 11kV Fuse Replacement
|  | INCD-178638-F | Chartwell | Network | CHACB13 | 11/10/2024 | 04:11 | 11/10/2024 | 06:10 | 0.15113 | 0.0020986 | 213 | 15339 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-178746-F | Finlayson Rd | Network | FINCB3 | 14/10/2024 | 12:00 | 14/10/2024 | 20:13 | 0.05865 | 0.0025321 | 257 | 5952.77 | Unplanned interruptions on the network | Defective Equipment | Contact problem
|  | INCD-178819-F | Gordonton | Network | GORCB13 | 16/10/2024 | 09:06 | 16/10/2024 | 14:33 | 0.012887 | 3.94e-05 | 4 | 1308 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-178383-F | Gordonton | Network | GORCB13 | 23/10/2024 | 09:18 | 23/10/2024 | 13:12 | 0.016138 | 6.9e-05 | 7 | 1638 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2829-E | Weavers | Network | WEACB3 | 23/10/2024 | 09:20 | 23/10/2024 | 13:40 | 0.040977 | 0.0001576 | 16 | 4159 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-179085-F | Whatawhata | Network | WHACB5 | 24/10/2024 | 06:03 | 24/10/2024 | 06:33 | 0.0005912 | 1.97e-05 | 2 | 60 | Unplanned interruptions on the network | Defective Equipment | Stay wire/ line clash
|  | INCD-179248-F | Horotiu | Network | HORCB5 | 28/10/2024 | 06:00 | 28/10/2024 | 08:18 | 0.0094683 | 6.9e-05 | 7 | 961 | Unplanned interruptions on the network | Defective Equipment | Jumpers come off
|  | INCD-2870-E | Weavers | Network | WEACB6 | 30/10/2024 | 09:06 | 30/10/2024 | 15:43 | 0.07083 | 0.0001872 | 19 | 7189 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2859-E | Finlayson | Network | FINCB3 | 01/11/2024 | 08:28 | 01/11/2024 | 14:33 | 0.35617 | 0.0010148 | 103 | 36150 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-179490-F | Gordonton | Network | GORCB11 | 02/11/2024 | 23:01 | 03/11/2024 | 02:18 | 0.017469 | 8.87e-05 | 9 | 1773 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-179611-F | Weavers | Network | WEACB2 | 09/11/2024 | 06:43 | 09/11/2024 | 09:40 | 0.015695 | 8.87e-05 | 9 | 1593 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2881-E | Borman | Network | BORCB2 | 12/11/2024 | 09:33 | 12/11/2024 | 15:32 | 0.017685 | 4.93e-05 | 5 | 1795 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-179713-F | Traspower Hamilton | Network | HAMCB2802 | 13/11/2024 | 05:32 | 13/11/2024 | 06:30 | 0.0005714 | 9.9e-06 | 1 | 58 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-179970-F | Raglan | Network | RAGCB2 | 21/11/2024 | 08:39 | 21/11/2024 | 09:18 | 0.50728 | 0.0012119 | 123 | 51487 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-180010-F | Raglan | Network | RAGCB2 | 22/11/2024 | 01:00 | 22/11/2024 | 01:32 | 0.038292 | 0.0077047 | 782 | 3886.55 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2861-E | Te Uku | Network | TEUCB11 | 22/11/2024 | 09:09 | 22/11/2024 | 14:57 | 0.12402 | 0.0003645 | 37 | 12588 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2901-E | Glasgow | Network | GLACB2 | 22/11/2024 | 09:37 | 22/11/2024 | 10:33 | 0.0011035 | 1.97e-05 | 2 | 112 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-180096-F | Transpower Hamilton | Network | HAMCB2802 | 25/11/2024 | 15:05 | 25/11/2024 | 15:16 | 0.0062563 | 0.0005517 | 56 | 635 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2924-E | Chartwell | Network | CHACB9 | 02/12/2024 | 09:05 | 02/12/2024 | 11:45 | 0.036257 | 0.0002266 | 23 | 3680 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2932-E | Weavers | Network | WEACB6 | 04/12/2024 | 08:41 | 04/12/2024 | 17:27 | 0.041932 | 8.87e-05 | 9 | 4256 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2925-E | Hoeka | Network | HOECB1 | 05/12/2024 | 09:00 | 05/12/2024 | 16:31 | 0.46151 | 0.0010838 | 110 | 46842 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-180455-F | Weavers | Network | WEACB3 | 06/12/2024 | 04:24 | 06/12/2024 | 06:02 | 0.0028966 | 2.96e-05 | 3 | 294 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-17686-G | Te Kauwhata | Network | TEKCB5 | 06/12/2024 | 09:04 | 06/12/2024 | 11:44 | 0.0031528 | 1.97e-05 | 2 | 320 | Planned interruptions on the network | Planned | Transformer Upgrade
|  | INCD-2928-E | Horotiu | Network | HORCB3 | 06/12/2024 | 09:06 | 06/12/2024 | 11:14 | 0.0037834 | 2.96e-05 | 3 | 384 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-17692-G | Glasgow | Network | GLACB2 | 09/12/2024 | 05:23 | 09/12/2024 | 06:38 | 0.0022168 | 2.96e-05 | 3 | 225 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2957-E | Gordonton | Network | GORCB11 | 11/12/2024 | 09:04 | 11/12/2024 | 20:00 | 0.067992 | 0.0001084 | 11 | 6901 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2965-E | Weavers | Network | WEACB3 | 19/12/2024 | 08:17 | 19/12/2024 | 16:56 | 0.22171 | 0.0006109 | 62 | 22503 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-17704-G | Horotiu | Network | HORCB5 | 23/12/2024 | 06:56 | 23/12/2024 | 13:06 | 0.24789 | 0.00067 | 68 | 25160 | Unplanned interruptions on the network | Defective Equipment | Cable fails unknown
|  | INCD-181007-F | Glasgow St | Network | GLACB6 | 27/12/2024 | 15:29 | 27/12/2024 | 20:55 | 0.08351 | 0.0002562 | 26 | 8476 | Unplanned interruptions on the network | Defective Equipment | Faulty joint/connection
|  | INCD-181095-F | Weavers | Network | FINCB3 | 02/01/2025 | 03:59 | 02/01/2025 | 04:00 | 0.0026763 | 0.0024336 | 247 | 271.64 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-181139-F | Wallace | Network | WALCB6 | 04/01/2025 | 19:04 | 04/01/2025 | 22:06 | 0.010759 | 5.91e-05 | 6 | 1092 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-181141-F | Transpower Hamilton | Network | HAMCB2802 | 05/01/2025 | 06:23 | 05/01/2025 | 08:10 | 0.0021084 | 1.97e-05 | 2 | 214 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2975-E | Ngaruawahia | Network | NGACB5 | 07/01/2025 | 10:06 | 07/01/2025 | 12:04 | 0.15346 | 0.0013005 | 132 | 15576 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-181249-F | Whatawhata | Network | WHACB5 | 09/01/2025 | 00:06 | 09/01/2025 | 01:06 | 0.031922 | 0.000532 | 54 | 3240 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (OUT of Zone)
|  | INCD-181389-F | Weavers | Network | GLACB2 | 14/01/2025 | 03:24 | 14/01/2025 | 05:24 | 0.0090822 | 0.0004631 | 47 | 921.82 | Unplanned interruptions on the network | Wildlife | Possum contacts line
|  | INCD-17722-G | Te Kauwhata | Network | TEKCB3 | 16/01/2025 | 00:01 | 16/01/2025 | 01:32 | 0.0035863 | 3.94e-05 | 4 | 364 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-181732-F | Finlayson | Network | FINCB2 | 23/01/2025 | 09:00 | 23/01/2025 | 14:13 | 0.168 | 0.0006798 | 69 | 17052 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-181938-F | Latham Court | Network | LATCB1 | 29/01/2025 | 22:31 | 30/01/2025 | 08:25 | 0.7986 | 0.0013695 | 139 | 81056 | Unplanned interruptions on the network | Defective Equipment | Cable termination fails
|  | INCD-182087-F | Te Kauwhata | Network | TEKCB5 | 03/02/2025 | 17:42 | 03/02/2025 | 20:51 | 0.014897 | 7.88e-05 | 8 | 1512 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-182132-F | Raglan | Network | RAGCB6 | 05/02/2025 | 07:37 | 05/02/2025 | 12:16 | 0.12795 | 0.0005222 | 53 | 12987 | Unplanned interruptions on the network | Defective Equipment | Line break at twist joint
|  | INCD-2993-E | Horotiu | Network | HORCB4 | 05/02/2025 | 10:06 | 05/02/2025 | 14:47 | 0.013843 | 4.93e-05 | 5 | 1405 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-182253-F | Finlayson Rd | Network | FINCB1 | 10/02/2025 | 18:46 | 10/02/2025 | 19:36 | 0.066908 | 0.0041085 | 417 | 6791 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-17739-G | Weavers | Private | WEACB2 | 12/02/2025 | 09:25 | 12/02/2025 | 10:31 | 0.0026011 | 3.94e-05 | 4 | 264 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-182375-F | Weavers | Network | WEACB4 | 12/02/2025 | 23:26 | 13/02/2025 | 01:07 | 0.010946 | 0.0001084 | 11 | 1111 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-3024-E | Weavers | Network | WEACB6 | 20/02/2025 | 12:22 | 20/02/2025 | 13:30 | 0.0033499 | 4.93e-05 | 5 | 340 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-182740-F | Te Uku | Network | TEUCB11 | 22/02/2025 | 01:07 | 22/02/2025 | 02:19 | 0.087047 | 0.0012119 | 123 | 8835 | Unplanned interruptions on the network | Unknown | Fire Risk Mitigation Patrol - Sucessfully reclosed
|  | INCD-3043-E | Horotiu | Network | HORCB4 | 22/02/2025 | 09:35 | 22/02/2025 | 11:47 | 0.0013005 | 9.9e-06 | 1 | 132 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-3036-E | Weavers | Network | GLACB6 | 25/02/2025 | 10:07 | 25/02/2025 | 13:58 | 0.0019606 | 9.9e-06 | 1 | 199 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-182845-F | Peacockes Rd | Network | PEACB12 | 26/02/2025 | 01:06 | 26/02/2025 | 02:02 | 0.12468 | 0.0022365 | 227 | 12655 | Unplanned interruptions on the network | Unknown | Fire Risk Mitigation Patrol - Sucessfully reclosed
|  | INCD-3038-E | Finlayson | Network | FINCB2 | 26/02/2025 | 09:31 | 26/02/2025 | 15:15 | 0.04745 | 0.0001379 | 14 | 4816 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-182904-F | Transpower Hamilton | Network | CLACB16 | 27/02/2025 | 10:02 | 27/02/2025 | 16:47 | 0.25678 | 0.0008178 | 83 | 26062 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-3044-E | Glasgow | Network | GLACB5 | 01/03/2025 | 08:46 | 01/03/2025 | 10:58 | 0.0013005 | 9.9e-06 | 1 | 132 | Planned interruptions on the network | Planned | New Connections
|  | INCD-183104-F | Whatawhata | Network | WHACB2 | 05/03/2025 | 13:36 | 05/03/2025 | 17:15 | 0.0064731 | 2.96e-05 | 3 | 657 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-17744-G | Transpower Hamilton | Network | HAMCB2722 | 05/03/2025 | 23:59 | 06/03/2025 | 00:06 | 0.016276 | 0.0023252 | 236 | 1652 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-17745-G | Transpower Hamilton | Network | HAMCB2722 | 06/03/2025 | 06:03 | 06/03/2025 | 06:41 | 0.028828 | 0.0007586 | 77 | 2926 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-183165-F | Whatawhata | Network | WHACB4 | 07/03/2025 | 10:04 | 07/03/2025 | 15:28 | 0.10686 | 0.0018424 | 187 | 10846 | Unplanned interruptions on the network | Third_party | High vehicle contact
|  | INCD-143-K | Hoeka | Network | HOECB2 | 12/03/2025 | 23:59 | 13/03/2025 | 00:00 | 0.0007586 | 0.0007882 | 80 | 77 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-145-K | Hoeka | Network | HOECB3 | 12/03/2025 | 23:59 | 13/03/2025 | 00:01 | 0.0055007 | 0.0024631 | 250 | 558.3 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-182-K | Transpower Hamilton | Network | HOECB1 | 14/03/2025 | 00:03 | 14/03/2025 | 00:05 | 0.012678 | 0.0062859 | 638 | 1286.79 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-184-K | Weavers | Network | WEACB6 | 14/03/2025 | 03:58 | 14/03/2025 | 05:33 | 0.062751 | 0.0012316 | 125 | 6369 | Unplanned interruptions on the network | Unknown | Fire Risk Mitigation Patrol - Sucessfully reclosed
|  | INCD-3083-E | Wallace | Network | WALCB2 | 18/03/2025 | 09:01 | 18/03/2025 | 15:51 | 0.38999 | 0.0036454 | 370 | 39583 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-3085-E | Te Uku | Network | RAGCB6 | 19/03/2025 | 08:39 | 19/03/2025 | 13:03 | 0.0026011 | 9.9e-06 | 1 | 264 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-409-K | Transpower Hamilton | Network | HAMCB2722 | 20/03/2025 | 15:59 | 20/03/2025 | 16:38 | 0.029587 | 0.0007586 | 77 | 3003 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-536-K | Steele Park | Network | STECB3 | 24/03/2025 | 14:32 | 24/03/2025 | 14:35 | 0.0036947 | 0.0012316 | 125 | 375 | Planned interruptions on the network | Planned | Relocations
|  | INCD-543-K | Transpower Hamilton | Network | CHACB9 | 25/03/2025 | 00:02 | 25/03/2025 | 00:02 | 0.0033597 | 0.0022365 | 227 | 341 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-3084-E | Weavers | Network | WEACB6 | 26/03/2025 | 08:31 | 26/03/2025 | 10:22 | 0.0021873 | 1.97e-05 | 2 | 222 | Planned interruptions on the network | Planned | New Connections
|  | INCD-595-K | Wallace Rd | Network | WALCB6 | 26/03/2025 | 09:22 | 26/03/2025 | 11:45 | 0.0098624 | 6.9e-05 | 7 | 1001 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-658-K | Weavers | Network | WEACB2 | 28/03/2025 | 07:36 | 28/03/2025 | 08:52 | 0.0022464 | 2.96e-05 | 3 | 228 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2265-E | Te Kauwhata | Network | TEKCB5 | 04/04/2024 | 10:05 | 04/04/2024 | 14:15 | 0.10968 | 0.0004631 | 47 | 11132 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-171156-F | Horotiu | Network | HORCB6 | 05/04/2024 | 12:35 | 05/04/2024 | 14:46 | 0.068396 | 0.0005222 | 53 | 6942 | Unplanned interruptions on the network | Third_party | Vehicle hits lines
|  | INCD-171206-F | Peacockes Rd | Network | PEACB17 | 07/04/2024 | 09:00 | 07/04/2024 | 13:44 | 0.25936 | 0.0009163 | 93 | 26324 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-171207-F | Peacockes Rd | Network | PEACB17 | 07/04/2024 | 09:00 | 07/04/2024 | 13:55 | 0.01738 | 5.91e-05 | 6 | 1764 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-171264-F | Te Uku | Network | TEUCB12 | 09/04/2024 | 21:52 | 09/04/2024 | 23:59 | 0.0046464 | 0.0026799 | 272 | 471.6 | Unplanned interruptions on the network | Wildlife | Possum contacts line
|  | INCD-171270-F | Te Uku | Network | TEUCB12 | 09/04/2024 | 23:50 | 09/04/2024 | 23:54 | 0.011876 | 0.0026799 | 272 | 1205.41 | Unplanned interruptions on the network | Wildlife | Possum contacts line
|  | INCD-171312-F | Sandwich Rd | Network | SANCB4 | 10/04/2024 | 22:18 | 11/04/2024 | 01:39 | 0.56516 | 0.0028178 | 286 | 57362 | Unplanned interruptions on the network | Defective Equipment | Insulator split
|  | INCD-171390-F | Te Kauwhata | Network | HPTCB4 | 11/04/2024 | 14:46 | 12/04/2024 | 14:06 | 0.0001542 | 9.9e-06 | 1 | 15.65 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-171372-F | Avalon Dr | Network | AVACB4 | 12/04/2024 | 08:32 | 12/04/2024 | 15:14 | 0.44782 | 0.0011429 | 116 | 45452 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-171386-F | Hoeka | Network | HOECB3 | 12/04/2024 | 12:24 | 12/04/2024 | 23:21 | 0.71026 | 0.0084929 | 862 | 72089.21 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-171386-F | Hoeka | Network | HOECB6 | 12/04/2024 | 12:24 | 12/04/2024 | 23:21 | 0.030767 | 0.0008276 | 84 | 3122.79 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-171389-F | Chartwell | Network | CHACB9 | 12/04/2024 | 13:05 | 12/04/2024 | 13:24 | 0.023262 | 0.0035666 | 362 | 2361 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-171411-F | Tasman | Network | TASCB4 | 13/04/2024 | 07:23 | 13/04/2024 | 15:20 | 0.031006 | 4.93e-05 | 5 | 3147 | Planned interruptions on the network | Planned | Distribution Transformer Replacement
|  | INCD-171475-F | Weavers | Network | WEACB5 | 15/04/2024 | 13:15 | 15/04/2024 | 17:21 | 0.16821 | 0.0040986 | 416 | 17073 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-171500-F | Tasman | Network | TASCB5 | 15/04/2024 | 22:11 | 16/04/2024 | 02:13 | 0.021459 | 8.87e-05 | 9 | 2178 | Unplanned interruptions on the network | Defective Equipment | Nut or bolt loose
|  | INCD-2312-E | Glasgow | Network | GLACB2 | 16/04/2024 | 09:06 | 16/04/2024 | 10:56 | 0.0010838 | 9.9e-06 | 1 | 110 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2266-E | Silverdale | Network | SILCB2 | 16/04/2024 | 09:34 | 16/04/2024 | 17:17 | 0.086071 | 0.0002069 | 21 | 8736 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-171542-F | Peacockes Rd | Network | PEACB12 | 16/04/2024 | 19:35 | 16/04/2024 | 20:12 | 0.0069263 | 0.0001872 | 19 | 703 | Unplanned interruptions on the network | Defective Equipment | Connect/jumper loose
|  | INCD-171610-F | Horotiu | Network | HORCB5 | 19/04/2024 | 09:50 | 19/04/2024 | 10:23 | 0.0013005 | 3.94e-05 | 4 | 132 | Unplanned interruptions on the network | Defective Equipment | Mechanism seized
|  | INCD-171623-F | Horotiu | Network | HORCB5 | 19/04/2024 | 14:29 | 19/04/2024 | 16:59 | 0.0014779 | 9.9e-06 | 1 | 150 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-2179-E | Te Kauwhata | Network | TEKCB5 | 21/04/2024 | 08:32 | 21/04/2024 | 17:35 | 0.14035 | 0.000266 | 27 | 14245 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-2353-E | Steele Park | Network | STECB2 | 22/04/2024 | 08:31 | 22/04/2024 | 16:16 | 0.19705 | 0.0047292 | 480 | 20000 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2260-E | Whatawhata | Network | WHACB3 | 23/04/2024 | 09:42 | 23/04/2024 | 13:03 | 0.0079214 | 3.94e-05 | 4 | 804 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2362-E | Latham | Network | LATCB5 | 24/04/2024 | 05:05 | 24/04/2024 | 23:16 | 0.065165 | 0.001872 | 190 | 6614 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2239-E | Hoeka | Network | HOECB4 | 30/04/2024 | 09:30 | 30/04/2024 | 15:52 | 0.36098 | 0.0010641 | 108 | 36638 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-171853-F | Horotiu | Private | HORCB5 | 01/05/2024 | 12:29 | 01/05/2024 | 13:12 | 0.0008473 | 1.97e-05 | 2 | 86 | Unplanned interruptions on the network | Third_party | Temp Disconnect / safety isolation
|  | INCD-2344-E | Glasgow | Network | GLACB6 | 02/05/2024 | 09:02 | 02/05/2024 | 11:14 | 0.010404 | 7.88e-05 | 8 | 1056 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2318-E | Glasgow | Network | GLACB5 | 05/05/2024 | 09:01 | 05/05/2024 | 10:58 | 0.0057637 | 4.93e-05 | 5 | 585 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-172093-F | Transpower Hamilton | Network | HAMCB2742 | 08/05/2024 | 07:35 | 08/05/2024 | 09:04 | 0.14616 | 0.0017439 | 177 | 14835 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2398-E | Wallace | Network | WALCB3 | 13/05/2024 | 09:07 | 13/05/2024 | 13:38 | 0.12816 | 0.0004729 | 48 | 13008 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2403-E | Te Uku | Network | TEUCB11 | 13/05/2024 | 09:21 | 13/05/2024 | 13:34 | 0.0074781 | 2.96e-05 | 3 | 759 | Planned interruptions on the network | Planned | Transformer Upgrade
|  | INCD-2393-E | Finlayson | Network | FINCB2 | 14/05/2024 | 09:10 | 14/05/2024 | 10:46 | 0.0028375 | 2.96e-05 | 3 | 288 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-172399-F | Norton Rd | Network | NORCB3 | 14/05/2024 | 21:00 | 15/05/2024 | 00:45 | 0.0022267 | 9.9e-06 | 1 | 226 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-172435-F | Weavers | Network | WEACB2 | 15/05/2024 | 13:45 | 15/05/2024 | 18:59 | 1.4227 | 0.0050445 | 512 | 144401 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-17586-G | Borman | Network | BORCB3 | 18/05/2024 | 16:58 | 18/05/2024 | 17:14 | 0.013242 | 0.0008276 | 84 | 1344 | Unplanned interruptions on the network | Defective Equipment | Flashovr on cable bush
|  | INCD-2417-E | Glasgow | Network | GLACB2 | 22/05/2024 | 09:04 | 22/05/2024 | 11:55 | 0.043804 | 0.0002562 | 26 | 4446 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-172863-F | Gordonton | Network | CHACB9 | 26/05/2024 | 07:27 | 26/05/2024 | 08:30 | 0.03339 | 0.000532 | 54 | 3389 | Unplanned interruptions on the network | Defective Equipment | Contact problem
|  | INCD-172922-F | Horotiu | Network | HORCB6 | 26/05/2024 | 14:44 | 26/05/2024 | 21:21 | 0.0039016 | 9.9e-06 | 1 | 396 | Unplanned interruptions on the network | Adverse weather | High wind lne break
|  | INCD-2424-E | Finlayson | Network | FINCB3 | 27/05/2024 | 09:03 | 27/05/2024 | 14:26 | 0.019094 | 5.91e-05 | 6 | 1938 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-173091-F | Transpower Hamilton | Network | BORCB2 | 29/05/2024 | 14:31 | 29/05/2024 | 19:03 | 0.55084 | 0.0055076 | 559 | 55909 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (IN Zone)
|  | INCD-173091-F | Transpower Hamilton | Network | CHACB7 | 29/05/2024 | 14:31 | 29/05/2024 | 19:03 | 0.31135 | 0.0033104 | 336 | 31601 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (IN Zone)
|  | INCD-173101-F | Te Uku Wind Farm | Network | RAGCB6 | 29/05/2024 | 14:42 | 30/05/2024 | 21:19 | 16.7714 | 0.009616 | 976 | 1702248.9 | Unplanned interruptions on the network | Lightning | Lightning strike surge
|  | INCD-173108-F | Weavers | Network | NGACB5 | 29/05/2024 | 15:01 | 29/05/2024 | 15:06 | 0.043662 | 0.0095963 | 974 | 4431.54 | Unplanned interruptions on the network | Adverse weather | Wind line clash
|  | INCD-173196-F | Weavers | Network | NGACB2 | 29/05/2024 | 18:16 | 30/05/2024 | 17:45 | 0.0045116 | 4.93e-05 | 5 | 457.91 | Unplanned interruptions on the network | Vegetation | Tree blown ovr on line (OUT of Zone)
|  | INCD-173357-F | Te Kauwhata | Network | TEKCB5 | 30/05/2024 | 06:50 | 30/05/2024 | 23:05 | 0.0096062 | 9.9e-06 | 1 | 975 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-173413-F | Te Uku | Network | TEUCB12 | 31/05/2024 | 11:25 | 31/05/2024 | 17:05 | 0.020099 | 5.91e-05 | 6 | 2040 | Unplanned interruptions on the network | Vegetation | Tree blown ovr on line (OUT of Zone)
|  | INCD-173424-F | Te Uku | Network | TEUCB11 | 31/05/2024 | 14:28 | 31/05/2024 | 14:54 | 0.0002562 | 9.9e-06 | 1 | 26 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-173468-F | Sandwich Rd | Network | SANCB4 | 01/06/2024 | 23:37 | 02/06/2024 | 10:09 | 1.691 | 0.014178 | 1439 | 171630 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-173470-F | Ngaruawahia | Network | NGACB6 | 02/06/2024 | 00:46 | 02/06/2024 | 05:11 | 0.08353 | 0.0003153 | 32 | 8478 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-4602-H | Finlayson | Network | FINCB2 | 06/06/2024 | 09:05 | 06/06/2024 | 12:51 | 0.069027 | 0.0003054 | 31 | 7006 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2466-E | Glasgow | Network | GLACB2 | 12/06/2024 | 09:03 | 12/06/2024 | 10:55 | 0.010858 | 9.85e-05 | 10 | 1102 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-173929-F | Finlayson | Network | FINCB1 | 13/06/2024 | 05:29 | 13/06/2024 | 07:31 | 0.003606 | 2.96e-05 | 3 | 366 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-173932-F | Te Kauwhata | Private | TEKCB5 | 13/06/2024 | 08:36 | 13/06/2024 | 17:00 | 0.0029459 | 9.9e-06 | 1 | 299 | Planned interruptions on the network | Unknown | New Connections
|  | INCD-174026-F | Raglan | Network | RAGCB6 | 16/06/2024 | 05:59 | 16/06/2024 | 06:16 | 0.16782 | 0.0096555 | 980 | 17033.04 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-174028-F | Weavers | Network | WEACB3 | 16/06/2024 | 07:45 | 16/06/2024 | 10:10 | 0.019873 | 0.0001379 | 14 | 2017 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-174042-F | Raglan | Network | RAGCB2 | 16/06/2024 | 23:11 | 17/06/2024 | 05:21 | 0.0006831 | 9.9e-06 | 1 | 69.33 | Unplanned interruptions on the network | Defective Equipment | Burning frm prev flt
|  | INCD-174042-F | Raglan | Network | RAGCB6 | 16/06/2024 | 23:11 | 17/06/2024 | 05:21 | 0.67064 | 0.0096555 | 980 | 68068.29 | Unplanned interruptions on the network | Defective Equipment | Burning frm prev flt
|  | INCD-2473-E | Finlayson | Network | FINCB1 | 17/06/2024 | 09:01 | 17/06/2024 | 10:15 | 0.0043745 | 5.91e-05 | 6 | 444 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2474-E | Chartwell | Network | CHACB9 | 18/06/2024 | 09:41 | 18/06/2024 | 15:46 | 0.057962 | 0.0001675 | 17 | 5883 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-174191-F | Weavers | Network | WEACB4 | 20/06/2024 | 06:26 | 20/06/2024 | 08:57 | 0.017853 | 0.0001182 | 12 | 1812 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-174215-F | Transpower Hamilton | Network | HAMCB2902 | 20/06/2024 | 12:01 | 20/06/2024 | 12:54 | 0.027154 | 0.0005123 | 52 | 2756 | Planned interruptions on the network | Planned | New Connections
|  | INCD-174316-F | Transpower Hamilton | Network | HAMCB2902 | 24/06/2024 | 08:04 | 24/06/2024 | 15:43 | 0.4446 | 0.0016749 | 170 | 45126 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-17611-G | Te Kauwhata | Network | TEKCB2 | 25/06/2024 | 11:30 | 25/06/2024 | 15:24 | 0.0063056 | 2.96e-05 | 3 | 640 | Unplanned interruptions on the network | Defective Equipment | Leaning pole
|  | INCD-17613-G | Glasgow St | Network | GLACB2 | 26/06/2024 | 09:08 | 26/06/2024 | 15:13 | 0.056356 | 0.0001576 | 16 | 5720 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-2477-E | Ngaruawahia | Network | NGACB2 | 27/06/2024 | 09:00 | 27/06/2024 | 14:46 | 0.11558 | 0.0003547 | 36 | 11731 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2521-E | Peacockes | Network | PEACB18 | 02/07/2024 | 09:11 | 02/07/2024 | 14:18 | 0.015124 | 4.93e-05 | 5 | 1535 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2513-E | Glasgow | Network | GLACB2 | 04/07/2024 | 09:49 | 04/07/2024 | 15:59 | 0.059647 | 0.0001675 | 17 | 6054 | Planned interruptions on the network | Planned | New Connections
|  | INCD-174709-F | Finlayson | Network | FINCB1 | 05/07/2024 | 08:46 | 05/07/2024 | 09:05 | 0.023912 | 0.0040986 | 416 | 2427 | Unplanned interruptions on the network | Defective Equipment | Line break at twist joint
|  | INCD-174859-F | Weavers | Network | WEACB3 | 09/07/2024 | 08:52 | 09/07/2024 | 09:44 | 0.0005123 | 9.9e-06 | 1 | 52 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-2541-E | Borman | Network | BORCB3 | 11/07/2024 | 23:33 | 12/07/2024 | 05:05 | 0.31075 | 0.000936 | 95 | 31540 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2543-E | Avalon | Network | AVACB4 | 12/07/2024 | 08:32 | 12/07/2024 | 11:52 | 0.07685 | 0.0003842 | 39 | 7800 | Planned interruptions on the network | Planned | Distribution Transformer Replacement
|  | INCD-2558-E | Chartwell | Network | CHACB9 | 15/07/2024 | 09:11 | 15/07/2024 | 13:10 | 0.072997 | 0.0003054 | 31 | 7409 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-17628-G | Weavers | Network | WEACB2 | 19/07/2024 | 08:53 | 19/07/2024 | 10:29 | 0.0009458 | 9.9e-06 | 1 | 96 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-2655-E | Chartwell | Network | CHACB9 | 22/07/2024 | 14:19 | 22/07/2024 | 14:56 | 0.0036454 | 9.85e-05 | 10 | 370 | Unplanned interruptions on the network | Third_party | Hit by vehicle
|  | INCD-175465-F | Hoeka | Private | HOECB2 | 22/07/2024 | 23:59 | 23/07/2024 | 00:01 | 0.0009458 | 0.0007882 | 80 | 96 | Unplanned interruptions on the network | Third_party | Temp Disconnect / safety isolation
|  | INCD-2563-E | Chartwell | Network | CHACB9 | 23/07/2024 | 09:03 | 23/07/2024 | 14:42 | 0.12107 | 0.0003645 | 37 | 12288 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2575-E | Te Uku | Network | TEUCB11 | 23/07/2024 | 09:12 | 23/07/2024 | 13:45 | 0.067243 | 0.0002463 | 25 | 6825 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-175554-F | Chartwell | Network | CHACB10 | 25/07/2024 | 22:04 | 26/07/2024 | 04:43 | 0.011784 | 2.96e-05 | 3 | 1196 | Unplanned interruptions on the network | Third_party | Cable hit by digger
|  | INCD-175578-F | Raglan | Network | RAGCB5 | 27/07/2024 | 08:08 | 27/07/2024 | 14:11 | 0.39852 | 0.0011133 | 113 | 40449 | Unplanned interruptions on the network | Defective Equipment | Connect/jumper loose
|  | INCD-175674-F | Weavers | Network | WEACB2 | 31/07/2024 | 12:13 | 31/07/2024 | 12:27 | 0.0001379 | 9.9e-06 | 1 | 14 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-2643-E | Gordonton | Network | GORCB11 | 01/08/2024 | 09:12 | 01/08/2024 | 11:51 | 0.010966 | 6.9e-05 | 7 | 1113 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2483-E | Pukete | Network | PUKCB5 | 01/08/2024 | 23:32 | 02/08/2024 | 06:30 | 0.0041183 | 9.9e-06 | 1 | 418 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2601-E | Chartwell | Network | CHACB12 | 02/08/2024 | 09:20 | 02/08/2024 | 14:48 | 0.40072 | 0.0012217 | 124 | 40672 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-175861-F | Te Kauwhata | Network | TEKCB3 | 05/08/2024 | 07:15 | 05/08/2024 | 09:25 | 0.030622 | 0.0002365 | 24 | 3108 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2598-E | Pukete | Network | PUKCB5 | 09/08/2024 | 08:02 | 09/08/2024 | 15:43 | 0.31689 | 0.0013991 | 142 | 32163 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-176139-F | Weavers | Network | WEACB2 | 10/08/2024 | 06:32 | 10/08/2024 | 12:28 | 0.29582 | 0.0091431 | 928 | 30025 | Unplanned interruptions on the network | Defective Equipment | faulty line connection
|  | INCD-176259-F | Transpower Hamilton | Network | HAMCB2742 | 13/08/2024 | 14:26 | 13/08/2024 | 14:47 | 0.12497 | 0.0059509 | 604 | 12684 | Unplanned interruptions on the network | Human error | Settings Incorrect
|  | INCD-176304-F | Weavers | Network | WEACB6 | 14/08/2024 | 09:04 | 14/08/2024 | 19:23 | 0.047716 | 0.000335 | 34 | 4843 | Unplanned interruptions on the network | Defective Equipment | Faulty joint/connection
|  | INCD-2675-E | Glasgow | Network | GLACB2 | 14/08/2024 | 14:00 | 14/08/2024 | 15:12 | 0.0042563 | 5.91e-05 | 6 | 432 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-176546-F | Gordonton | Network | GORCB13 | 15/08/2024 | 19:14 | 15/08/2024 | 21:07 | 0.0011133 | 9.9e-06 | 1 | 113 | Unplanned interruptions on the network | Defective Equipment | Loss or failure of oil
|  | INCD-176439-F | Whatawhata | Network | WHACB5 | 17/08/2024 | 14:18 | 17/08/2024 | 23:09 | 0.49649 | 0.0038425 | 390 | 50392 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-176497-F | Whatawhata | Network | RAGCB6 | 19/08/2024 | 02:55 | 19/08/2024 | 03:13 | 0.15867 | 0.0097244 | 987 | 16104.43 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-176533-F | Whatawhata | Network | RAGCB4 | 19/08/2024 | 06:57 | 19/08/2024 | 16:19 | 3.0331 | 0.0065027 | 660 | 307850 | Unplanned interruptions on the network | Defective Equipment | Cable termination fails
|  | INCD-176533-F | Whatawhata | Network | RAGCB5 | 19/08/2024 | 06:57 | 19/08/2024 | 16:19 | 0.7131 | 0.0015271 | 155 | 72378 | Unplanned interruptions on the network | Defective Equipment | Cable termination fails
|  | INCD-176601-F | Te Uku | Network | TEUCB11 | 19/08/2024 | 15:31 | 20/08/2024 | 10:42 | 0.30132 | 0.0013005 | 132 | 30583 | Unplanned interruptions on the network | Defective Equipment | Broken binder
|  | INCD-176597-F | Whatawhata | Network | WHACB2 | 19/08/2024 | 15:42 | 19/08/2024 | 17:36 | 0.51073 | 0.004611 | 468 | 51838 | Unplanned interruptions on the network | Defective Equipment | Faulty joint/connection
|  | INCD-17647-G | Te Kauwhata | Network | TEKCB5 | 19/08/2024 | 12:28 | 19/08/2024 | 16:29 | 0.0023745 | 9.9e-06 | 1 | 241 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-176655-F | Horotiu | Network | HORCB5 | 20/08/2024 | 06:46 | 20/08/2024 | 09:38 | 0.0016946 | 9.9e-06 | 1 | 172 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-176664-F | Borman Rd | Network | BORCB5 | 20/08/2024 | 09:33 | 20/08/2024 | 14:30 | 0.019932 | 6.9e-05 | 7 | 2023 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-176696-F | Horotiu | Network | HORCB6 | 20/08/2024 | 14:47 | 20/08/2024 | 15:32 | 0.0066504 | 0.0001478 | 15 | 675 | Unplanned interruptions on the network | Defective Equipment | Internal short
|  | INCD-176728-F | Claudelands | Network | CLACB16 | 21/08/2024 | 08:33 | 21/08/2024 | 17:18 | 0.26713 | 0.0007783 | 79 | 27113 | Unplanned interruptions on the network | Defective Equipment | Intnl insulation failure
|  | INCD-176904-F | Hoeka | Network | HOECB4 | 23/08/2024 | 22:58 | 24/08/2024 | 02:45 | 0.035784 | 0.0001576 | 16 | 3632 | Unplanned interruptions on the network | Defective Equipment | Faulty joint/connection
|  | INCD-2714-E | Finlayson | Network | FINCB2 | 26/08/2024 | 09:03 | 26/08/2024 | 13:09 | 0.095234 | 0.0003941 | 40 | 9666 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2653-E | Hampton Downs | Network | HPTCB5 | 27/08/2024 | 09:19 | 27/08/2024 | 12:25 | 0.0073303 | 3.94e-05 | 4 | 744 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-177083-F | Raglan | Network | RAGCB6 | 29/08/2024 | 11:29 | 30/08/2024 | 09:13 | 0.34134 | 0.0040001 | 406 | 34645 | Unplanned interruptions on the network | Defective Equipment | Faulty joint/connection
|  | INCD-177146-F | Te Kauwhata | Network | TEKCB5 | 30/08/2024 | 11:31 | 30/08/2024 | 11:55 | 0.0026011 | 0.0001084 | 11 | 264 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-177193-F | Hoeka | Network | HOECB4 | 31/08/2024 | 22:01 | 01/09/2024 | 01:24 | 0.0040001 | 1.97e-05 | 2 | 406 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-177221-F | Transpower Hamilton | Network | HAMCB2802 | 01/09/2024 | 05:38 | 01/09/2024 | 14:00 | 0.004946 | 9.9e-06 | 1 | 502 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-177452-F | Whitiora School | Network | WHICB7 | 05/09/2024 | 10:37 | 05/09/2024 | 11:34 | 0.0005517 | 9.9e-06 | 1 | 56 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-177466-F | Whatawhata | Network | WHACB4 | 06/09/2024 | 14:28 | 06/09/2024 | 21:44 | 0.021479 | 4.93e-05 | 5 | 2180 | Unplanned interruptions on the network | Vegetation | Tree blown ovr on line (OUT of Zone)
|  | INCD-177497-F | Hampton Downs | Network | HPTCB5 | 08/09/2024 | 11:56 | 08/09/2024 | 16:31 | 0.089215 | 0.0006109 | 62 | 9055 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2650-E | Cobham | Network | COBCB11 | 08/09/2024 | 21:03 | 08/09/2024 | 22:40 | 0.034405 | 0.0003547 | 36 | 3492 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-2607-E | Whatawhata | Network | WHACB5 | 10/09/2024 | 09:30 | 10/09/2024 | 14:22 | 0.29369 | 0.0011133 | 113 | 29809 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-177882-F | Chartwell | Network | CHACB9 | 20/09/2024 | 05:37 | 20/09/2024 | 06:41 | 0.0037834 | 5.91e-05 | 6 | 384 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-177912-F | Whatawhata | Network | WHACB2 | 20/09/2024 | 09:23 | 20/09/2024 | 17:32 | 0.0093993 | 3.94e-05 | 4 | 954 | Unplanned interruptions on the network | Defective Equipment | Intnl insulation failure
|  | INCD-177936-F | Kent St | Network | KENCB2 | 20/09/2024 | 22:40 | 21/09/2024 | 00:26 | 0.0010444 | 9.9e-06 | 1 | 106 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-178113-F | Weavers | Network | WEACB3 | 25/09/2024 | 14:56 | 25/09/2024 | 15:29 | 0.0003251 | 9.9e-06 | 1 | 33 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-178121-F | Te Uku | Network | TEUCB11 | 26/09/2024 | 08:30 | 26/09/2024 | 13:12 | 0.2809 | 0.0010739 | 109 | 28510 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2768-E | Horotiu | Network | HORCB5 | 30/09/2024 | 09:02 | 30/09/2024 | 13:14 | 0.26653 | 0.0011232 | 114 | 27052 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-17660-G | Peacockes | Network | PEACB13 | 06/10/2024 | 16:35 | 06/10/2024 | 16:52 | 0.021607 | 0.001271 | 129 | 2193 | Planned interruptions on the network | Planned | 11kV Fuse Replacement
|  | INCD-178530-F | Whatawhata | Network | WHACB5 | 08/10/2024 | 10:22 | 08/10/2024 | 12:16 | 0.0044927 | 3.94e-05 | 4 | 456 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-2806-E | Ngaruawahia | Network | NGACB2 | 09/10/2024 | 09:47 | 09/10/2024 | 15:12 | 0.37296 | 0.0011823 | 120 | 37854 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2801-E | Whatawhata | Network | WHACB5 | 10/10/2024 | 09:03 | 10/10/2024 | 14:48 | 0.10089 | 0.0002956 | 30 | 10240 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-178725-F | Chartwell | Network | CHACB13 | 11/10/2024 | 04:11 | 11/10/2024 | 05:57 | 0.0031331 | 2.96e-05 | 3 | 318 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-178694-F | Peacockes Rd | Network | PEACB18 | 13/10/2024 | 15:04 | 14/10/2024 | 00:38 | 0.27775 | 0.0010247 | 104 | 28191 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-17665-G | Hampton Downs | Private | HPTCB5 | 14/10/2024 | 17:12 | 14/10/2024 | 17:46 | 0.0013399 | 3.94e-05 | 4 | 136 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-178795-F | Whatawhata | Network | WHACB4 | 15/10/2024 | 11:00 | 15/10/2024 | 11:06 | 0.0002365 | 3.94e-05 | 4 | 24 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2826-E | Peacockes | Network | PEACB12 | 16/10/2024 | 08:34 | 16/10/2024 | 10:53 | 0.16249 | 0.0012217 | 124 | 16492 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2838-E | Peacockes | Network | PEACB12 | 18/10/2024 | 09:33 | 18/10/2024 | 15:26 | 0.072091 | 0.0002069 | 21 | 7317 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-178972-F | Latham Court | Network | LATCB5 | 21/10/2024 | 09:02 | 21/10/2024 | 12:29 | 0.17743 | 0.0008572 | 87 | 18009 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-179026-F | Weavers | Network | WEACB2 | 22/10/2024 | 07:30 | 22/10/2024 | 10:15 | 0.0016257 | 9.9e-06 | 1 | 165 | Unplanned interruptions on the network | Wildlife | Bird betw line & pole
|  | INCD-179139-F | Weavers | Network | WEACB2 | 25/10/2024 | 12:21 | 25/10/2024 | 15:34 | 0.0095077 | 4.93e-05 | 5 | 965 | Unplanned interruptions on the network | Defective Equipment | Intnl insulation failure
|  | INCD-179165-F | Weavers | Network | NGACB3 | 26/10/2024 | 23:59 | 27/10/2024 | 00:35 | 0.10641 | 0.0051529 | 523 | 10800 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-179252-F | Whatawhata | Network | HORCB5 | 28/10/2024 | 06:00 | 28/10/2024 | 07:22 | 0.031558 | 0.0003842 | 39 | 3203 | Unplanned interruptions on the network | Defective Equipment | Jumpers come off
|  | INCD-179249-F | Horotiu | Network | HORCB5 | 28/10/2024 | 06:00 | 28/10/2024 | 07:52 | 0.093156 | 0.0008375 | 85 | 9455 | Unplanned interruptions on the network | Defective Equipment | Jumpers come off
|  | INCD-2846-E | Horotiu | Network | HORCB3 | 29/10/2024 | 09:38 | 29/10/2024 | 15:05 | 0.016109 | 4.93e-05 | 5 | 1635 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2878-E | Gordonton | Network | GORCB11 | 30/10/2024 | 09:08 | 30/10/2024 | 13:40 | 0.12335 | 0.0004631 | 47 | 12520 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-17668-G | Wallace Rd | Network | WALCB2 | 30/10/2024 | 09:14 | 30/10/2024 | 13:47 | 0.27973 | 0.0010247 | 104 | 28392 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-179317-F | Silverdale | Network | SILCB2 | 30/10/2024 | 16:11 | 30/10/2024 | 16:38 | 0.30039 | 0.011468 | 1164 | 30489 | Unplanned interruptions on the network | Adverse weather | Wind debris on line (IN Zone)
|  | INCD-179329-F | Avalon | Network | AVACB8 | 31/10/2024 | 09:30 | 31/10/2024 | 15:09 | 0.22352 | 0.00067 | 68 | 22687 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-179359-F | Weavers | Network | WEACB5 | 31/10/2024 | 15:09 | 31/10/2024 | 17:50 | 0.0015863 | 9.9e-06 | 1 | 161 | Unplanned interruptions on the network | Wildlife | Bird betw line & pole
|  | INCD-2876-E | Pukete | Network | PUKCB10 | 01/11/2024 | 09:14 | 01/11/2024 | 15:10 | 0.11208 | 0.0003153 | 32 | 11376 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-179399-F | Foreman Rd | Network | FORCB3 | 02/11/2024 | 08:07 | 02/11/2024 | 21:06 | 0.0076751 | 9.9e-06 | 1 | 779 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-179413-F | Pukete | Network | PUKCB5 | 03/11/2024 | 15:58 | 03/11/2024 | 18:23 | 0.062859 | 0.0004335 | 44 | 6380 | Unplanned interruptions on the network | Third_party | Pillar Hit by vehicle
|  | INCD-179489-F | Peacockes Rd | Network | PEACB12 | 04/11/2024 | 08:56 | 04/11/2024 | 09:28 | 0.068554 | 0.0022365 | 227 | 6958 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-179516-F | Avalon | Network | AVACB8 | 06/11/2024 | 09:30 | 06/11/2024 | 13:34 | 0.16158 | 0.0006798 | 69 | 16400 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-179711-F | Whatawhata | Network | WHACB2 | 13/11/2024 | 01:02 | 13/11/2024 | 07:37 | 0.47194 | 0.0082071 | 833 | 47900 | Unplanned interruptions on the network | Wildlife | Bird lne clash/break
|  | INCD-2891-E | Te Uku | Network | TEUCB12 | 13/11/2024 | 10:07 | 13/11/2024 | 13:54 | 0.13993 | 0.0006503 | 66 | 14202 | Planned interruptions on the network | Planned | Pole Replacement
|  | INCD-179827-F | Te Uku | Network | TEUCB11 | 16/11/2024 | 02:46 | 16/11/2024 | 10:39 | 0.17122 | 0.0024927 | 253 | 17378 | Unplanned interruptions on the network | Defective Equipment | faulty line connection
|  | INCD-179837-F | Avalon | Network | AVACB3 | 16/11/2024 | 15:20 | 16/11/2024 | 16:06 | 0.070721 | 0.0016257 | 165 | 7178 | Unplanned interruptions on the network | Third_party | Cable hit by digger
|  | INCD-2882-E | Borman | Network | BORCB2 | 19/11/2024 | 09:32 | 19/11/2024 | 14:20 | 0.048238 | 0.0001675 | 17 | 4896 | Planned interruptions on the network | Planned | Conductor Replacement
|  | INCD-17675-G | Te Uku | Network | TEUCB2 | 20/11/2024 | 08:32 | 20/11/2024 | 15:54 | 0.016355 | 3.94e-05 | 4 | 1660 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-180106-F | Tasman | Network | TASCB2 | 25/11/2024 | 20:02 | 25/11/2024 | 21:05 | 0.0012414 | 1.97e-05 | 2 | 126 | Unplanned interruptions on the network | Defective Equipment | Insecure termination
|  | INCD-180108-F | Rural Bank | Network | RURCB1 | 25/11/2024 | 21:19 | 25/11/2024 | 22:31 | 0.025538 | 0.0003547 | 36 | 2592 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-180225-F | Rural Bank | Network | RURCB1 | 28/11/2024 | 21:07 | 29/11/2024 | 03:01 | 0.09017 | 0.0002562 | 26 | 9152 | Planned interruptions on the network | Planned | Distribution Transformer Replacement
|  | INCD-2830-E | Finlayson | Network | FINCB2 | 01/12/2024 | 08:01 | 01/12/2024 | 14:34 | 0.030829 | 7.88e-05 | 8 | 3129 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2935-E | Te Uku | Network | TEUCB11 | 03/12/2024 | 08:36 | 03/12/2024 | 12:45 | 0.031597 | 0.0001281 | 13 | 3207 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-2945-E | Weavers | Network | WEACB4 | 04/12/2024 | 09:09 | 04/12/2024 | 14:54 | 0.03739 | 0.0001084 | 11 | 3795 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-17695-G | Weavers | Network | WEACB4 | 10/12/2024 | 03:56 | 10/12/2024 | 05:15 | 0.0085618 | 0.0001084 | 11 | 869 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-2956-E | Peacockes | Network | PEACB12 | 10/12/2024 | 08:31 | 10/12/2024 | 10:11 | 0.073214 | 0.0008178 | 83 | 7431 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-2971-E | Chartwell | Network | CHACB9 | 15/12/2024 | 00:00 | 15/12/2024 | 00:01 | 0.0013301 | 0.0022365 | 227 | 135 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-180692-F | Weavers | Network | WEACB4 | 16/12/2024 | 04:36 | 16/12/2024 | 05:59 | 0.031893 | 0.0003842 | 39 | 3237 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2955-E | Hampton Downs | Network | HPTCB5 | 19/12/2024 | 09:18 | 19/12/2024 | 12:28 | 0.013104 | 6.9e-05 | 7 | 1330 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-2961-E | Latham | Network | LATCB1 | 19/12/2024 | 22:08 | 20/12/2024 | 04:44 | 0.031213 | 7.88e-05 | 8 | 3168 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-17706-G | Gordonton | Network | GORCB12 | 23/12/2024 | 08:04 | 23/12/2024 | 14:14 | 0.029163 | 7.88e-05 | 8 | 2960 | Unplanned interruptions on the network | Lightning | Lightning damage
|  | INCD-180983-F | Te Uku | Network | TEUCB11 | 26/12/2024 | 07:16 | 26/12/2024 | 11:07 | 0.055144 | 0.0017833 | 181 | 5597 | Unplanned interruptions on the network | Defective Equipment | Corros causes lne brk
|  | INCD-181094-F | Wallace Rd | Network | WALCB6 | 01/01/2025 | 22:38 | 02/01/2025 | 00:09 | 0.0008966 | 9.9e-06 | 1 | 91 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-181095-F | Weavers | Network | FINCB4 | 02/01/2025 | 03:59 | 02/01/2025 | 04:00 | 4.33e-05 | 3.95e-05 | 4 | 4.4 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-181167-F | Weavers | Network | WEACB3 | 06/01/2025 | 09:46 | 06/01/2025 | 12:57 | 0.0018818 | 9.9e-06 | 1 | 191 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-181177-F | Chartwell | Network | CHACB9 | 06/01/2025 | 21:00 | 07/01/2025 | 12:46 | 0.009616 | 2.96e-05 | 3 | 976 | Unplanned interruptions on the network | Defective Equipment | Split crossarm
|  | INCD-181236-F | Weavers | Network | WEACB6 | 08/01/2025 | 14:15 | 08/01/2025 | 16:51 | 0.072485 | 0.0012316 | 125 | 7357 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-2991-E | Gordonton | Network | GORCB13 | 13/01/2025 | 08:16 | 13/01/2025 | 13:52 | 0.078584 | 0.0011035 | 112 | 7976 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-17717-G | Te Uku | Network | TEUCB12 | 13/01/2025 | 05:56 | 13/01/2025 | 08:52 | 0.0069362 | 3.94e-05 | 4 | 704 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-17719-G | Pukete | Network | PUKCB4 | 13/01/2025 | 17:04 | 13/01/2025 | 20:39 | 0.038129 | 0.0001773 | 18 | 3870 | Unplanned interruptions on the network | Defective Equipment | Loss or failure of oil
|  | INCD-3016-E | Chartwell | Network | CHACB9 | 14/01/2025 | 09:05 | 14/01/2025 | 11:12 | 0.0025025 | 1.97e-05 | 2 | 254 | Planned interruptions on the network | Planned | Crossarm Replacement
|  | INCD-17720-G | Weavers | Private | WEACB2 | 14/01/2025 | 09:44 | 14/01/2025 | 10:10 | 0.0002562 | 9.9e-06 | 1 | 26 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-181444-F | Chartwell | Network | CHACB7 | 15/01/2025 | 09:03 | 15/01/2025 | 12:21 | 0.56573 | 0.0028572 | 290 | 57420 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-3013-E | Hoeka | Network | HOECB1 | 17/01/2025 | 10:30 | 17/01/2025 | 13:19 | 0.029794 | 0.0001773 | 18 | 3024 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-181565-F | Wallace Rd | Network | WALCB6 | 18/01/2025 | 05:46 | 18/01/2025 | 07:50 | 0.0012217 | 9.9e-06 | 1 | 124 | Unplanned interruptions on the network | Wildlife | Foreign Objt obstruct /Animal contact
|  | INCD-181598-F | Ngaruawahia | Network | NGACB2 | 20/01/2025 | 03:19 | 20/01/2025 | 05:28 | 0.036858 | 0.0002857 | 29 | 3741 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-17726-G | Te Uku | Network | TEUCB11 | 22/01/2025 | 09:45 | 22/01/2025 | 12:29 | 0.011311 | 6.9e-05 | 7 | 1148 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-181701-F | Pukete | Network | PUKCB4 | 22/01/2025 | 15:12 | 22/01/2025 | 15:53 | 0.0044435 | 0.0001084 | 11 | 451 | Planned interruptions on the network | Unknown | OTHER Maintenance
|  | INCD-17729-G | Gordonton | Network | GORCB12 | 29/01/2025 | 17:03 | 29/01/2025 | 20:06 | 0.001803 | 9.9e-06 | 1 | 183 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-182182-F | Peachgrove Rd | Network | PCHCB1 | 30/01/2025 | 15:09 | 30/01/2025 | 15:53 | 0.062426 | 0.0014188 | 144 | 6336 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-182183-F | Chartwell | Network | CHACB15 | 04/02/2025 | 15:08 | 04/02/2025 | 16:13 | 0.058278 | 0.0008966 | 91 | 5915 | Planned interruptions on the network | Planned | RMU Replacement
|  | INCD-3026-E | Te Uku | Network | TEUCB13 | 05/02/2025 | 09:10 | 05/02/2025 | 13:40 | 0.071825 | 0.000266 | 27 | 7290 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-182412-F | Chartwell | Network | CHACB5 | 13/02/2025 | 14:34 | 13/02/2025 | 15:28 | 0.0074485 | 0.0001379 | 14 | 756 | Unplanned interruptions on the network | Defective Equipment | Cable joint fails
|  | INCD-182481-F | Gordonton | Network | GORCB13 | 16/02/2025 | 08:22 | 16/02/2025 | 15:01 | 0.011794 | 2.96e-05 | 3 | 1197 | Unplanned interruptions on the network | Defective Equipment | Rotten crossarm
|  | INCD-182649-F | Wallace Rd | Network | WALCB4 | 19/02/2025 | 23:01 | 20/02/2025 | 00:57 | 0.0011429 | 9.9e-06 | 1 | 116 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-182676-F | Finlayson | Network | FINCB2 | 20/02/2025 | 09:32 | 20/02/2025 | 12:04 | 0.0044927 | 2.96e-05 | 3 | 456 | Unplanned interruptions on the network | Unknown | All Ok - Fault cause not established
|  | INCD-182692-F | Whatawhata | Private | WHACB4 | 20/02/2025 | 16:42 | 20/02/2025 | 16:55 | 0.0006404 | 4.93e-05 | 5 | 65 | Unplanned interruptions on the network | Defective Equipment | LVC - WEL & Customer
|  | INCD-183076-F | Te Kauwhata | Network | TEKCB5 | 05/03/2025 | 04:10 | 05/03/2025 | 05:00 | 0.031597 | 0.0015764 | 160 | 3207 | Unplanned interruptions on the network | Unknown | Fire Risk Mitigation Patrol - Sucessfully reclosed
|  | INCD-183145-F | Transpower Hamilton | Network | HAMCB2722 | 06/03/2025 | 16:06 | 06/03/2025 | 16:33 | 0.020483 | 0.0007586 | 77 | 2079 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-25-K | Whatawhata | Network | WALCB6 | 07/03/2025 | 10:54 | 10/03/2025 | 04:25 | 8.89e-05 | 9.9e-06 | 1 | 9.02 | Unplanned interruptions on the network | Unknown | Fire Risk Mitigation Patrol - Sucessfully reclosed
|  | INCD-3072-E | Glasgow | Network | GLACB6 | 08/03/2025 | 08:40 | 08/03/2025 | 12:22 | 0.0043745 | 1.97e-05 | 2 | 444 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-18-K | Peacockes Rd | Network | PEACB12 | 09/03/2025 | 09:07 | 09/03/2025 | 14:21 | 0.37986 | 0.0066307 | 673 | 38555 | Unplanned interruptions on the network | Defective Equipment | Contact problem
|  | INCD-62-K | Te Kauwhata | Network | TEKCB3 | 11/03/2025 | 02:18 | 11/03/2025 | 03:42 | 0.23153 | 0.0027784 | 282 | 23500 | Unplanned interruptions on the network | Unknown | Fire Risk Mitigation Patrol - Sucessfully reclosed
|  | INCD-145-K | Hoeka | Network | HOECB6 | 12/03/2025 | 23:59 | 13/03/2025 | 00:01 | 0.013114 | 0.0058721 | 596 | 1330.98 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-204-K | Peacockes | Network | PEACB12 | 14/03/2025 | 11:04 | 14/03/2025 | 18:23 | 0.097264 | 0.0002266 | 23 | 9872 | Unplanned interruptions on the network | Third_party | Car in contact with pole
|  | INCD-291-K | Horotiu | Private | HORCB6 | 18/03/2025 | 09:40 | 18/03/2025 | 14:49 | 0.0030444 | 9.9e-06 | 1 | 309 | Unplanned interruptions on the network | Third_party | Temp Disconnect / safety isolation
|  | INCD-317-K | Sandwich Rd | Network | SANCB5 | 18/03/2025 | 14:46 | 18/03/2025 | 14:51 | 0.0079017 | 0.001872 | 190 | 802 | Planned interruptions on the network | Planned | ABS Replacement
|  | INCD-3091-E | Peacockes | Network | PEACB12 | 19/03/2025 | 09:14 | 19/03/2025 | 12:03 | 0.0066603 | 3.94e-05 | 4 | 676 | Planned interruptions on the network | Planned | Transformer Upgrade
|  | INCD-3108-E | Weavers | Network | WEACB5 | 27/03/2025 | 10:05 | 27/03/2025 | 15:12 | 0.16728 | 0.0005912 | 60 | 16978 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-632-K | Silverdale | Network | SILCB2 | 27/03/2025 | 11:32 | 27/03/2025 | 12:39 | 0.57946 | 0.011508 | 1168 | 58813 | Unplanned interruptions on the network | Unknown | Fire Risk Mitigation Patrol - Sucessfully reclosed
|  | INCD-10-M | Claudelands | Network | CLACB3 | 28/03/2025 | 08:38 | 28/03/2025 | 12:34 | 0.14416 | 0.0006109 | 62 | 14632 | Planned interruptions on the network | Planned | Mixed Asset Replacement
|  | INCD-3094-E | Wallace | Network | WALCB6 | 28/03/2025 | 09:15 | 28/03/2025 | 12:18 | 0.003606 | 1.97e-05 | 2 | 366 | Planned interruptions on the network | Planned | OTHER Maintenance
|  | INCD-182856-F | Gordonton | Network | GORCB13 | 31/03/2025 | 09:04 | 31/03/2025 | 11:38 | 0.0091037 | 5.91e-05 | 6 | 924 | Planned interruptions on the network | Planned | OTHER Maintenance
25
26
27 |  | ¹ Extend table as necessary to disclose information for all individual interruptions