## CoverSheet
EDB Information Disclosure Requirements
Information Templates
Schedule 10a
| Company Name | WEL Networks Ltd
| Disclosure Date | 2026-08-31
| Disclosure Year (year ended) | 2026-03-31
Template for Schedule 10a
Prepared 2 June 2026.

## TOC
Table of Contents
Schedule | Schedule name
10a | REPORT ON INTERRUPTIONS

## Instructions
Disclosure Template Instructions
This document forms Schedule 10a to the Electricity Distribution Information Disclosure (Non-material) Amendment Determination 2026 [2026] NZCC 21.
The Schedules take the form of templates for use by EDBs when making disclosures under subclause 2.5.1 of the Electricity Distribution Information Disclosure Determination 2012, as amended.
Company Name and Dates
To prepare the templates for disclosure, the supplier's company name should be entered in cell C8, the date of the last day of the current (disclosure) year should be entered in cell C12, and the date on which the information is disclosed should be entered in cell C10 of the CoverSheet worksheet.
The cell C12 entry (current year) is used to calculate disclosure years in the column headings that show above some of the tables and in labels adjacent to some entry cells. It is also used to calculate the ‘For year ended’ date in the template title blocks (the title blocks are the light green shaded areas at the top of each template). The cell C8 entry (company name) is used in the template title blocks. Dates should be entered in day/month/year order (Example -"1 April 2023").
Data Entry Cells and Calculated Cells
Data entered into this workbook may be entered only into the data entry cells. Data entry cells are the bordered, unshaded areas (white cells) in each template. Under no circumstances should data be entered into the workbook outside a data entry cell.
In some cases, where the information for disclosure is able to be ascertained from disclosures elsewhere in the workbook, such information is disclosed in a calculated cell.
Validation Settings on Data Entry Cells
To maintain a consistency of format and to help guard against errors in data entry, some data entry cells test keyboard entries for validity and accept only a limited range of values. For example, entries may be limited to a list of category names, to values between 0% and 100%, or either a numeric entry or the text entry “N/A”. Where this occurs, a validation message will appear when data is being entered. These checks are applied to keyboard entries only and not, for example, to entries made using Excel’s copy and paste facility.
Inserting Additional Rows and Columns
The schedule 10a template may require additional rows to be inserted in tables marked 'include additional rows if needed' or similar. Column A schedule references should not be entered in additional rows, and should be deleted from additional rows that are created by copying and pasting rows that have schedule references.
Additional rows in the schedule 10a template must not be inserted directly above the first row or below the last row of a table. This is to ensure that entries made in the new row are included in the totals.
Description of Calculation References
Calculation cell formulas contain links to other cells within the same template or elsewhere in the workbook. Key cell references are described in a column to the right of each template. These descriptions are provided to assist data entry. Cell references refer to the row of the template and not the schedule reference.

## S10a.Interruptions
[15 empty] | Company Name | WEL Networks Ltd
[15 empty] | For Year Ended | 2026-03-31
SCHEDULE 10a: REPORT ON INTERRUPTIONS
This schedule requires raw interruption data for the disclosure year. SAIDI and SAIFI is to be recorded using the multi-count approach.Where multiple feeders are affected, the interruption record is to be split into multiple interruptions, ie, one interruption record per feeder. This information is part of audited disclosure information (as defined in section 1.4 of this ID determination), and so is subject to the assurance report required by section 2.8.
sch ref
10a(i): Raw interruption data
|  | Interruption identifier | Circuit location | Sub-network (where applicable) | Feeder(s) affected by interruption | Start date (dd/mm/yyyy) | Start time (hh:mm:ss) | End date (dd/mm/yyyy) | End time (hh:mm:ss) | SAIDI value | SAIFI value | Number of ICPs interrupted | ICP interruption minutes | Planned or unplanned interruption (Class B or C) | Cause | Any explanation to help clarify the context of the interruption, including what the cause is if recorded as 'Other cause'
1 |  | INCD-4065-K | Alexandra St | Network | ALECB15 | 01/07/2025 | 12:31 | 01/07/2025 | 13:58 | 0.0203 | 0.002 | 203 | 2084 | Unplanned | Third_party | Cable hit by digger
2 |  | INCD-10698-K | Alexandra St | Private | ALECB15 | 16/01/2026 | 06:46 | 16/01/2026 | 12:52 | 0.0036 | 0 | 1 | 366 | Unplanned | Third_party | Temp Disconnect / safety isolation
3 |  | INCD-12619-K | Avalon Dr | Network | AVACB1 | 18/03/2026 | 14:04 | 18/03/2026 | 14:45 | 0.0296 | 0.0007 | 74 | 3034 | Planned | Planned | New Connections
4 |  | INCD-2353-L | Avalon | Network | AVACB1 | 24/03/2026 | 14:10 | 24/03/2026 | 14:40 | 0.0205 | 0.0007 | 70 | 2100 | Planned | Planned | New Connections
5 |  | INCD-78-L | Avalon Dr | Private | AVACB1 | 04/06/2025 | 12:47 | 04/06/2025 | 12:47 | 0.0089 | 0.0003 | 34 | 918 | Unplanned | Defective Equipment | LVC - WEL & Customer
6 |  | INCD-12434-K | Avalon Dr | Network | AVACB1 | 16/03/2026 | 05:08 | 16/03/2026 | 05:49 | 0.0611 | 0.0015 | 153 | 6273 | Planned | Planned | RMU Replacement
7 |  | INCD-351-M | Avalon | Network | AVACB1 | 07/10/2025 | 09:49 | 07/10/2025 | 15:22 | 0.003 | 0 | 1 | 303 | Planned | Planned | Recloser & Sectionaliser replacement
8 |  | INCD-12608-K | Avalon Dr | Network | AVACB1 | 23/03/2026 | 05:06 | 23/03/2026 | 05:32 | 0.0177 | 0.0007 | 70 | 1820 | Planned | Planned | RMU Replacement
9 |  | INCD-6584-K | Avalon Dr | Network | AVACB1 | 02/09/2025 | 20:38 | 02/09/2025 | 21:09 | 0.1249 | 0.004 | 414 | 12820 | Unplanned | Third_party | Car in contact with pole
10 |  | INCD-3049-K | Avalon Dr | Network | AVACB1 | 29/05/2025 | 19:21 | 30/05/2025 | 03:18 | 0.4569 | 0.001 | 99 | 46900 | Unplanned | Adverse weather | High wind lne break
11 |  | INCD-3956-K | Avalon Dr | Network | AVACB1 | 26/06/2025 | 23:55 | 27/06/2025 | 06:15 | 0.0008 | 0 | 1 | 85 | Unplanned | Third_party | Car in contact with pole
12 |  | INCD-9812-K | Wallace Rd | Network | AVACB1 | 17/12/2025 | 09:30 | 17/12/2025 | 11:12 | 0.0001 | 0 | 2 | 10 | Planned | Planned | OTHER Maintenance
13 |  | INCD-12700-K | Avalon Dr | Network | AVACB1 | 27/03/2026 | 05:07 | 27/03/2026 | 05:15 | 0.009 | 0.0011 | 115 | 920 | Planned | Unknown | Mixed Asset Replacement
14 |  | INCD-12871-K | Avalon Dr | Network | AVACB1 | 27/03/2026 | 15:06 | 27/03/2026 | 15:21 | 0.0168 | 0.0011 | 115 | 1725 | Planned | Planned | Mixed Asset Replacement
15 |  | INCD-2260-L | Avalon | Network | AVACB1 | 20/03/2026 | 14:02 | 20/03/2026 | 14:30 | 0.0216 | 0.0008 | 79 | 2212 | Planned | Planned | New Connections
16 |  | INCD-142-M | Avalon | Network | AVACB3 | 04/07/2025 | 10:05 | 04/07/2025 | 14:55 | 0.7901 | 0.0028 | 292 | 81098 | Planned | Planned | ABS Replacement
17 |  | INCD-319-M | Avalon | Network | AVACB3 | 26/09/2025 | 10:23 | 26/09/2025 | 11:45 | 0.2325 | 0.0028 | 291 | 23862 | Planned | Planned | OTHER Maintenance
18 |  | INCD-12799-K | Avalon Dr | Network | AVACB3 | 30/03/2026 | 20:42 | 31/03/2026 | 17:51 | 0.6721 | 0.0033 | 339 | 68991 | Unplanned | Third_party | Hit by car
19 |  | INCD-95-M | Avalon | Network | AVACB3 | 19/06/2025 | 09:05 | 19/06/2025 | 09:38 | 0.0338 | 0.001 | 105 | 3465 | Planned | Planned | OTHER Maintenance
20 |  | INCD-3956-K | Avalon Dr | Network | AVACB3 | 26/06/2025 | 23:55 | 27/06/2025 | 06:15 | 1.6318 | 0.0087 | 889 | 167490 | Unplanned | Third_party | Car in contact with pole
21 |  | INCD-8171-K | Avalon Dr | Network | AVACB3 | 13/10/2025 | 10:44 | 15/10/2025 | 18:01 | 0.8036 | 0.0037 | 377 | 82482 | Unplanned | Third_party | Car in contact with pole
22 |  | INCD-351-M | Avalon | Network | AVACB3 | 07/10/2025 | 09:49 | 07/10/2025 | 15:22 | 0.7729 | 0.0024 | 246 | 79332 | Planned | Planned | Recloser & Sectionaliser replacement
23 |  | INCD-4571-K | Avalon | Network | AVACB3 | 15/07/2025 | 09:11 | 15/07/2025 | 11:30 | 0.111 | 0.0008 | 82 | 11398 | Unplanned | Defective Equipment | Connect/jumper loose
24 |  | INCD-4075-K | Avalon Dr | Network | AVACB3 | 28/06/2025 | 05:07 | 28/06/2025 | 05:54 | 0.0655 | 0.0014 | 143 | 6721 | Unplanned | Third_party | Car in contact with pole
25 |  | INCD-159-M | Avalon | Network | AVACB3 | 07/07/2025 | 08:50 | 07/07/2025 | 12:05 | 0.1805 | 0.0009 | 95 | 18525 | Planned | Planned | OTHER Maintenance
26 |  | INCD-4076-K | Avalon Dr | Network | AVACB3 | 27/06/2025 | 15:57 | 27/06/2025 | 18:06 | 0.3379 | 0.0026 | 267 | 34688 | Unplanned | Third_party | Car in contact with pole
27 |  | INCD-557-M | Avalon | Network | AVACB4 | 23/01/2026 | 09:43 | 23/01/2026 | 15:49 | 0.9392 | 0.0027 | 275 | 96404 | Planned | Planned | ABS Replacement
28 |  | INCD-1442-L | Avalon Dr | Network | AVACB4 | 23/11/2025 | 13:22 | 23/11/2025 | 14:43 | 0.041 | 0.0005 | 52 | 4212 | Unplanned | Defective Equipment | Cable fails unknown
29 |  | INCD-5927-K | Avalon Dr | Private | AVACB4 | 18/08/2025 | 22:24 | 18/08/2025 | 22:36 | 0.0116 | 0.001 | 99 | 1188 | Unplanned | Defective Equipment | LVC - WEL & Customer
30 |  | INCD-9102-K | Avalon Dr | Network | AVACB4 | 20/11/2025 | 08:26 | 20/11/2025 | 14:07 | 0.1634 | 0.0007 | 72 | 16772 | Unplanned | Defective Equipment | Cable fails unknown
31 |  | INCD-165-L | Avalon | Network | AVACB4 | 23/06/2025 | 09:02 | 23/06/2025 | 12:42 | 0.1419 | 0.0012 | 124 | 14564 | Unplanned | Defective Equipment | Cable termination fails
32 |  | INCD-3799-K | Avalon Dr | Network | AVACB4 | 18/06/2025 | 09:15 | 18/06/2025 | 15:10 | 0.4154 | 0.0012 | 124 | 42639 | Unplanned | Defective Equipment | Cable termination fails
33 |  | INCD-79-L | Avalon Dr | Network | AVACB4 | 04/06/2025 | 13:45 | 04/06/2025 | 14:34 | 0.0306 | 0.0006 | 64 | 3136 | Unplanned | Defective Equipment | Blown Fuse
34 |  | INCD-1443-L | Avalon Dr | Network | AVACB4 | 23/11/2025 | 13:22 | 23/11/2025 | 14:31 | 0.08 | 0.0012 | 119 | 8211 | Unplanned | Defective Equipment | Cable fails unknown
35 |  | INCD-12264-K | Avalon | Network | AVACB6 | 07/03/2026 | 23:08 | 08/03/2026 | 00:34 | 0.1421 | 0.0017 | 171 | 14590 | Planned | Planned | OTHER Maintenance
36 |  | INCD-10296-K | Avalon Dr | Network | AVACB6 | 01/01/2026 | 11:04 | 01/01/2026 | 11:54 | 0.038 | 0.0008 | 78 | 3900 | Unplanned | Defective Equipment | Cable fails unknown
37 |  | INCD-12248-K | Avalon Dr | Network | AVACB6 | 07/03/2026 | 00:02 | 07/03/2026 | 01:41 | 0.1649 | 0.0017 | 171 | 16929 | Planned | Planned | OTHER Maintenance
38 |  | INCD-10176-K | Avalon Dr | Network | AVACB6 | 30/12/2025 | 08:51 | 30/12/2025 | 18:34 | 0.9495 | 0.0017 | 171 | 97459 | Unplanned | Defective Equipment | Cable fails unknown
39 |  | INCD-10297-K | Avalon Dr | Network | AVACB6 | 01/01/2026 | 11:04 | 01/01/2026 | 11:54 | 0.0268 | 0.0005 | 55 | 2750 | Unplanned | Defective Equipment | Cable fails unknown
40 |  | INCD-11556-K | Avalon Dr | Network | AVACB6 | 09/02/2026 | 08:32 | 09/02/2026 | 15:07 | 0.5259 | 0.0017 | 171 | 53977 | Unplanned | Unknown | All Ok - Fault cause not established
41 |  | INCD-10299-K | Avalon Dr | Network | AVACB6 | 01/01/2026 | 11:04 | 01/01/2026 | 11:54 | 0.0185 | 0.0004 | 38 | 1900 | Unplanned | Defective Equipment | Cable fails unknown
42 |  | INCD-3373-K | Avalon Dr | Network | AVACB7 | 08/06/2025 | 08:06 | 08/06/2025 | 17:15 | 0.0053 | 0 | 1 | 549 | Planned | Planned | OTHER Maintenance
43 |  | INCD-11776-K | Avalon | Network | AVACB8 | 16/03/2026 | 08:38 | 16/03/2026 | 16:23 | 0.0449 | 0.0037 | 384 | 4608 | Planned | Planned | New Connections
44 |  | INCD-562-M | Avalon | Network | AVACB8 | 28/01/2026 | 09:03 | 28/01/2026 | 15:13 | 0.1911 | 0.0005 | 53 | 19610 | Planned | Planned | OTHER Maintenance
45 |  | INCD-594-M | Avalon | Network | AVACB8 | 29/01/2026 | 08:33 | 29/01/2026 | 12:05 | 0.0103 | 0 | 5 | 1060 | Planned | Planned | Crossarm Replacement
46 |  | INCD-207-M | Avalon | Network | AVACB8 | 30/07/2025 | 10:14 | 30/07/2025 | 14:42 | 0.1877 | 0.0007 | 74 | 19265 | Planned | Planned | Mixed Asset Replacement
47 |  | INCD-458-M | Avalon | Network | AVACB8 | 19/12/2025 | 09:00 | 19/12/2025 | 12:41 | 0.1343 | 0.0007 | 69 | 13789 | Planned | Planned | Pole Replacement
48 |  | INCD-90-L | Avalon | Network | AVACB8 | 07/08/2025 | 08:32 | 07/08/2025 | 15:49 | 0.2863 | 0.0007 | 68 | 29385 | Planned | Planned | Distribution Transformer Replacement
49 |  | INCD-9019-K | Avalon | Network | AVACB8 | 18/12/2025 | 09:07 | 18/12/2025 | 13:26 | 0.037 | 0.0037 | 380 | 3800 | Planned | Planned | Mixed Asset Replacement
50 |  | INCD-3376-K | Avalon Dr | Network | AVACB8 | 08/06/2025 | 09:20 | 08/06/2025 | 15:09 | 0.0034 | 0 | 1 | 349 | Planned | Planned | OTHER Maintenance
51 |  | INCD-8250-K | Avalon | Network | AVACB8 | 15/11/2025 | 08:48 | 15/11/2025 | 15:41 | 0.0907 | 0.0037 | 380 | 9310 | Planned | Planned | Mixed Asset Replacement
52 |  | INCD-4648-K | Avalon Dr | Network | AVACB8 | 16/07/2025 | 23:27 | 17/07/2025 | 02:07 | 0.1162 | 0.0013 | 130 | 11926 | Unplanned | Third_party | Cable isolated- saftey reasons
53 |  | INCD-7010-K | Borman Rd | Network | BORCB1 | 11/09/2025 | 21:11 | 12/09/2025 | 02:18 | 1.6195 | 0.0087 | 888 | 166226 | Unplanned | Lightning | Spontaneous failure
54 |  | INCD-12272-K | Transpower Hamilton | Network | BORCB1 | 09/03/2026 | 06:33 | 09/03/2026 | 07:44 | 0.2417 | 0.0087 | 894 | 24808 | Unplanned | Defective Equipment | Loose connection
55 |  | INCD-397-M | Borman | Network | BORCB1 | 05/03/2026 | 09:33 | 05/03/2026 | 15:57 | 0.2432 | 0.0006 | 65 | 24960 | Planned | Planned | New Connections
56 |  | INCD-12272-K | Transpower Hamilton | Network | BORCB2 | 09/03/2026 | 06:33 | 09/03/2026 | 07:44 | 0.2991 | 0.006 | 614 | 30700 | Unplanned | Defective Equipment | Loose connection
57 |  | INCD-372-M | Borman | Network | BORCB3 | 23/10/2025 | 09:09 | 23/10/2025 | 11:17 | 0.1035 | 0.0008 | 83 | 10624 | Planned | Planned | OTHER Maintenance
58 |  | INCD-383-M | Borman | Network | BORCB3 | 28/10/2025 | 09:13 | 28/10/2025 | 12:18 | 0.119 | 0.0006 | 66 | 12210 | Planned | Planned | OTHER Maintenance
59 |  | INCD-369-M | Borman | Network | BORCB3 | 22/10/2025 | 09:05 | 22/10/2025 | 13:25 | 0.2305 | 0.0009 | 91 | 23660 | Planned | Planned | OTHER Maintenance
60 |  | INCD-12272-K | Transpower Hamilton | Network | BORCB3 | 09/03/2026 | 06:33 | 09/03/2026 | 07:44 | 0.7857 | 0.0116 | 1193 | 80647 | Unplanned | Defective Equipment | Loose connection
61 |  | INCD-12272-K | Transpower Hamilton | Network | BORCB4 | 09/03/2026 | 06:33 | 09/03/2026 | 07:44 | 0.383 | 0.0138 | 1417 | 39312 | Unplanned | Defective Equipment | Loose connection
62 |  | INCD-467-M | Borman | Network | BORCB5 | 12/12/2025 | 10:04 | 12/12/2025 | 13:16 | 0.0206 | 0.0001 | 11 | 2112 | Planned | Planned | Pole Replacement
63 |  | INCD-384-M | Borman | Network | BORCB5 | 29/10/2025 | 09:24 | 29/10/2025 | 14:51 | 0.3058 | 0.0009 | 96 | 31392 | Planned | Planned | OTHER Maintenance
64 |  | INCD-12272-K | Transpower Hamilton | Network | BORCB5 | 09/03/2026 | 06:33 | 09/03/2026 | 07:44 | 0.7783 | 0.0142 | 1459 | 79895 | Unplanned | Defective Equipment | Loose connection
65 |  | INCD-12272-K | Transpower Hamilton | Network | BORCB6 | 09/03/2026 | 06:33 | 09/03/2026 | 07:44 | 0.3146 | 0.0139 | 1429 | 32295 | Unplanned | Defective Equipment | Loose connection
66 |  | INCD-371-M | Borman | Network | BORCB7 | 24/10/2025 | 09:07 | 24/10/2025 | 11:32 | 0.0268 | 0.0002 | 19 | 2755 | Planned | Planned | OTHER Maintenance
67 |  | INCD-12272-K | Transpower Hamilton | Network | BORCB7 | 09/03/2026 | 06:33 | 09/03/2026 | 07:44 | 0.8524 | 0.0135 | 1382 | 87493 | Unplanned | Defective Equipment | Loose connection
68 |  | INCD-12800-K | Bryce St | Network | BRYCB12 | 30/03/2026 | 22:13 | 31/03/2026 | 05:47 | 0.0941 | 0.0009 | 92 | 9660 | Planned | Planned | OTHER Maintenance
69 |  | INCD-3755-K | Bryce St | Network | BRYCB12 | 17/06/2025 | 09:13 | 17/06/2025 | 09:13 | 0.005 | 0 | 1 | 511 | Planned | Planned | OTHER Maintenance
70 |  | INCD-9083-K | Bryce St | Network | BRYCB12 | 19/11/2025 | 14:41 | 19/11/2025 | 15:03 | 0.0206 | 0.0009 | 96 | 2112 | Unplanned | Defective Equipment | Fuse blown on overload
71 |  | INCD-3205-K | Bryce St | Network | BRYCB12 | 04/06/2025 | 08:14 | 04/06/2025 | 08:14 | 0.0037 | 0 | 1 | 379 | Planned | Planned | OTHER Maintenance
72 |  | INCD-2846-K | Cobham Dr | Network | BRYCB3 | 25/05/2025 | 06:47 | 25/05/2025 | 06:52 | 0.0001 | 0 | 3 | 15 | Planned | Unknown | RMU Replacement
73 |  | INCD-12462-K | Bryce St | Network | BRYCB6 | 18/03/2026 | 06:11 | 18/03/2026 | 07:31 | 0.0312 | 0.0022 | 221 | 3202 | Unplanned | Defective Equipment | Cable joint fails
74 |  | INCD-9078-K | Bryce St | Network | BRYCB6 | 19/11/2025 | 14:07 | 19/11/2025 | 16:26 | 0.0571 | 0.0022 | 221 | 5860 | Unplanned | Defective Equipment | Cable fails unknown
75 |  | INCD-146-M | Chartwell | Network | CHACB12 | 01/07/2025 | 09:39 | 01/07/2025 | 12:48 | 0.197 | 0.001 | 107 | 20223 | Planned | Planned | OTHER Maintenance
76 |  | INCD-421-M | Chartwell | Network | CHACB12 | 14/11/2025 | 08:25 | 14/11/2025 | 15:20 | 0.2426 | 0.0006 | 60 | 24900 | Planned | Planned | OTHER Maintenance
77 |  | INCD-12131-K | Chartwell | Network | CHACB12 | 26/03/2026 | 08:30 | 26/03/2026 | 10:43 | 0.0222 | 0.003 | 304 | 2280 | Planned | Planned | New Connections
78 |  | INCD-261-N | Chartwell | Network | CHACB12 | 25/02/2026 | 08:04 | 25/02/2026 | 11:19 | 0.3857 | 0.002 | 203 | 39585 | Planned | Planned | OTHER Maintenance
79 |  | INCD-7010-K | Borman Rd | Network | CHACB12 | 11/09/2025 | 21:11 | 12/09/2025 | 02:18 | 0.0004 | 0 | 1 | 45 | Unplanned | Lightning | Spontaneous failure
80 |  | INCD-48-M | Chartwell | Network | CHACB12 | 14/05/2025 | 10:10 | 14/05/2025 | 17:59 | 0.813 | 0.0018 | 189 | 83446 | Planned | Planned | OTHER Maintenance
81 |  | INCD-74-L | Chartwell | Network | CHACB13 | 01/06/2025 | 05:23 | 01/06/2025 | 06:43 | 0.097 | 0.0015 | 156 | 9961 | Unplanned | Defective Equipment | Flashovr on cable bush
82 |  | INCD-2896-K | Chartwell | Network | CHACB13 | 27/05/2025 | 00:08 | 27/05/2025 | 01:52 | 0.0933 | 0.0015 | 156 | 9575 | Unplanned | Defective Equipment | Poor contacts
83 |  | INCD-9129-K | Chartwell | Network | CHACB5 | 20/11/2025 | 14:08 | 20/11/2025 | 15:17 | 0.0414 | 0.0009 | 91 | 4254 | Unplanned | Defective Equipment | LV Panel fire
84 |  | INCD-32-M | Chartwell | Network | CHACB5 | 13/04/2025 | 09:45 | 13/04/2025 | 17:34 | 0.0274 | 0.0001 | 6 | 2814 | Planned | Planned | Pole Replacement
85 |  | INCD-9048-K | Chartwell | Network | CHACB5 | 19/11/2025 | 00:34 | 19/11/2025 | 14:08 | 0.5142 | 0.0009 | 91 | 52781 | Unplanned | Defective Equipment | LV Panel fire
86 |  | INCD-4307-K | Chartwell | Network | CHACB6 | 08/07/2025 | 09:21 | 08/07/2025 | 16:40 | 0.7827 | 0.0018 | 183 | 80337 | Planned | Planned | ABS Replacement
87 |  | INCD-9644-K | Chartwell | Network | CHACB7 | 11/12/2025 | 14:11 | 11/12/2025 | 14:49 | 0.0292 | 0.0008 | 79 | 3002 | Planned | Planned | New Connections
88 |  | INCD-9492-K | Borman Rd | Network | CHACB7 | 08/12/2025 | 09:08 | 08/12/2025 | 11:26 | 0.1949 | 0.002 | 205 | 20006 | Planned | Planned | RMU Replacement
89 |  | INCD-9555-K | Chartwell | Network | CHACB7 | 09/12/2025 | 14:01 | 09/12/2025 | 14:44 | 0.0126 | 0.0003 | 30 | 1290 | Planned | Planned | RMU Replacement
90 |  | INCD-201-M | Chartwell | Network | CHACB9 | 25/07/2025 | 09:00 | 25/07/2025 | 15:07 | 0.0822 | 0.0002 | 23 | 8441 | Planned | Planned | Mixed Asset Replacement
91 |  | INCD-11450-K | Chartwell | Network | CHACB9 | 04/02/2026 | 09:37 | 04/02/2026 | 11:10 | 0.0251 | 0.0003 | 31 | 2575 | Planned | Planned | OTHER Maintenance
92 |  | INCD-279-M | Chartwell | Network | CHACB9 | 03/09/2025 | 09:30 | 03/09/2025 | 15:59 | 0.1337 | 0.0006 | 64 | 13724 | Planned | Planned | Mixed Asset Replacement
93 |  | INCD-4242-K | Chartwell | Network | CHACB9 | 07/07/2025 | 09:34 | 07/07/2025 | 11:21 | 0.0344 | 0.0003 | 33 | 3531 | Planned | Planned | OTHER Maintenance
94 |  | INCD-12236-K | Chartwell | Network | CHACB9 | 06/03/2026 | 09:43 | 06/03/2026 | 12:12 | 0.1071 | 0.0007 | 74 | 10991 | Unplanned | Third_party | Car in contact with pole
95 |  | INCD-11836-K | Chartwell | Network | CHACB9 | 17/02/2026 | 21:55 | 17/02/2026 | 23:24 | 0.0338 | 0.0004 | 39 | 3471 | Unplanned | Defective Equipment | Split crossarm
96 |  | INCD-294-M | Chartwell | Network | CHACB9 | 17/09/2025 | 09:09 | 17/09/2025 | 12:13 | 0.0108 | 0.0001 | 6 | 1104 | Planned | Planned | Crossarm Replacement
97 |  | INCD-216-M | Chartwell | Network | CHACB9 | 07/08/2025 | 10:03 | 07/08/2025 | 15:42 | 0.1123 | 0.0003 | 35 | 11529 | Planned | Planned | Mixed Asset Replacement
98 |  | INCD-401-M | Chartwell | Network | CHACB9 | 14/11/2025 | 09:05 | 14/11/2025 | 15:52 | 0.2097 | 0.0006 | 57 | 21522 | Planned | Planned | Mixed Asset Replacement
99 |  | INCD-12226-K | Chartwell | Network | CHACB9 | 05/03/2026 | 23:43 | 06/03/2026 | 00:43 | 0.0999 | 0.0055 | 566 | 10251 | Unplanned | Third_party | Car in contact with pole
100 |  | INCD-8103-K | Chartwell | Network | CHACB9 | 09/10/2025 | 12:00 | 10/10/2025 | 02:06 | 0.3839 | 0.0035 | 364 | 39409 | Unplanned | Third_party | High vehicle contact
101 |  | INCD-10548-K | Chartwell | Network | CHACB9 | 13/01/2026 | 03:17 | 13/01/2026 | 03:40 | 0.0281 | 0.0036 | 365 | 2883 | Unplanned | Unknown | All Ok - Fault cause not established
102 |  | INCD-295-M | Chartwell | Network | CHACB9 | 12/09/2025 | 09:11 | 12/09/2025 | 14:27 | 0.0954 | 0.0003 | 31 | 9796 | Planned | Planned | Mixed Asset Replacement
103 |  | INCD-330-M | Chartwell | Network | CHACB9 | 09/10/2025 | 09:24 | 09/10/2025 | 12:35 | 0.0707 | 0.0004 | 38 | 7258 | Planned | Planned | Crossarm Replacement
104 |  | INCD-10770-K | Chartwell | Network | CHACB9 | 18/01/2026 | 07:40 | 18/01/2026 | 09:10 | 0.0035 | 0 | 4 | 360 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
105 |  | INCD-5034-K | Chartwell | Network | CHACB9 | 25/07/2025 | 14:49 | 25/07/2025 | 19:08 | 0.0958 | 0.0006 | 65 | 9838 | Unplanned | Third_party | Car in contact with pole
106 |  | INCD-12615-K | Chartwell | Network | CHACB9 | 23/03/2026 | 09:56 | 23/03/2026 | 11:19 | 0.0008 | 0 | 1 | 83 | Unplanned | Unknown | All Ok - Fault cause not established
107 |  | INCD-310-M | Chartwell | Network | CHACB9 | 17/09/2025 | 09:19 | 17/09/2025 | 16:07 | 0.1232 | 0.0003 | 31 | 12648 | Planned | Planned | Mixed Asset Replacement
108 |  | INCD-6075-K | Chartwell | Network | CHACB9 | 22/08/2025 | 02:28 | 22/08/2025 | 04:23 | 0.0581 | 0.0005 | 52 | 5964 | Unplanned | Unknown | All Ok - Fault cause not established
109 |  | INCD-272-N | Chartwell | Network | CHACB9 | 20/03/2026 | 09:05 | 20/03/2026 | 11:40 | 0.0121 | 0.0001 | 8 | 1240 | Planned | Planned | New Connections
110 |  | INCD-619-M | Chartwell | Network | CHACB9 | 11/03/2026 | 09:05 | 11/03/2026 | 17:05 | 0.1788 | 0.0017 | 179 | 18354 | Planned | Planned | Mixed Asset Replacement
111 |  | INCD-385-M | Chartwell | Network | CHACB9 | 31/10/2025 | 09:04 | 31/10/2025 | 15:08 | 0.1365 | 0.0004 | 39 | 14011 | Planned | Planned | Mixed Asset Replacement
112 |  | INCD-6525-K | Chartwell | Network | CHACB9 | 02/09/2025 | 03:31 | 02/09/2025 | 05:38 | 0.0037 | 0 | 3 | 381 | Unplanned | Unknown | All Ok - Fault cause not established
113 |  | INCD-382-M | Civic Car Park | Network | CIVCB4 | 29/10/2025 | 22:08 | 29/10/2025 | 23:09 | 0.0256 | 0.0004 | 43 | 2623 | Planned | Planned | OTHER Maintenance
114 |  | INCD-8242-K | Civic Car Park | Network | CIVCB5 | 15/10/2025 | 22:01 | 16/10/2025 | 03:22 | 0.1626 | 0.0005 | 52 | 16692 | Planned | Planned | Distribution Transformer Replacement
115 |  | INCD-11129-K | Claudelands | Network | CLACB10 | 24/01/2026 | 21:55 | 25/01/2026 | 00:16 | 0.8368 | 0.0141 | 1446 | 85895 | Unplanned | Defective Equipment | Cable fails unknown
116 |  | INCD-510-M | Transpower Hamilton | Network | CLACB10 | 04/12/2025 | 00:09 | 04/12/2025 | 00:37 | 0.0644 | 0.0023 | 236 | 6608 | Planned | Planned | OTHER Maintenance
117 |  | INCD-807-K | Claudelands | Network | CLACB10 | 02/04/2025 | 00:09 | 02/04/2025 | 00:16 | 0.0161 | 0.0023 | 236 | 1652 | Unplanned | Defective Equipment | Wear or shear of pins
118 |  | INCD-8898-K | Transpower Hamilton | Network | CLACB10 | 14/11/2025 | 08:49 | 14/11/2025 | 13:32 | 0.6294 | 0.0023 | 236 | 64604 | Planned | Planned | Mixed Asset Replacement
119 |  | INCD-12562-K | Claudelands | Network | CLACB10 | 21/03/2026 | 00:28 | 21/03/2026 | 00:28 | 0.0037 | 0.0055 | 568 | 379 | Planned | Planned | Mixed Asset Replacement
120 |  | INCD-11660-K | Transpower Hamilton | Network | CLACB10 | 11/02/2026 | 16:09 | 11/02/2026 | 19:51 | 0.1471 | 0.0007 | 68 | 15096 | Unplanned | Defective Equipment | Connect/jumper loose
121 |  | INCD-12548-K | Transpower Hamilton | Network | CLACB10 | 20/03/2026 | 23:59 | 21/03/2026 | 00:01 | 0.0159 | 0.0055 | 568 | 1628 | Planned | Planned | Mixed Asset Replacement
122 |  | INCD-396-M | Transpower Hamilton | Network | CLACB10 | 05/11/2025 | 08:49 | 05/11/2025 | 14:18 | 0.218 | 0.0007 | 68 | 22372 | Planned | Planned | OTHER Maintenance
123 |  | INCD-264-N | Transpower Hamilton | Network | CLACB10 | 20/02/2026 | 08:20 | 20/02/2026 | 16:10 | 0.7784 | 0.0017 | 170 | 79900 | Planned | Planned | RMU Replacement
124 |  | INCD-4487-K | Claudelands | Network | CLACB13 | 11/07/2025 | 23:48 | 11/07/2025 | 23:58 | 0.0112 | 0.0011 | 115 | 1150 | Unplanned | Defective Equipment | Fuse blown on overload
125 |  | INCD-8224-K | Claudelands | Network | CLACB13 | 15/10/2025 | 09:04 | 15/10/2025 | 15:15 | 0.0614 | 0.0002 | 17 | 6307 | Planned | Planned | Conductor Replacement
126 |  | INCD-3598-K | Claudelands | Network | CLACB13 | 12/06/2025 | 18:09 | 12/06/2025 | 18:58 | 0.0466 | 0.0022 | 228 | 4788 | Unplanned | Defective Equipment | Fuse blown on overload
127 |  | INCD-89-L | Claudelands | Network | CLACB13 | 10/06/2025 | 22:19 | 11/06/2025 | 02:29 | 0.2777 | 0.0011 | 114 | 28500 | Unplanned | Defective Equipment | Cable fails unknown
128 |  | INCD-1762-L | Claudelands | Network | CLACB16 | 15/01/2026 | 22:04 | 15/01/2026 | 22:42 | 0.0267 | 0.0007 | 72 | 2736 | Planned | Planned | Mixed Asset Replacement
129 |  | INCD-8095-K | Transpower Hamilton | Network | CLACB16 | 09/10/2025 | 07:12 | 09/10/2025 | 11:29 | 0.1798 | 0.0007 | 72 | 18456 | Unplanned | Third_party | Car in contact with pole
130 |  | INCD-8139-K | Transpower Hamilton | Network | CLACB16 | 10/10/2025 | 17:39 | 10/10/2025 | 19:00 | 0.1413 | 0.0019 | 198 | 14508 | Unplanned | Defective Equipment | Bus chamber flashovr
131 |  | INCD-498-M | Claudelands | Network | CLACB16 | 13/01/2026 | 22:01 | 14/01/2026 | 03:20 | 0.2236 | 0.0007 | 72 | 22956 | Planned | Planned | Mixed Asset Replacement
132 |  | INCD-8608-K | Transpower Hamilton | Network | CLACB16 | 03/11/2025 | 06:00 | 03/11/2025 | 12:42 | 0.0038 | 0.0007 | 72 | 392 | Planned | Planned | Transformer Upgrade
133 |  | INCD-7236-K | Claudelands | Network | CLACB3 | 16/09/2025 | 15:04 | 16/09/2025 | 15:19 | 0.0172 | 0.0011 | 118 | 1770 | Unplanned | Third_party | Cable isolated - safety reasons
134 |  | INCD-2086-K | Claudelands | Network | CLACB3 | 05/05/2025 | 17:54 | 05/05/2025 | 23:35 | 0.4391 | 0.0013 | 136 | 45069 | Unplanned | Defective Equipment | Cable fails unknown
135 |  | INCD-35-L | Claudelands | Private | CLACB3 | 23/04/2025 | 14:45 | 23/04/2025 | 14:47 | 0.0032 | 0.0016 | 164 | 328 | Unplanned | Third_party | Temp Disconnect / safety isolation
136 |  | INCD-760-K | Claudelands | Network | CLACB3 | 01/04/2025 | 00:06 | 01/04/2025 | 00:26 | 0.0116 | 0.0006 | 62 | 1191 | Unplanned | Third_party | Cable isolated - safety reasons
137 |  | INCD-2354-K | Claudelands | Network | CLACB3 | 07/05/2025 | 00:02 | 11/05/2025 | 01:05 | 0.3267 | 0.0032 | 326 | 33532 | Unplanned | Defective Equipment | Cable fails unknown
138 |  | INCD-78-N | Claudeland | Network | CLACB3 | 18/08/2025 | 22:04 | 19/08/2025 | 05:26 | 0.0119 | 0.0007 | 74 | 1221 | Planned | Planned | Mixed Asset Replacement
139 |  | INCD-12115-K | Peachgrove Rd | Network | CLACB5 | 01/03/2026 | 08:17 | 01/03/2026 | 15:27 | 0.0042 | 0 | 1 | 429 | Planned | Planned | OTHER Maintenance
140 |  | INCD-148-M | Cobham | Network | COBCB11 | 23/07/2025 | 08:07 | 26/07/2025 | 12:27 | 0.0811 | 0.0003 | 32 | 8320 | Planned | Planned | Mixed Asset Replacement
141 |  | INCD-8192-K | Cobham Dr | Network | COBCB12 | 14/10/2025 | 08:36 | 14/10/2025 | 09:59 | 0.0454 | 0.0005 | 47 | 4656 | Planned | Planned | Mixed Asset Replacement
142 |  | INCD-1767-L | Cobham Dr | Network | COBCB3 | 21/01/2026 | 14:57 | 21/01/2026 | 15:03 | 0.0085 | 0.0014 | 145 | 870 | Planned | Planned | OTHER Maintenance
143 |  | INCD-10891-K | Cobham Dr | Network | COBCB3 | 21/01/2026 | 09:33 | 21/01/2026 | 10:19 | 0.065 | 0.0014 | 145 | 6670 | Planned | Planned | OTHER Maintenance
144 |  | INCD-6883-K | Kent St | Network | COBCB9 | 09/09/2025 | 09:15 | 09/09/2025 | 09:33 | 0.0001 | 0 | 1 | 13 | Unplanned | Defective Equipment | Cable joint fails
145 |  | INCD-12804-K | Cobham | Network | COBCB9 | 31/03/2026 | 04:19 | 31/03/2026 | 05:12 | 0.0005 | 0 | 1 | 53 | Planned | Planned | OTHER Maintenance
146 |  | INCD-455-M | Cobham | Network | COBCB9 | 13/12/2025 | 08:33 | 13/12/2025 | 10:17 | 0.002 | 0 | 2 | 208 | Planned | Planned | RMU Replacement
147 |  | INCD-12803-K | Cobham Dr | Network | COBCB9 | 30/03/2026 | 23:16 | 31/03/2026 | 00:28 | 0.0007 | 0 | 1 | 72 | Planned | Planned | OTHER Maintenance
148 |  | INCD-8364-K | Crawford Rd | Network | CRACB4 | 22/10/2025 | 08:20 | 22/10/2025 | 16:17 | 0.0046 | 0 | 1 | 477 | Planned | Planned | OTHER Maintenance
149 |  | INCD-528-M | Findlay | Network | FDLCB2 | 18/12/2025 | 08:01 | 18/12/2025 | 16:55 | 0.143 | 0.0036 | 374 | 14679 | Planned | Planned | OTHER Maintenance
150 |  | INCD-10312-K | Finlayson | Network | FINCB1 | 10/02/2026 | 09:28 | 10/02/2026 | 14:35 | 0.0449 | 0.0001 | 15 | 4605 | Planned | Planned | Mixed Asset Replacement
151 |  | INCD-265-N | Hampton Downs | Network | FINCB1 | 15/02/2026 | 08:29 | 15/02/2026 | 17:24 | 0.0042 | 0 | 1 | 431 | Planned | Planned | Mixed Asset Replacement
152 |  | INCD-10256-K | Finlayson Rd | Network | FINCB1 | 03/01/2026 | 04:16 | 03/01/2026 | 12:31 | 0.1208 | 0.0075 | 774 | 12396 | Unplanned | Defective Equipment | Split crossarm
153 |  | INCD-459-M | Finlayson | Network | FINCB1 | 08/12/2025 | 09:14 | 08/12/2025 | 14:39 | 0.1077 | 0.0003 | 34 | 11050 | Planned | Planned | Crossarm Replacement
154 |  | INCD-7921-K | Te Kauwhata | Network | FINCB1 | 04/10/2025 | 08:21 | 04/10/2025 | 10:03 | 0.12 | 0.004 | 413 | 12319 | Unplanned | Lightning | Lightning strike surge
155 |  | INCD-12153-K | Finlayson Rd | Network | FINCB1 | 03/03/2026 | 05:37 | 03/03/2026 | 11:49 | 0.1367 | 0.004 | 411 | 14034 | Unplanned | Defective Equipment | Line break at twist joint
156 |  | INCD-10201-K | Finlayson Rd | Network | FINCB1 | 29/12/2025 | 16:20 | 30/12/2025 | 20:03 | 0.1458 | 0.0001 | 9 | 14967 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
157 |  | INCD-8094-K | Finlayson | Network | FINCB1 | 08/10/2025 | 13:51 | 08/10/2025 | 19:06 | 0.0184 | 0.0001 | 6 | 1890 | Unplanned | Unknown | All Ok - Fault cause not established
158 |  | INCD-4-N | Finlayson | Network | FINCB1 | 30/06/2025 | 10:41 | 30/06/2025 | 12:32 | 0.0011 | 0 | 2 | 110 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
159 |  | INCD-10517-K | Finlayson Rd | Network | FINCB1 | 12/01/2026 | 09:14 | 12/01/2026 | 12:05 | 0.0625 | 0.0004 | 41 | 6417 | Planned | Planned | OTHER Maintenance
160 |  | INCD-1782-L | Finlayson Rd | Private | FINCB1 | 10/02/2026 | 14:53 | 10/02/2026 | 16:20 | 0.0068 | 0.0001 | 8 | 696 | Unplanned | Unknown | All Ok - Fault cause not established
161 |  | INCD-6897-K | Finlayson Rd | Network | FINCB1 | 09/09/2025 | 12:55 | 09/09/2025 | 23:13 | 0.094 | 0.0004 | 38 | 9650 | Unplanned | Third_party | Car in contact with pole
162 |  | INCD-206-M | Finlayson | Network | FINCB1 | 30/07/2025 | 10:09 | 30/07/2025 | 14:08 | 0.021 | 0.0001 | 9 | 2151 | Planned | Planned | Pole Replacement
163 |  | INCD-7089-K | Finlayson Rd | Network | FINCB1 | 13/09/2025 | 08:32 | 13/09/2025 | 10:06 | 0.0009 | 0 | 1 | 94 | Unplanned | Defective Equipment | Mechanism seized
164 |  | INCD-174-M | Finlayson | Network | FINCB1 | 25/06/2025 | 09:45 | 25/06/2025 | 11:15 | 0.0333 | 0.0004 | 38 | 3420 | Planned | Planned | Conductor Replacement
165 |  | INCD-6351-K | Finlayson Rd | Network | FINCB1 | 31/08/2025 | 08:04 | 31/08/2025 | 18:21 | 0.0019 | 0 | 1 | 197 | Unplanned | Vegetation | Tree blown ovr on line (OUT of Zone)
166 |  | INCD-4014-K | Finlayson | Network | FINCB1 | 28/06/2025 | 18:38 | 28/06/2025 | 21:18 | 0.0109 | 0.0001 | 7 | 1120 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
167 |  | INCD-10181-K | Finlayson Rd | Network | FINCB1 | 30/12/2025 | 05:30 | 30/12/2025 | 11:12 | 0.0033 | 0 | 1 | 342 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
168 |  | INCD-378-M | Finlayson | Network | FINCB1 | 04/11/2025 | 10:13 | 04/11/2025 | 16:52 | 0.0078 | 0 | 2 | 798 | Planned | Planned | ABS Replacement
169 |  | INCD-533-M | Finlayson | Network | FINCB1 | 07/01/2026 | 09:07 | 07/01/2026 | 11:17 | 0.0089 | 0.0001 | 7 | 910 | Planned | Planned | Mixed Asset Replacement
170 |  | INCD-444-L | Finlayson Rd | Network | FINCB1 | 25/07/2025 | 08:41 | 25/07/2025 | 12:17 | 0.0021 | 0 | 1 | 216 | Unplanned | Unknown | All Ok - Fault cause not established
171 |  | INCD-3119-E | Finlayson | Network | FINCB1 | 09/04/2025 | 08:03 | 09/04/2025 | 13:47 | 0.538 | 0.0017 | 179 | 55221 | Planned | Planned | Mixed Asset Replacement
172 |  | INCD-338-M | Finlayson | Network | FINCB1 | 05/10/2025 | 09:32 | 05/10/2025 | 12:51 | 0.0403 | 0.0002 | 22 | 4134 | Planned | Planned | Mixed Asset Replacement
173 |  | INCD-250-M | Finalyson | Network | FINCB1 | 19/08/2025 | 09:11 | 19/08/2025 | 13:45 | 0.0107 | 0 | 4 | 1096 | Planned | Planned | Pole Replacement
174 |  | INCD-8882-K | Finlayson Rd | Network | FINCB1 | 13/11/2025 | 09:16 | 13/11/2025 | 17:03 | 0.0045 | 0 | 1 | 467 | Unplanned | Vegetation | Wind debris on line (IN Zone)
175 |  | INCD-8659-K | Finlayson Rd | Network | FINCB1 | 04/11/2025 | 17:20 | 04/11/2025 | 19:51 | 0.0015 | 0 | 1 | 151 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
176 |  | INCD-10710-K | Finlayson Rd | Network | FINCB1 | 16/01/2026 | 08:25 | 16/01/2026 | 09:34 | 0.004 | 0.0001 | 6 | 414 | Unplanned | Lightning | Lightning damage
177 |  | INCD-12229-K | Finalyson | Network | FINCB1 | 05/03/2026 | 13:28 | 06/03/2026 | 02:35 | 0.3112 | 0.0005 | 51 | 31938 | Unplanned | Third_party | Car in contact with pole
178 |  | INCD-11070-K | Finlayson Rd | Network | FINCB1 | 23/01/2026 | 13:40 | 23/01/2026 | 15:43 | 0.1541 | 0.004 | 412 | 15819 | Unplanned | Vegetation | Wind debris on line (OUT of Zone)
179 |  | INCD-1190-K | Finlayson Rd | Network | FINCB1 | 11/04/2025 | 09:40 | 11/04/2025 | 12:18 | 0.0015 | 0 | 1 | 158 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
180 |  | INCD-2315-K | Te Kauwhata | Network | FINCB1 | 11/05/2025 | 07:54 | 11/05/2025 | 08:59 | 0.0801 | 0.0041 | 417 | 8225 | Unplanned | Unknown | All Ok - Fault cause not established
181 |  | INCD-6486-K | Finlayson Rd | Network | FINCB1 | 01/09/2025 | 10:50 | 01/09/2025 | 13:25 | 0.0375 | 0.0003 | 34 | 3844 | Unplanned | Defective Equipment | Faulty joint/connection
182 |  | INCD-10124-K | Finlayson Rd | Network | FINCB1 | 29/12/2025 | 15:20 | 30/12/2025 | 02:40 | 0.3441 | 0.0005 | 52 | 35318 | Unplanned | Unknown | All Ok - Fault cause not established
183 |  | INCD-12208-K | Finlayson Rd | Network | FINCB2 | 05/03/2026 | 10:32 | 05/03/2026 | 13:11 | 0.0015 | 0 | 1 | 159 | Unplanned | Defective Equipment | Split crossarm
184 |  | INCD-3747-K | Finlayson Rd | Network | FINCB2 | 16/06/2025 | 22:00 | 16/06/2025 | 23:51 | 0.0032 | 0 | 3 | 333 | Unplanned | Unknown | All Ok - Fault cause not established
185 |  | INCD-519-M | Finlayson | Network | FINCB2 | 08/01/2026 | 09:17 | 08/01/2026 | 13:18 | 0.0023 | 0 | 1 | 241 | Planned | Planned | Mixed Asset Replacement
186 |  | INCD-6351-K | Finlayson Rd | Network | FINCB2 | 31/08/2025 | 08:04 | 31/08/2025 | 18:21 | 0.114 | 0.0005 | 51 | 11697 | Unplanned | Vegetation | Tree blown ovr on line (OUT of Zone)
187 |  | INCD-9303-K | Finlayson Rd | Network | FINCB2 | 29/11/2025 | 09:01 | 29/11/2025 | 14:03 | 0.0219 | 0.0001 | 8 | 2246 | Planned | Planned | Mixed Asset Replacement
188 |  | INCD-7933-K | Finlayson | Network | FINCB2 | 04/10/2025 | 11:02 | 04/10/2025 | 19:57 | 0.0156 | 0 | 3 | 1605 | Unplanned | Lightning | Lightning damage
189 |  | INCD-265-N | Hampton Downs | Network | FINCB2 | 15/02/2026 | 08:29 | 15/02/2026 | 17:24 | 0.4688 | 0.0017 | 175 | 48124 | Planned | Planned | Mixed Asset Replacement
190 |  | INCD-1-M | Finlayson | Network | FINCB2 | 09/04/2025 | 08:42 | 09/04/2025 | 13:48 | 0.0309 | 0.0002 | 19 | 3176 | Planned | Planned | Mixed Asset Replacement
191 |  | INCD-441-M | Finlayson | Network | FINCB2 | 02/12/2025 | 09:35 | 02/12/2025 | 15:40 | 0.1329 | 0.0004 | 40 | 13639 | Planned | Planned | Pole Replacement
192 |  | INCD-7729-K | Finlayson Rd | Network | FINCB2 | 29/09/2025 | 20:06 | 30/09/2025 | 11:58 | 0.1896 | 0.0124 | 1270 | 19463 | Unplanned | Lightning | Lightning damage
193 |  | INCD-116-N | Finlayson Rd | Network | FINCB2 | 31/08/2025 | 08:04 | 31/08/2025 | 08:21 | 0.0104 | 0.0006 | 65 | 1072 | Unplanned | Vegetation | Tree blown ovr on line (OUT of Zone)
194 |  | INCD-9132-K | Finlayson | Network | FINCB2 | 20/11/2025 | 14:46 | 20/11/2025 | 17:00 | 0.0039 | 0 | 3 | 402 | Unplanned | Defective Equipment | Stay wire/ line clash
195 |  | INCD-111-N | Finlayson Rd | Network | FINCB2 | 31/08/2025 | 08:04 | 31/08/2025 | 08:18 | 0.0191 | 0.0014 | 145 | 1957 | Unplanned | Vegetation | Tree blown ovr on line (OUT of Zone)
196 |  | INCD-368-M | Finlayson | Network | FINCB2 | 21/10/2025 | 09:31 | 21/10/2025 | 12:25 | 0.0583 | 0.0005 | 55 | 5981 | Planned | Planned | Mixed Asset Replacement
197 |  | INCD-624-M | Finlayson Rd | Network | FINCB2 | 17/02/2026 | 08:51 | 17/02/2026 | 11:23 | 0.003 | 0 | 2 | 304 | Planned | Planned | New Connections
198 |  | INCD-386-M | Finlayson | Network | FINCB2 | 29/10/2025 | 09:13 | 29/10/2025 | 15:00 | 0.0302 | 0.0001 | 9 | 3099 | Planned | Planned | Mixed Asset Replacement
199 |  | INCD-640-M | Finlayson | Network | FINCB2 | 09/03/2026 | 09:05 | 09/03/2026 | 12:56 | 0.0203 | 0.0001 | 9 | 2079 | Planned | Planned | Pole Replacement
200 |  | INCD-7928-K | Finlayson Rd | Network | FINCB2 | 04/10/2025 | 10:25 | 04/10/2025 | 22:27 | 0.0352 | 0 | 5 | 3610 | Unplanned | Lightning | Lightning damage
201 |  | INCD-10727-K | Finlayson Rd | Network | FINCB2 | 16/01/2026 | 09:51 | 16/01/2026 | 14:04 | 0.0099 | 0 | 4 | 1012 | Unplanned | Unknown | All Ok - Fault cause not established
202 |  | INCD-10091-K | Finlayson Rd | Network | FINCB2 | 29/12/2025 | 13:40 | 29/12/2025 | 20:47 | 0.2204 | 0.0043 | 446 | 22620 | Unplanned | Vegetation | Wind debris on line (IN Zone)
203 |  | INCD-1434-L | Finlayson | Network | FINCB2 | 21/01/2026 | 08:35 | 21/01/2026 | 13:57 | 0.0251 | 0.0001 | 8 | 2576 | Planned | Planned | Transformer Upgrade
204 |  | INCD-1913-L | Finlayson Rd | Network | FINCB2 | 04/03/2026 | 09:10 | 04/03/2026 | 11:20 | 0.0051 | 0 | 4 | 520 | Planned | Planned | Conductor Replacement
205 |  | INCD-430-M | Finlayson | Network | FINCB2 | 14/11/2025 | 08:33 | 14/11/2025 | 16:10 | 0.2182 | 0.0008 | 82 | 22397 | Planned | Planned | Mixed Asset Replacement
206 |  | INCD-266-N | Finlayson | Network | FINCB2 | 27/02/2026 | 09:07 | 27/02/2026 | 13:47 | 0.0889 | 0.0003 | 35 | 9121 | Planned | Planned | Mixed Asset Replacement
207 |  | INCD-7020-K | Finlayson | Network | FINCB2 | 12/09/2025 | 09:02 | 12/09/2025 | 15:21 | 0.1145 | 0.0005 | 54 | 11756 | Planned | Planned | Mixed Asset Replacement
208 |  | INCD-306-M | Finlayson | Network | FINCB2 | 08/09/2025 | 09:51 | 08/09/2025 | 15:43 | 0.0171 | 0 | 5 | 1760 | Planned | Planned | Pole Replacement
209 |  | INCD-353-M | Finlayson | Network | FINCB2 | 08/10/2025 | 08:33 | 08/10/2025 | 17:02 | 0.2398 | 0.0008 | 82 | 24616 | Planned | Planned | Transformer Upgrade
210 |  | INCD-7723-K | Finlayson | Network | FINCB2 | 29/09/2025 | 16:05 | 29/09/2025 | 18:34 | 0.0087 | 0.0001 | 6 | 892 | Unplanned | Lightning | Lightning damage
211 |  | INCD-1686-K | Finlayson Rd | Network | FINCB2 | 23/04/2025 | 23:49 | 23/04/2025 | 23:51 | 0.0014 | 0.0043 | 442 | 146 | Unplanned | Unknown | All Ok - Fault cause not established
212 |  | INCD-496-M | Finlayson | Network | FINCB2 | 17/12/2025 | 09:16 | 17/12/2025 | 15:13 | 0.0304 | 0.0001 | 9 | 3117 | Planned | Planned | Mixed Asset Replacement
213 |  | INCD-12651-K | Finlayson Rd | Network | FINCB2 | 26/03/2026 | 06:17 | 26/03/2026 | 06:30 | 0.028 | 0.0043 | 446 | 2879 | Unplanned | Defective Equipment | Hairline crack
214 |  | INCD-11543-K | Finlayson Rd | Network | FINCB2 | 08/02/2026 | 04:34 | 08/02/2026 | 07:24 | 0.0017 | 0 | 1 | 170 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
215 |  | INCD-7089-K | Finlayson Rd | Network | FINCB2 | 13/09/2025 | 08:32 | 13/09/2025 | 10:06 | 0.0009 | 0 | 1 | 94 | Unplanned | Defective Equipment | Mechanism seized
216 |  | INCD-117-N | Finlayson Rd | Network | FINCB2 | 31/08/2025 | 08:04 | 31/08/2025 | 08:18 | 0.0098 | 0.0007 | 73 | 1004 | Unplanned | Vegetation | Tree blown ovr on line (OUT of Zone)
217 |  | INCD-7728-K | Finlayson | Network | FINCB2 | 29/09/2025 | 16:12 | 30/09/2025 | 13:42 | 0.0251 | 0 | 2 | 2579 | Unplanned | Lightning | Lightning damage
218 |  | INCD-4575-K | Finlayson Rd | Network | FINCB2 | 15/07/2025 | 11:14 | 15/07/2025 | 12:46 | 0.0036 | 0 | 4 | 368 | Unplanned | Defective Equipment | Split crossarm
219 |  | INCD-440-M | Finlayson | Network | FINCB2 | 03/12/2025 | 09:44 | 03/12/2025 | 14:45 | 0.078 | 0.0003 | 29 | 8004 | Planned | Planned | Crossarm Replacement
220 |  | INCD-7939-K | Finlayson | Network | FINCB2 | 04/10/2025 | 12:17 | 05/10/2025 | 14:28 | 0.0306 | 0 | 2 | 3142 | Unplanned | Lightning | Lightning damage
221 |  | INCD-2315-K | Te Kauwhata | Network | FINCB2 | 11/05/2025 | 07:54 | 11/05/2025 | 08:59 | 0.0963 | 0.0054 | 558 | 9881 | Unplanned | Unknown | All Ok - Fault cause not established
222 |  | INCD-488-M | Finlayson | Network | FINCB2 | 15/12/2025 | 09:42 | 15/12/2025 | 16:30 | 0.0159 | 0 | 4 | 1632 | Planned | Planned | Crossarm Replacement
223 |  | INCD-10946-K | Finlayson Rd | Network | FINCB2 | 21/01/2026 | 22:30 | 22/01/2026 | 01:01 | 0.138 | 0.0043 | 446 | 14164 | Unplanned | Vegetation | Wind debris on line (OUT of Zone)
224 |  | INCD-7754-K | Finlayson Rd | Network | FINCB2 | 30/09/2025 | 11:19 | 30/09/2025 | 15:11 | 0.0068 | 0 | 3 | 696 | Unplanned | Defective Equipment | Jumpers come off
225 |  | INCD-232-M | Finlayson | Network | FINCB2 | 12/08/2025 | 09:45 | 12/08/2025 | 16:14 | 0.0076 | 0 | 2 | 778 | Planned | Planned | Transformer Upgrade
226 |  | INCD-2628-K | Finlayson Rd | Network | FINCB2 | 20/05/2025 | 06:52 | 20/05/2025 | 08:55 | 0.0251 | 0.0002 | 21 | 2577 | Unplanned | Unknown | All Ok - Fault cause not established
227 |  | INCD-11389-K | Finlayson Rd | Network | FINCB2 | 02/02/2026 | 09:16 | 03/02/2026 | 13:19 | 0.0164 | 0 | 1 | 1683 | Planned | Planned | Pole Replacement
228 |  | INCD-7945-K | Finlayson Rd | Network | FINCB2 | 04/10/2025 | 11:41 | 04/10/2025 | 15:00 | 0.0078 | 0 | 4 | 796 | Unplanned | Lightning | Lightning damage
229 |  | INCD-8292-K | Finlayson | Network | FINCB2 | 18/10/2025 | 12:41 | 18/10/2025 | 14:41 | 0.0356 | 0.0003 | 32 | 3656 | Unplanned | Defective Equipment | Faulty joint/connection
230 |  | INCD-12813-K | Finlayson Rd | Network | FINCB2 | 31/03/2026 | 11:54 | 31/03/2026 | 13:01 | 0.0855 | 0.0043 | 446 | 8774 | Unplanned | Unknown | All Ok - Fault cause not established
231 |  | INCD-115-N | Finlayson Rd | Network | FINCB2 | 31/08/2025 | 08:04 | 31/08/2025 | 08:14 | 0.0205 | 0.0022 | 226 | 2102 | Unplanned | Vegetation | Tree blown ovr on line (OUT of Zone)
232 |  | INCD-12652-K | Finlayson Rd | Network | FINCB2 | 26/03/2026 | 07:05 | 26/03/2026 | 13:44 | 0.1876 | 0.0083 | 852 | 19256 | Unplanned | Defective Equipment | Hairline crack
233 |  | INCD-348-M | Finlayson | Network | FINCB2 | 17/10/2025 | 09:45 | 17/10/2025 | 12:30 | 0.0048 | 0 | 3 | 495 | Planned | Planned | Crossarm Replacement
234 |  | INCD-4462-K | Finlayson Rd | Network | FINCB2 | 11/07/2025 | 14:24 | 12/07/2025 | 06:32 | 0.6121 | 0.0043 | 442 | 62823 | Unplanned | Third_party | Car in contact with pole
235 |  | INCD-7921-K | Te Kauwhata | Network | FINCB2 | 04/10/2025 | 08:21 | 04/10/2025 | 10:03 | 0.0961 | 0.0055 | 564 | 9862 | Unplanned | Lightning | Lightning strike surge
236 |  | INCD-10758-K | Finlayson Rd | Private | FINCB2 | 17/01/2026 | 13:08 | 17/01/2026 | 14:46 | 0.0048 | 0 | 5 | 490 | Unplanned | Defective Equipment | LVC - WEL & Customer
237 |  | INCD-113-N | Finlayson Rd | Network | FINCB2 | 31/08/2025 | 08:04 | 31/08/2025 | 11:09 | 0.0523 | 0.0003 | 29 | 5366 | Unplanned | Vegetation | Tree blown ovr on line (OUT of Zone)
238 |  | INCD-346-M | Finlayson | Network | FINCB2 | 17/10/2025 | 09:40 | 17/10/2025 | 11:12 | 0.0018 | 0 | 2 | 184 | Planned | Planned | New Connections
239 |  | INCD-268-M | Finlayson | Network | FINCB2 | 26/08/2025 | 08:34 | 26/08/2025 | 14:34 | 0.0225 | 0.0012 | 125 | 2305 | Planned | Planned | New Connections
240 |  | INCD-569-M | Finlayson | Network | FINCB2 | 28/01/2026 | 09:37 | 28/01/2026 | 18:02 | 0.1408 | 0.0003 | 32 | 14452 | Planned | Planned | Mixed Asset Replacement
241 |  | INCD-10300-K | Finlayson Rd | Network | FINCB2 | 03/01/2026 | 17:10 | 03/01/2026 | 19:27 | 0.0067 | 0 | 5 | 685 | Unplanned | Lightning | Lightning damage
242 |  | INCD-507-M | Finlayson | Network | FINCB2 | 12/12/2025 | 10:18 | 12/12/2025 | 17:00 | 0.179 | 0.0005 | 48 | 18374 | Planned | Planned | Mixed Asset Replacement
243 |  | INCD-7940-K | Finlayson | Network | FINCB2 | 04/10/2025 | 12:46 | 04/10/2025 | 16:33 | 0.0022 | 0 | 1 | 227 | Unplanned | Lightning | Lightning damage
244 |  | INCD-11083-K | Finlayson Rd | Network | FINCB2 | 23/01/2026 | 19:38 | 23/01/2026 | 19:57 | 0.0397 | 0.0043 | 446 | 4078 | Unplanned | Unknown | All Ok - Fault cause not established
245 |  | INCD-4083-K | Finlayson | Network | FINCB2 | 02/07/2025 | 00:10 | 02/07/2025 | 00:14 | 0.0098 | 0.0022 | 225 | 1001 | Unplanned | Defective Equipment | Loose connection
246 |  | INCD-1765-L | Finlayson Rd | Network | FINCB3 | 16/01/2026 | 10:04 | 16/01/2026 | 10:21 | 0.0005 | 0 | 3 | 51 | Unplanned | Lightning | Lightning damage
247 |  | INCD-527-M | Finlayson | Network | FINCB3 | 16/01/2026 | 09:38 | 16/01/2026 | 14:06 | 0.1471 | 0.0006 | 60 | 15100 | Planned | Planned | Mixed Asset Replacement
248 |  | INCD-7921-K | Te Kauwhata | Network | FINCB3 | 04/10/2025 | 08:21 | 04/10/2025 | 10:03 | 0.037 | 0.0012 | 127 | 3799 | Unplanned | Lightning | Lightning strike surge
249 |  | INCD-2315-K | Te Kauwhata | Network | FINCB3 | 11/05/2025 | 07:54 | 11/05/2025 | 08:59 | 0.0299 | 0.0012 | 127 | 3071 | Unplanned | Unknown | All Ok - Fault cause not established
250 |  | INCD-336-M | Finlayson | Network | FINCB3 | 15/10/2025 | 09:34 | 15/10/2025 | 15:01 | 0.0643 | 0.0002 | 21 | 6599 | Planned | Planned | Mixed Asset Replacement
251 |  | INCD-280-M | Finlayson | Network | FINCB3 | 05/09/2025 | 09:40 | 05/09/2025 | 15:20 | 0.0132 | 0 | 4 | 1360 | Planned | Planned | Crossarm Replacement
252 |  | INCD-1764-L | Finlayson Rd | Network | FINCB3 | 18/01/2026 | 21:42 | 18/01/2026 | 23:13 | 0.0027 | 0 | 3 | 273 | Unplanned | Defective Equipment | Fuse blown on overload
253 |  | INCD-2245-L | Finlayson Rd | Network | FINCB3 | 20/03/2026 | 07:36 | 20/03/2026 | 09:56 | 0.0041 | 0 | 3 | 420 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
254 |  | INCD-3069-K | Finlayson Rd | Network | FINCB3 | 30/05/2025 | 01:35 | 30/05/2025 | 04:01 | 0.002 | 0.0025 | 254 | 210 | Unplanned | Unknown | All Ok - Fault cause not established
255 |  | INCD-520-M | Finlayson | Network | FINCB3 | 14/12/2025 | 09:05 | 14/12/2025 | 22:14 | 0.0676 | 0.0001 | 9 | 6939 | Planned | Planned | New Connections
256 |  | INCD-5897-K | Finlayson Rd | Network | FINCB4 | 18/08/2025 | 09:05 | 18/08/2025 | 11:18 | 0.0052 | 0 | 4 | 532 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
257 |  | INCD-8868-K | Finlayson Rd | Network | FINCB4 | 13/11/2025 | 09:51 | 13/11/2025 | 12:58 | 0.0073 | 0 | 4 | 745 | Unplanned | Unknown | All Ok - Fault cause not established
258 |  | INCD-541-M | Finlayson | Network | FINCB4 | 28/01/2026 | 08:31 | 28/01/2026 | 12:32 | 0.0141 | 0.0001 | 6 | 1446 | Planned | Planned | New Connections
259 |  | INCD-9637-K | Finlayson | Network | FINCB4 | 11/12/2025 | 10:14 | 11/12/2025 | 11:25 | 0.0007 | 0 | 1 | 71 | Planned | Planned | New Connections
260 |  | INCD-251-N | Finlayson Rd | Network | FINCB4 | 14/12/2025 | 12:48 | 14/12/2025 | 15:21 | 0.0015 | 0 | 1 | 153 | Unplanned | Human error | Settings Incorrect
261 |  | INCD-8380-K | Finlayson Rd | Network | FINCB4 | 22/10/2025 | 18:45 | 22/10/2025 | 21:38 | 0.0067 | 0 | 4 | 692 | Unplanned | Unknown | All Ok - Fault cause not established
262 |  | INCD-2315-K | Te Kauwhata | Network | FINCB4 | 11/05/2025 | 07:54 | 11/05/2025 | 08:59 | 0.0322 | 0.0012 | 123 | 3306 | Unplanned | Unknown | All Ok - Fault cause not established
263 |  | INCD-520-M | Finlayson | Network | FINCB4 | 14/12/2025 | 09:05 | 14/12/2025 | 22:14 | 0.0071 | 0 | 1 | 725 | Planned | Planned | New Connections
264 |  | INCD-9486-K | Finlayson Rd | Network | FINCB4 | 08/12/2025 | 06:56 | 08/12/2025 | 08:16 | 0.0008 | 0 | 1 | 79 | Planned | Planned | OTHER Maintenance
265 |  | INCD-1694-L | Finlayson | Network | FINCB4 | 10/01/2026 | 09:39 | 10/01/2026 | 11:17 | 0.0286 | 0.0003 | 30 | 2940 | Unplanned | Defective Equipment | Broken binder
266 |  | INCD-5627-K | Finlayson Rd | Network | FINCB4 | 11/08/2025 | 10:03 | 11/08/2025 | 12:24 | 0.0055 | 0 | 4 | 564 | Unplanned | Unknown | All Ok - Fault cause not established
267 |  | INCD-10420-K | Finlayson | Network | FINCB4 | 08/01/2026 | 12:27 | 09/01/2026 | 14:55 | 0.0359 | 0.0003 | 30 | 3690 | Unplanned | Defective Equipment | Nut or bolt loose
268 |  | INCD-8354-K | Finlayson | Network | FINCB4 | 21/10/2025 | 12:33 | 21/10/2025 | 17:20 | 0.014 | 0 | 5 | 1435 | Unplanned | Unknown | All Ok - Fault cause not established
269 |  | INCD-1709-L | Finlayson | Network | FINCB4 | 14/01/2026 | 15:20 | 15/01/2026 | 03:09 | 0.0019 | 0.0002 | 19 | 199 | Unplanned | Vegetation | Wind debris on line (IN Zone)
270 |  | INCD-1706-L | Finlayson | Network | FINCB4 | 14/01/2026 | 15:20 | 14/01/2026 | 16:23 | 0.0502 | 0.0012 | 122 | 5151 | Unplanned | Vegetation | Wind debris on line (IN Zone)
271 |  | INCD-1763-L | Finlason | Network | FINCB4 | 16/01/2026 | 11:20 | 16/01/2026 | 12:04 | 0.0017 | 0 | 4 | 176 | Unplanned | Unknown | All Ok - Fault cause not established
272 |  | INCD-3069-K | Finlayson Rd | Network | FINCB4 | 30/05/2025 | 01:35 | 30/05/2025 | 04:01 | 0.1348 | 0.0024 | 244 | 13833 | Unplanned | Unknown | All Ok - Fault cause not established
273 |  | INCD-9979-K | Finlayson | Network | FINCB4 | 22/12/2025 | 08:00 | 22/12/2025 | 11:50 | 0.0022 | 0 | 1 | 230 | Planned | Planned | OTHER Maintenance
274 |  | INCD-8213-K | Finlayson | Network | FINCB4 | 14/10/2025 | 20:36 | 14/10/2025 | 21:23 | 0.0023 | 0 | 5 | 235 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
275 |  | INCD-394-M | Finlayson | Network | FINCB4 | 05/11/2025 | 09:17 | 05/11/2025 | 11:29 | 0.0129 | 0.0001 | 10 | 1320 | Planned | Planned | Crossarm Replacement
276 |  | INCD-516-M | Finlayson | Network | FINCB4 | 07/01/2026 | 09:31 | 07/01/2026 | 13:44 | 0.0431 | 0.0002 | 19 | 4420 | Planned | Planned | Crossarm Replacement
277 |  | INCD-7921-K | Te Kauwhata | Network | FINCB4 | 04/10/2025 | 08:21 | 04/10/2025 | 10:03 | 0.0193 | 0.0012 | 123 | 1982 | Unplanned | Lightning | Lightning strike surge
278 |  | INCD-3103-E | Foreman | Network | FORCB3 | 05/04/2025 | 07:08 | 05/04/2025 | 14:12 | 0.0041 | 0 | 1 | 424 | Planned | Planned | OTHER Maintenance
279 |  | INCD-680-M | Foreaman Rd | Network | FORCB4 | 28/03/2026 | 08:22 | 28/03/2026 | 15:01 | 0.0078 | 0 | 2 | 798 | Planned | Planned | OTHER Maintenance
280 |  | INCD-12234-K | Glasgow | Network | GLACB1 | 06/03/2026 | 06:27 | 06/03/2026 | 09:07 | 0.0016 | 0 | 1 | 160 | Unplanned | Unknown | All Ok - Fault cause not established
281 |  | INCD-571-M | Glasgow | Network | GLACB1 | 16/01/2026 | 08:34 | 16/01/2026 | 11:23 | 0.0181 | 0.0001 | 11 | 1859 | Planned | Planned | Distribution Transformer Replacement
282 |  | INCD-649-M | Glasgow | Network | GLACB1 | 04/03/2026 | 08:35 | 04/03/2026 | 10:20 | 0.0015 | 0.0008 | 79 | 158 | Planned | Planned | Mixed Asset Replacement
283 |  | INCD-1746-K | Weavers | Network | GLACB1 | 26/04/2025 | 16:02 | 26/04/2025 | 16:32 | 0.1791 | 0.007 | 721 | 18387 | Unplanned | Third_party | Car in contact with pole
284 |  | INCD-318-M | Glasgow | Network | GLACB1 | 15/09/2025 | 09:50 | 15/09/2025 | 16:30 | 0.0195 | 0 | 5 | 2000 | Planned | Planned | Mixed Asset Replacement
285 |  | INCD-55-M | Glasgow | Network | GLACB1 | 16/05/2025 | 09:09 | 16/05/2025 | 11:55 | 0.0016 | 0 | 1 | 166 | Planned | Planned | Crossarm Replacement
286 |  | INCD-3943-K | Glasgow | Network | GLACB1 | 26/06/2025 | 08:40 | 26/06/2025 | 12:28 | 0.0044 | 0 | 2 | 456 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
287 |  | INCD-312-M | Glasgow | Network | GLACB1 | 11/09/2025 | 08:34 | 11/09/2025 | 13:58 | 0.0032 | 0 | 1 | 324 | Planned | Planned | Mixed Asset Replacement
288 |  | INCD-7439-K | Glasgow St | Network | GLACB1 | 21/09/2025 | 09:43 | 21/09/2025 | 10:29 | 0.3215 | 0.007 | 721 | 32998 | Unplanned | Third_party | Object thrown on line
289 |  | INCD-575-M | Glasgow | Network | GLACB1 | 05/02/2026 | 09:41 | 05/02/2026 | 15:14 | 0.028 | 0.0001 | 9 | 2873 | Planned | Planned | ABS Replacement
290 |  | INCD-12235-K | Glasgow | Network | GLACB1 | 06/03/2026 | 08:09 | 06/03/2026 | 10:37 | 0.0101 | 0.0001 | 7 | 1033 | Unplanned | Unknown | All Ok - Fault cause not established
291 |  | INCD-8551-K | Glasgow St | Network | GLACB2 | 30/10/2025 | 20:52 | 30/10/2025 | 22:59 | 0.0308 | 0.0002 | 25 | 3160 | Unplanned | Unknown | All Ok - Fault cause not established
292 |  | INCD-119-M | Glasgow | Network | GLACB2 | 17/06/2025 | 09:44 | 17/06/2025 | 15:52 | 0.0906 | 0.0003 | 26 | 9302 | Planned | Planned | Mixed Asset Replacement
293 |  | INCD-129-M | Glasgow | Network | GLACB2 | 25/06/2025 | 10:09 | 25/06/2025 | 14:26 | 0.0526 | 0.0002 | 24 | 5397 | Planned | Planned | Crossarm Replacement
294 |  | INCD-526-M | Glasgow St | Network | GLACB2 | 20/01/2026 | 09:31 | 20/01/2026 | 17:06 | 0.0089 | 0 | 2 | 911 | Planned | Planned | Crossarm Replacement
295 |  | INCD-8305-K | Glasgow St | Network | GLACB2 | 19/10/2025 | 08:47 | 19/10/2025 | 10:28 | 0.0039 | 0 | 4 | 404 | Unplanned | Unknown | All Ok - Fault cause not established
296 |  | INCD-68-M | Glasgow | Network | GLACB2 | 04/06/2025 | 09:10 | 04/06/2025 | 13:19 | 0.0291 | 0.0001 | 12 | 2988 | Planned | Planned | OTHER Maintenance
297 |  | INCD-6128-K | Glasgow St | Network | GLACB2 | 24/08/2025 | 08:36 | 24/08/2025 | 10:45 | 0.0025 | 0 | 2 | 258 | Unplanned | Defective Equipment | Wear or shear of pins
298 |  | INCD-419-M | Glasgow | Network | GLACB2 | 28/11/2025 | 10:08 | 28/11/2025 | 13:16 | 0.011 | 0.0001 | 6 | 1128 | Planned | Planned | Crossarm Replacement
299 |  | INCD-9246-K | Glasgow | Network | GLACB2 | 26/11/2025 | 05:41 | 26/11/2025 | 07:58 | 0.008 | 0.0001 | 6 | 822 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
300 |  | INCD-140-M | Glasgow | Network | GLACB2 | 04/07/2025 | 09:49 | 04/07/2025 | 15:43 | 0.1444 | 0.0004 | 44 | 14818 | Planned | Planned | Crossarm Replacement
301 |  | INCD-5386-K | Glasgow St | Network | GLACB2 | 05/08/2025 | 09:38 | 05/08/2025 | 16:05 | 0.6519 | 0.002 | 208 | 66917 | Planned | Planned | Mixed Asset Replacement
302 |  | INCD-110-M | Glasgow | Network | GLACB2 | 03/06/2025 | 08:33 | 03/06/2025 | 12:29 | 0.0184 | 0.0001 | 8 | 1888 | Planned | Planned | OTHER Maintenance
303 |  | INCD-425-M | Glasgow | Network | GLACB2 | 17/11/2025 | 09:30 | 17/11/2025 | 13:11 | 0.1094 | 0.0005 | 56 | 11229 | Planned | Planned | Crossarm Replacement
304 |  | INCD-97-M | Glasgow | Network | GLACB2 | 04/06/2025 | 10:05 | 04/06/2025 | 13:33 | 0.0101 | 0 | 5 | 1040 | Planned | Planned | Pole Replacement
305 |  | INCD-169-M | Glasgow | Network | GLACB2 | 18/07/2025 | 09:06 | 18/07/2025 | 10:58 | 0.0022 | 0 | 2 | 224 | Planned | Planned | Mixed Asset Replacement
306 |  | INCD-8222-K | Glasgow St | Network | GLACB2 | 15/10/2025 | 07:32 | 15/10/2025 | 09:09 | 0.0019 | 0 | 2 | 194 | Unplanned | Unknown | All Ok - Fault cause not established
307 |  | INCD-1746-K | Weavers | Network | GLACB2 | 26/04/2025 | 16:02 | 26/04/2025 | 16:32 | 0.1915 | 0.0065 | 672 | 19657 | Unplanned | Third_party | Car in contact with pole
308 |  | INCD-513-L | Glasgow | Network | GLACB2 | 17/08/2025 | 14:37 | 17/08/2025 | 17:35 | 0.0017 | 0 | 1 | 178 | Unplanned | Unknown | All Ok - Fault cause not established
309 |  | INCD-3432-K | Glasgow | Network | GLACB2 | 09/06/2025 | 18:55 | 09/06/2025 | 22:42 | 0.0022 | 0 | 1 | 227 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
310 |  | INCD-691-M | Glasgow | Network | GLACB2 | 31/03/2026 | 09:31 | 31/03/2026 | 16:29 | 0.008 | 0 | 2 | 821 | Planned | Planned | Mixed Asset Replacement
311 |  | INCD-3852-K | Glasgow St | Network | GLACB2 | 19/06/2025 | 10:10 | 19/06/2025 | 15:12 | 0.0235 | 0.0001 | 8 | 2416 | Planned | Planned | Mixed Asset Replacement
312 |  | INCD-9087-K | Glasgow St | Network | GLACB2 | 19/11/2025 | 14:14 | 19/11/2025 | 16:41 | 0.0029 | 0 | 2 | 294 | Unplanned | Unknown | All Ok - Fault cause not established
313 |  | INCD-202-M | Glasgow | Network | GLACB2 | 23/07/2025 | 09:05 | 23/07/2025 | 14:59 | 0.0124 | 0 | 4 | 1272 | Planned | Planned | Crossarm Replacement
314 |  | INCD-352-M | Glasgow | Network | GLACB2 | 09/09/2025 | 09:18 | 09/09/2025 | 12:41 | 0.0336 | 0.0002 | 17 | 3451 | Planned | Planned | OTHER Maintenance
315 |  | INCD-7765-K | Glasgow St | Network | GLACB2 | 24/09/2025 | 11:17 | 24/09/2025 | 11:41 | 0.0049 | 0.0002 | 21 | 504 | Unplanned | Defective Equipment | Overheated connections
316 |  | INCD-228-M | Glasgow | Network | GLACB2 | 23/09/2025 | 09:13 | 23/09/2025 | 18:05 | 0.4974 | 0.001 | 100 | 51055 | Planned | Planned | ABS Replacement
317 |  | INCD-693-L | Glasgow | Network | GLACB2 | 07/10/2025 | 17:27 | 07/10/2025 | 20:26 | 0.0035 | 0 | 2 | 358 | Unplanned | Vegetation | Wind debris on line (OUT of Zone)
318 |  | INCD-158-M | Glasgow | Network | GLACB2 | 10/07/2025 | 10:08 | 10/07/2025 | 16:42 | 0.0368 | 0.0001 | 10 | 3780 | Planned | Planned | Distribution Transformer Replacement
319 |  | INCD-2287-K | Glasgow St | Network | GLACB2 | 10/05/2025 | 05:01 | 10/05/2025 | 06:35 | 0.0009 | 0 | 1 | 94 | Unplanned | Unknown | All Ok - Fault cause not established
320 |  | INCD-9376-K | Glasgow St | Network | GLACB2 | 03/12/2025 | 18:18 | 03/12/2025 | 19:57 | 0.0077 | 0.0001 | 8 | 792 | Unplanned | Unknown | All Ok - Fault cause not established
321 |  | INCD-4198-K | Glasgow St | Network | GLACB2 | 05/07/2025 | 08:16 | 05/07/2025 | 11:31 | 0.0779 | 0.0004 | 41 | 7995 | Unplanned | Defective Equipment | Connect/jumper loose
322 |  | INCD-60-M | Glasgow | Network | GLACB2 | 26/06/2025 | 08:39 | 26/06/2025 | 14:55 | 0.2235 | 0.0006 | 62 | 22940 | Planned | Planned | ABS Replacement
323 |  | INCD-8907-K | Glasgow St | Network | GLACB2 | 14/11/2025 | 09:45 | 14/11/2025 | 11:01 | 0.0015 | 0 | 2 | 152 | Unplanned | Defective Equipment | Nut or bolt loose
324 |  | INCD-9316-K | Glasgow | Network | GLACB2 | 30/11/2025 | 21:30 | 30/11/2025 | 23:13 | 0.003 | 0 | 3 | 309 | Unplanned | Unknown | All Ok - Fault cause not established
325 |  | INCD-3709-K | Glasgow St | Network | GLACB2 | 16/06/2025 | 10:04 | 16/06/2025 | 13:48 | 0.0175 | 0.0001 | 8 | 1792 | Planned | Planned | Mixed Asset Replacement
326 |  | INCD-1746-K | Weavers | Network | GLACB5 | 26/04/2025 | 16:02 | 26/04/2025 | 16:32 | 0.0743 | 0.0027 | 281 | 7629 | Unplanned | Third_party | Car in contact with pole
327 |  | INCD-677-M | Glasgow | Network | GLACB5 | 19/03/2026 | 08:30 | 19/03/2026 | 13:22 | 0.2552 | 0.0009 | 94 | 26194 | Planned | Planned | ABS Replacement
328 |  | INCD-60-M | Glasgow | Network | GLACB5 | 26/06/2025 | 08:39 | 26/06/2025 | 14:55 | 0.1262 | 0.0004 | 37 | 12950 | Planned | Planned | ABS Replacement
329 |  | INCD-12603-K | Glasgow St | Network | GLACB5 | 22/03/2026 | 17:28 | 23/03/2026 | 00:58 | 0.2175 | 0.001 | 101 | 22325 | Unplanned | Lightning | Spontaneous failure
330 |  | INCD-138-M | Glasgow | Network | GLACB6 | 04/07/2025 | 09:07 | 04/07/2025 | 13:40 | 0.1144 | 0.0004 | 43 | 11739 | Planned | Planned | Crossarm Replacement
331 |  | INCD-315-M | Glasgow | Network | GLACB6 | 16/09/2025 | 09:40 | 16/09/2025 | 16:14 | 0.1464 | 0.0004 | 39 | 15024 | Planned | Planned | Crossarm Replacement
332 |  | INCD-951-L | Glasgow St | Network | GLACB6 | 17/10/2025 | 07:50 | 17/10/2025 | 09:14 | 0.009 | 0.0001 | 11 | 924 | Unplanned | Unknown | All Ok - Fault cause not established
333 |  | INCD-649-M | Glasgow | Network | GLACB6 | 04/03/2026 | 08:35 | 04/03/2026 | 10:20 | 0.188 | 0.0018 | 183 | 19297 | Planned | Planned | Mixed Asset Replacement
334 |  | INCD-1746-K | Weavers | Network | GLACB6 | 26/04/2025 | 16:02 | 26/04/2025 | 16:32 | 0.2294 | 0.0087 | 888 | 23547 | Unplanned | Third_party | Car in contact with pole
335 |  | INCD-716-M | Glasgow | Network | GLACB6 | 25/03/2026 | 08:31 | 25/03/2026 | 14:15 | 0.6133 | 0.0018 | 183 | 62952 | Planned | Planned | Mixed Asset Replacement
336 |  | INCD-8217-K | Glasgow St | Network | GLACB6 | 15/10/2025 | 05:18 | 15/10/2025 | 06:48 | 0.0228 | 0.0003 | 26 | 2340 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
337 |  | INCD-4762-K | Glasgow St | Network | GLACB6 | 19/07/2025 | 18:14 | 19/07/2025 | 20:12 | 0.0126 | 0.0001 | 11 | 1292 | Unplanned | Unknown | All Ok - Fault cause not established
338 |  | INCD-9761-K | Glasgow St | Network | GLACB6 | 16/12/2025 | 06:56 | 16/12/2025 | 11:01 | 0.0024 | 0 | 1 | 245 | Unplanned | Defective Equipment | Faulty joint/connection
339 |  | INCD-389-M | Glasgow | Network | GLACB6 | 02/11/2025 | 08:09 | 02/11/2025 | 13:42 | 0.0496 | 0.001 | 104 | 5096 | Planned | Planned | OTHER Maintenance
340 |  | INCD-209-M | Glasgow | Network | GLACB6 | 22/07/2025 | 08:32 | 22/07/2025 | 14:08 | 0.0825 | 0.0003 | 26 | 8472 | Planned | Planned | Crossarm Replacement
341 |  | INCD-1746-K | Weavers | Network | GLACB7 | 26/04/2025 | 16:02 | 26/04/2025 | 16:32 | 0.0185 | 0.0009 | 89 | 1896 | Unplanned | Third_party | Car in contact with pole
342 |  | INCD-11366-K | Glasgow St | Network | GLACB7 | 01/02/2026 | 08:00 | 01/02/2026 | 14:51 | 0.3519 | 0.0009 | 88 | 36125 | Planned | Planned | OTHER Maintenance
343 |  | INCD-1746-K | Weavers | Network | GLACB8 | 26/04/2025 | 16:02 | 26/04/2025 | 16:32 | 0.0131 | 0.0005 | 48 | 1342 | Unplanned | Third_party | Car in contact with pole
344 |  | INCD-10873-K | Gordonton | Network | GORCB11 | 20/01/2026 | 20:35 | 21/01/2026 | 03:14 | 0.7018 | 0.0018 | 185 | 72036 | Unplanned | Third_party | Car in contact with pole
345 |  | INCD-5969-K | Horotiu | Network | GORCB11 | 19/08/2025 | 20:17 | 19/08/2025 | 20:52 | 0.1482 | 0.0056 | 579 | 15210 | Unplanned | Lightning | Lightning damage
346 |  | INCD-7764-K | Gordonton | Network | GORCB11 | 22/09/2025 | 09:06 | 22/09/2025 | 11:48 | 0.0142 | 0.0001 | 9 | 1458 | Planned | Planned | Crossarm Replacement
347 |  | INCD-6410-K | Horotiu | Network | GORCB11 | 31/08/2025 | 18:22 | 31/08/2025 | 18:41 | 0.101 | 0.0056 | 579 | 10364 | Unplanned | Defective Equipment | Broken binder
348 |  | INCD-3132-K | Gordonton | Network | GORCB11 | 31/05/2025 | 13:59 | 31/05/2025 | 15:13 | 0.0022 | 0 | 3 | 222 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
349 |  | INCD-8888-K | Gordonton | Network | GORCB11 | 13/11/2025 | 20:37 | 13/11/2025 | 23:23 | 0.0049 | 0 | 3 | 498 | Unplanned | Unknown | All Ok - Fault cause not established
350 |  | INCD-3864-K | Gordonton | Network | GORCB11 | 19/06/2025 | 16:39 | 19/06/2025 | 22:52 | 0.1547 | 0.0007 | 76 | 15874 | Unplanned | Defective Equipment | Mechanism seized
351 |  | INCD-10173-K | Gordonton | Network | GORCB11 | 30/12/2025 | 07:53 | 30/12/2025 | 12:35 | 0.011 | 0 | 4 | 1127 | Unplanned | Adverse weather | Line clash high wind
352 |  | INCD-9178-K | Gordonton | Network | GORCB11 | 22/11/2025 | 09:14 | 22/11/2025 | 09:38 | 0.0021 | 0.0001 | 9 | 216 | Unplanned | Unknown | All Ok - Fault cause not established
353 |  | INCD-506-M | Gordonton | Network | GORCB11 | 18/12/2025 | 09:10 | 18/12/2025 | 11:41 | 0.0132 | 0.0001 | 9 | 1359 | Planned | Planned | Mixed Asset Replacement
354 |  | INCD-6943-K | Gordonton | Network | GORCB11 | 10/09/2025 | 09:33 | 10/09/2025 | 15:23 | 0.2334 | 0.0017 | 174 | 23956 | Planned | Planned | Mixed Asset Replacement
355 |  | INCD-11744-K | Gordonton | Network | GORCB11 | 14/02/2026 | 13:02 | 14/02/2026 | 19:03 | 0.6512 | 0.0018 | 185 | 66837 | Unplanned | Third_party | Car in contact with pole
356 |  | INCD-7766-K | Gordonton | Network | GORCB11 | 22/09/2025 | 09:06 | 22/09/2025 | 11:48 | 0.0521 | 0.0003 | 33 | 5346 | Planned | Planned | Crossarm Replacement
357 |  | INCD-461-M | Gordonton | Network | GORCB11 | 11/12/2025 | 08:49 | 11/12/2025 | 16:49 | 1.1024 | 0.0024 | 248 | 113153 | Planned | Planned | Mixed Asset Replacement
358 |  | INCD-202-M | Glasgow | Network | GORCB11 | 23/07/2025 | 09:05 | 23/07/2025 | 14:59 | 0.1625 | 0.0005 | 49 | 16675 | Planned | Planned | Crossarm Replacement
359 |  | INCD-12309-K | Gordonton | Network | GORCB11 | 11/03/2026 | 04:19 | 11/03/2026 | 04:23 | 0.0082 | 0.0018 | 186 | 837 | Unplanned | Defective Equipment | Flickers misaligned
360 |  | INCD-443-M | Gordonton | Network | GORCB11 | 05/12/2025 | 09:49 | 05/12/2025 | 15:18 | 0.343 | 0.001 | 107 | 35203 | Planned | Planned | Pole Replacement
361 |  | INCD-4670-K | Gordonton | Network | GORCB11 | 17/07/2025 | 10:30 | 17/07/2025 | 16:11 | 0.0813 | 0.0047 | 486 | 8343 | Unplanned | Defective Equipment | Split crossarm
362 |  | INCD-224-M | Gordonton | Network | GORCB11 | 11/08/2025 | 08:34 | 11/08/2025 | 13:11 | 0.0678 | 0.0003 | 26 | 6960 | Planned | Planned | Mixed Asset Replacement
363 |  | INCD-8959-K | Gordonton | Network | GORCB11 | 16/11/2025 | 11:39 | 16/11/2025 | 18:11 | 0.0251 | 0.0002 | 21 | 2572 | Unplanned | Defective Equipment | Mechanism seized
364 |  | INCD-9008-K | Gordonton | Network | GORCB11 | 17/11/2025 | 19:54 | 17/11/2025 | 21:48 | 0.0011 | 0 | 1 | 114 | Unplanned | Unknown | All Ok - Fault cause not established
365 |  | INCD-3112-E | Gordonton | Network | GORCB11 | 04/04/2025 | 09:15 | 04/04/2025 | 12:05 | 0.0386 | 0.0003 | 27 | 3966 | Planned | Planned | Crossarm Replacement
366 |  | INCD-9150-K | Gordonton | Network | GORCB12 | 21/11/2025 | 07:57 | 21/11/2025 | 09:34 | 0.0028 | 0 | 3 | 291 | Unplanned | Unknown | All Ok - Fault cause not established
367 |  | INCD-6441-K | Gordonton | Network | GORCB12 | 31/08/2025 | 19:19 | 31/08/2025 | 23:48 | 0.0209 | 0.0001 | 8 | 2146 | Unplanned | Adverse weather | Line clash high wind
368 |  | INCD-278-M | Goedonton | Network | GORCB12 | 05/09/2025 | 09:49 | 05/09/2025 | 15:38 | 0.0374 | 0.0001 | 11 | 3839 | Planned | Planned | Crossarm Replacement
369 |  | INCD-87-M | Gordonton | Network | GORCB12 | 28/05/2025 | 10:01 | 28/05/2025 | 16:44 | 0.206 | 0.0005 | 54 | 21146 | Planned | Planned | Mixed Asset Replacement
370 |  | INCD-300-M | Gordonton | Network | GORCB12 | 08/09/2025 | 09:42 | 08/09/2025 | 12:10 | 0.0216 | 0.0001 | 15 | 2220 | Planned | Planned | Crossarm Replacement
371 |  | INCD-9295-K | Gordonton | Network | GORCB12 | 28/11/2025 | 16:35 | 28/11/2025 | 18:55 | 0.0014 | 0 | 1 | 140 | Unplanned | Unknown | All Ok - Fault cause not established
372 |  | INCD-7807-K | Gordonton | Network | GORCB12 | 02/10/2025 | 07:15 | 02/10/2025 | 12:44 | 0.1222 | 0.0007 | 74 | 12543 | Unplanned | Third_party | Car in contact with pole
373 |  | INCD-5969-K | Horotiu | Network | GORCB12 | 19/08/2025 | 20:17 | 19/08/2025 | 20:52 | 0.1463 | 0.0047 | 478 | 15012 | Unplanned | Lightning | Lightning damage
374 |  | INCD-5691-K | Gordonton | Network | GORCB12 | 13/08/2025 | 05:11 | 13/08/2025 | 06:30 | 0.0008 | 0 | 1 | 79 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
375 |  | INCD-435-M | Gordonton | Network | GORCB12 | 02/12/2025 | 09:16 | 02/12/2025 | 14:40 | 0.1862 | 0.0006 | 59 | 19116 | Planned | Planned | Crossarm Replacement
376 |  | INCD-7644-K | Gordonton | Network | GORCB12 | 26/09/2025 | 09:40 | 26/09/2025 | 15:24 | 0.116 | 0.0007 | 74 | 11902 | Planned | Planned | Mixed Asset Replacement
377 |  | INCD-6410-K | Horotiu | Network | GORCB12 | 31/08/2025 | 18:22 | 31/08/2025 | 18:41 | 0.081 | 0.0047 | 478 | 8309 | Unplanned | Defective Equipment | Broken binder
378 |  | INCD-11473-K | Gordonton | Network | GORCB13 | 05/02/2026 | 08:02 | 05/02/2026 | 12:21 | 0.0025 | 0 | 1 | 259 | Planned | Planned | Crossarm Replacement
379 |  | INCD-7056-K | Gordonton | Network | GORCB13 | 12/09/2025 | 11:49 | 12/09/2025 | 20:59 | 0.0054 | 0 | 1 | 550 | Unplanned | Lightning | Lightning damage
380 |  | INCD-4371-K | Gordonton | Network | GORCB13 | 09/07/2025 | 10:16 | 09/07/2025 | 12:55 | 0.0196 | 0.0001 | 15 | 2016 | Unplanned | Wildlife | Bird betw line & pole
381 |  | INCD-2591-K | Gordonton | Network | GORCB13 | 19/05/2025 | 09:34 | 19/05/2025 | 13:16 | 0.0649 | 0.0003 | 30 | 6660 | Planned | Planned | Pole Replacement
382 |  | INCD-466-M | Gordonton | Network | GORCB13 | 08/12/2025 | 09:41 | 08/12/2025 | 15:32 | 0.0171 | 0 | 5 | 1755 | Planned | Planned | Pole Replacement
383 |  | INCD-519-L | Gordonton | Network | GORCB13 | 17/08/2025 | 08:05 | 17/08/2025 | 08:43 | 0.0048 | 0.0001 | 13 | 494 | Unplanned | Defective Equipment | Overheated connections
384 |  | INCD-230-M | Gordonton | Network | GORCB13 | 14/08/2025 | 10:04 | 14/08/2025 | 15:37 | 0.2248 | 0.0007 | 76 | 23074 | Planned | Planned | Mixed Asset Replacement
385 |  | INCD-2695-K | Gordonton | Network | GORCB13 | 21/05/2025 | 09:10 | 21/05/2025 | 14:25 | 0.0123 | 0 | 4 | 1260 | Planned | Planned | Distribution Transformer Replacement
386 |  | INCD-3529-K | Gordonton | Network | GORCB13 | 11/06/2025 | 12:43 | 11/06/2025 | 14:10 | 0.0025 | 0 | 3 | 261 | Unplanned | Unknown | All Ok - Fault cause not established
387 |  | INCD-1614-L | Gordonton | Network | GORCB13 | 08/12/2025 | 13:54 | 08/12/2025 | 15:56 | 0.0036 | 0 | 3 | 366 | Unplanned | Defective Equipment | Split crossarm
388 |  | INCD-556-M | Gordonton | Network | GORCB13 | 19/01/2026 | 09:08 | 19/01/2026 | 10:46 | 0.0516 | 0.0005 | 54 | 5292 | Planned | Planned | Recloser & Sectionaliser replacement
389 |  | INCD-2590-K | Gordonton | Network | GORCB13 | 19/05/2025 | 09:12 | 19/05/2025 | 14:48 | 0.1356 | 0.001 | 101 | 13921 | Planned | Planned | Mixed Asset Replacement
390 |  | INCD-10027-K | Gordonton | Network | GORCB13 | 23/12/2025 | 15:51 | 23/12/2025 | 18:15 | 0.0759 | 0.0005 | 54 | 7787 | Unplanned | Defective Equipment | Split crossarm
391 |  | INCD-6410-K | Horotiu | Network | GORCB13 | 31/08/2025 | 18:22 | 31/08/2025 | 18:41 | 0.1096 | 0.0062 | 633 | 11247 | Unplanned | Defective Equipment | Broken binder
392 |  | INCD-8156-K | Gordonton | Network | GORCB13 | 12/10/2025 | 06:59 | 12/10/2025 | 07:27 | 0.0003 | 0 | 1 | 28 | Unplanned | Wildlife | Bird betw line & pole
393 |  | INCD-10055-K | Gordonton | Network | GORCB13 | 24/12/2025 | 20:27 | 24/12/2025 | 22:46 | 0.0014 | 0 | 1 | 139 | Unplanned | Defective Equipment | Split crossarm
394 |  | INCD-7009-K | Gordonton | Network | GORCB13 | 11/09/2025 | 18:47 | 11/09/2025 | 20:19 | 0.0009 | 0 | 1 | 92 | Unplanned | Unknown | All Ok - Fault cause not established
395 |  | INCD-251-M | Gordonton | Network | GORCB13 | 19/08/2025 | 09:08 | 19/08/2025 | 14:33 | 0.038 | 0.0001 | 12 | 3900 | Planned | Planned | Pole Replacement
396 |  | INCD-5969-K | Horotiu | Network | GORCB13 | 19/08/2025 | 20:17 | 19/08/2025 | 20:52 | 0.2016 | 0.0062 | 633 | 20695 | Unplanned | Lightning | Lightning damage
397 |  | INCD-8813-K | Gordonton | Network | GORCB13 | 11/11/2025 | 21:56 | 11/11/2025 | 23:28 | 0.0027 | 0 | 3 | 276 | Unplanned | Unknown | All Ok - Fault cause not established
398 |  | INCD-270-M | Gordonton | Network | GORCB13 | 28/08/2025 | 09:12 | 28/08/2025 | 14:46 | 0.0358 | 0.0001 | 11 | 3674 | Planned | Planned | Mixed Asset Replacement
399 |  | INCD-3917-K | Gordonton | Network | GORCB13 | 24/06/2025 | 09:39 | 24/06/2025 | 15:06 | 0.2299 | 0.0007 | 76 | 23594 | Planned | Planned | Crossarm Replacement
400 |  | INCD-582-M | Gordonton | Network | GORCB13 | 11/02/2026 | 09:02 | 11/02/2026 | 13:31 | 0.2631 | 0.001 | 103 | 27008 | Planned | Planned | Mixed Asset Replacement
401 |  | INCD-302-M | Gordonton | Network | GORCB13 | 16/09/2025 | 09:12 | 16/09/2025 | 15:30 | 0.0108 | 0 | 3 | 1108 | Planned | Planned | Pole Replacement
402 |  | INCD-9384-K | Gordonton | Network | GORCB13 | 03/12/2025 | 20:02 | 03/12/2025 | 22:29 | 0.0043 | 0 | 3 | 441 | Unplanned | Lightning | Lightning damage
403 |  | INCD-9455-K | Gordonton | Network | GORCB13 | 06/12/2025 | 06:12 | 06/12/2025 | 08:25 | 0.0039 | 0 | 3 | 399 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
404 |  | INCD-849-K | Gordonton | Network | GORCB13 | 03/04/2025 | 09:52 | 03/04/2025 | 09:52 | 0.0036 | 0 | 1 | 372 | Planned | Planned | Crossarm Replacement
405 |  | INCD-12236-K | Chartwell | Network | GORCB13 | 06/03/2026 | 09:43 | 06/03/2026 | 12:12 | 0.0099 | 0.0001 | 10 | 1020 | Unplanned | Third_party | Car in contact with pole
406 |  | INCD-8389-K | Gordonton | Network | GORCB13 | 23/10/2025 | 15:29 | 24/10/2025 | 01:45 | 0.0119 | 0 | 2 | 1217 | Unplanned | Defective Equipment | Intnl insulation failure
407 |  | INCD-400-M | Gordonton | Network | GORCB13 | 12/11/2025 | 09:16 | 12/11/2025 | 12:10 | 0.0203 | 0.0001 | 12 | 2088 | Planned | Planned | Mixed Asset Replacement
408 |  | INCD-1729-L | Gordonton | Network | GORCB13 | 21/01/2026 | 09:07 | 21/01/2026 | 13:34 | 0.0026 | 0 | 1 | 267 | Planned | Planned | Crossarm Replacement
409 |  | INCD-6018-K | Transpower Hamilton | Network | HAMCB2722 | 20/08/2025 | 20:53 | 20/08/2025 | 21:04 | 0.008 | 0.0011 | 118 | 826 | Unplanned | Defective Equipment | Fuse blown on overload
410 |  | INCD-5689-K | Transpower Hamilton | Network | HAMCB2722 | 13/08/2025 | 00:34 | 13/08/2025 | 01:40 | 0.0379 | 0.0006 | 59 | 3894 | Unplanned | Defective Equipment | Fuse blown on overload
411 |  | INCD-6029-K | Transpower Hamilton | Network | HAMCB2722 | 20/08/2025 | 23:57 | 21/08/2025 | 00:07 | 0.0092 | 0.0011 | 118 | 944 | Unplanned | Defective Equipment | Fuse blown on overload
412 |  | INCD-517-L | Transpower Hamilton | Network | HAMCB2722 | 13/08/2025 | 01:41 | 13/08/2025 | 01:51 | 0.0057 | 0.0006 | 59 | 590 | Unplanned | Defective Equipment | Fuse blown on overload
413 |  | INCD-12821-K | Transpower Hamilton | Network | HAMCB2822 | 31/03/2026 | 02:07 | 31/03/2026 | 14:19 | 0.0088 | 0.003 | 312 | 905 | Unplanned | Third_party | Car in contact with pole
414 |  | INCD-12812-K | Transpower Hamilton | Network | HAMCB2822 | 30/03/2026 | 23:08 | 31/03/2026 | 11:22 | 0.0127 | 0.003 | 312 | 1300 | Unplanned | Third_party | Car in contact with pole
415 |  | INCD-333-M | Transpower Hamilton | Network | HAMCB2742 | 16/09/2025 | 11:11 | 16/09/2025 | 15:39 | 0.1619 | 0.0006 | 62 | 16616 | Planned | Planned | Crossarm Replacement
416 |  | INCD-287-M | Transpower Hamilton | Network | HAMCB2742 | 08/09/2025 | 09:01 | 08/09/2025 | 12:12 | 0.1641 | 0.0009 | 88 | 16846 | Planned | Planned | Crossarm Replacement
417 |  | INCD-8589-K | Transpower Hamilton | Network | HAMCB2742 | 02/11/2025 | 09:52 | 02/11/2025 | 11:58 | 0.1399 | 0.0011 | 114 | 14364 | Planned | Planned | Mixed Asset Replacement
418 |  | INCD-7750-K | Transpower Hamilton | Network | HAMCB2742 | 30/09/2025 | 10:03 | 30/09/2025 | 17:52 | 1.6241 | 0.0035 | 361 | 166704 | Planned | Planned | Mixed Asset Replacement
419 |  | INCD-6166-K | Transpower Hamilton | Network | HAMCB2762 | 25/08/2025 | 09:13 | 25/08/2025 | 10:32 | 0.0523 | 0.0007 | 68 | 5372 | Planned | Planned | New Connections
420 |  | INCD-343-M | Transpower Hamilton | Network | HAMCB2762 | 08/10/2025 | 09:09 | 08/10/2025 | 15:59 | 0.2716 | 0.0007 | 68 | 27880 | Planned | Planned | OTHER Maintenance
421 |  | INCD-8400-K | Transpower Hamilton | Network | HAMCB2762 | 24/10/2025 | 09:02 | 24/10/2025 | 10:47 | 0.0532 | 0.0005 | 52 | 5460 | Planned | Planned | Distribution Transformer Replacement
422 |  | INCD-112-N | Transpower Hamilton | Network | HAMCB2762 | 26/08/2025 | 14:01 | 26/08/2025 | 14:11 | 0.0066 | 0.0007 | 68 | 680 | Planned | Planned | New Connections
423 |  | INCD-287-M | Transpower Hamilton | Network | HAMCB2762 | 08/09/2025 | 09:01 | 08/09/2025 | 12:12 | 0.2382 | 0.0014 | 139 | 24453 | Planned | Planned | Crossarm Replacement
424 |  | INCD-8320-K | Transpower Hamilton | Network | HAMCB2762 | 20/10/2025 | 09:11 | 20/10/2025 | 12:52 | 0.112 | 0.0005 | 52 | 11492 | Planned | Planned | Distribution Transformer Replacement
425 |  | INCD-7673-K | Transpower Hamilton | Network | HAMCB2782 | 28/09/2025 | 09:30 | 28/09/2025 | 15:56 | 0.1692 | 0.0004 | 45 | 17370 | Unplanned | Defective Equipment | Twist crossarm
426 |  | INCD-3487-K | Transpower Hamilton | Network | HAMCB2802 | 11/06/2025 | 00:03 | 11/06/2025 | 00:07 | 0.0055 | 0.0015 | 153 | 561 | Planned | Planned | Mixed Asset Replacement
427 |  | INCD-1528-K | Transpower Hamilton | Network | HAMCB2802 | 18/04/2025 | 07:22 | 18/04/2025 | 12:16 | 0.0029 | 0 | 1 | 294 | Unplanned | Defective Equipment | Split crossarm
428 |  | INCD-3508-K | Hoeka | Network | HAMCB2802 | 11/06/2025 | 09:37 | 11/06/2025 | 14:12 | 0.0817 | 0.0003 | 33 | 8391 | Planned | Planned | Mixed Asset Replacement
429 |  | INCD-5827-K | Transpower Hamilton | Network | HAMCB2802 | 16/08/2025 | 10:49 | 16/08/2025 | 11:17 | 0.0072 | 0.0003 | 27 | 740 | Unplanned | Unknown | All Ok - Fault cause not established
430 |  | INCD-1919-K | Hoeka | Network | HAMCB2802 | 01/05/2025 | 00:27 | 01/05/2025 | 00:50 | 0.0321 | 0.0035 | 355 | 3294 | Planned | Planned | Mixed Asset Replacement
431 |  | INCD-1369-K | Transpower Hamilton | Network | HAMCB2802 | 17/04/2025 | 07:42 | 17/04/2025 | 08:23 | 0.0004 | 0 | 1 | 41 | Unplanned | Adverse weather | Line clash high wind
432 |  | INCD-11178-K | Transpower Hamilton | Network | HAMCB2802 | 27/01/2026 | 05:37 | 27/01/2026 | 10:49 | 0.1844 | 0.0055 | 568 | 18924 | Unplanned | Third_party | Car in contact with pole
433 |  | INCD-8300-K | Transpower Hamilton | Network | HAMCB2802 | 19/10/2025 | 03:24 | 19/10/2025 | 04:48 | 0.0016 | 0 | 2 | 168 | Unplanned | Unknown | All Ok - Fault cause not established
434 |  | INCD-1874-K | Transpower Hamilton | Network | HAMCB2802 | 30/04/2025 | 08:41 | 30/04/2025 | 19:03 | 0.2662 | 0.0004 | 45 | 27323 | Planned | Planned | Mixed Asset Replacement
435 |  | INCD-1866-K | Transpower Hamilton | Network | HAMCB2802 | 30/04/2025 | 00:08 | 30/04/2025 | 00:51 | 0.1212 | 0.0035 | 355 | 12441 | Planned | Planned | New Connections
436 |  | INCD-9298-K | Transpower Hamilton | Network | HAMCB2802 | 28/11/2025 | 17:47 | 28/11/2025 | 23:38 | 0.1131 | 0.0005 | 51 | 11612 | Unplanned | Third_party | High vehicle contact
437 |  | INCD-10990-K | Transpower Hamilton | Network | HAMCB2802 | 22/01/2026 | 09:30 | 22/01/2026 | 11:10 | 0.0107 | 0.0001 | 11 | 1100 | Unplanned | Vegetation | Wind debris on line (OUT of Zone)
438 |  | INCD-4150-K | Transpower Hamilton | Network | HAMCB2802 | 04/07/2025 | 00:02 | 04/07/2025 | 01:14 | 0.0358 | 0.0005 | 51 | 3672 | Unplanned | Unknown | All Ok - Fault cause not established
439 |  | INCD-141-M | Transpower Hamilton | Network | HAMCB2802 | 02/07/2025 | 09:45 | 02/07/2025 | 14:15 | 0.2102 | 0.0008 | 82 | 21577 | Planned | Planned | Mixed Asset Replacement
440 |  | INCD-112-M | Transpower Hamilton | Network | HAMCB2862 | 11/06/2025 | 00:00 | 11/06/2025 | 08:41 | 0.1562 | 0.0096 | 983 | 16036 | Planned | Planned | ABS Replacement
441 |  | INCD-9559-K | Transpower Hamilton | Network | HAMCB2862 | 09/12/2025 | 15:09 | 09/12/2025 | 15:58 | 0.0005 | 0 | 1 | 49 | Unplanned | Unknown | All Ok - Fault cause not established
442 |  | INCD-12148-K | Silverdale | Network | HAMCB2862 | 03/03/2026 | 04:13 | 03/03/2026 | 05:16 | 0.1022 | 0.0017 | 172 | 10492 | Planned | Planned | Mixed Asset Replacement
443 |  | INCD-610-M | Transpower Hamilton | Network | HAMCB2862 | 12/03/2026 | 09:15 | 12/03/2026 | 13:31 | 0.4185 | 0.0017 | 172 | 42952 | Planned | Planned | Mixed Asset Replacement
444 |  | INCD-9706-K | Transpower Hamilton | Network | HAMCB2862 | 13/12/2025 | 10:30 | 13/12/2025 | 12:04 | 0.011 | 0.0001 | 12 | 1128 | Unplanned | Defective Equipment | Cable termination fails
445 |  | INCD-69-M | Transpower Hamilton | Network | HAMCB2862 | 22/05/2025 | 09:32 | 22/05/2025 | 15:19 | 0.7858 | 0.0023 | 237 | 80662 | Planned | Planned | Pole Replacement
446 |  | INCD-9523-K | Transpower Hamilton | Network | HAMCB2862 | 08/12/2025 | 17:49 | 08/12/2025 | 20:58 | 0.5565 | 0.0114 | 1168 | 57120 | Unplanned | Defective Equipment | Cable termination fails
447 |  | INCD-3607-K | Transpower Hamilton | Network | HAMCB2862 | 13/06/2025 | 05:14 | 13/06/2025 | 06:40 | 0.1928 | 0.0023 | 232 | 19790 | Unplanned | Unknown | All Ok - Fault cause not established
448 |  | INCD-12157-K | Silverdale | Network | HAMCB2862 | 03/03/2026 | 09:02 | 03/03/2026 | 17:41 | 0.1532 | 0.0017 | 172 | 15724 | Planned | Planned | Mixed Asset Replacement
449 |  | INCD-3543-K | Transpower Hamilton | Network | HAMCB2862 | 11/06/2025 | 16:04 | 11/06/2025 | 16:30 | 0.0322 | 0.0012 | 127 | 3302 | Planned | Planned | ABS Replacement
450 |  | INCD-9889-K | Transpower Hamilton | Network | HAMCB2882 | 18/12/2025 | 16:55 | 18/12/2025 | 17:09 | 0.0001 | 0 | 1 | 14 | Planned | Planned | RMU Replacement
451 |  | INCD-287-M | Transpower Hamilton | Network | HAMCB2902 | 08/09/2025 | 09:01 | 08/09/2025 | 12:12 | 0.1667 | 0.0009 | 93 | 17112 | Planned | Planned | Crossarm Replacement
452 |  | INCD-0-M | Transpower Hamilton | Network | HAMCB2902 | 08/04/2025 | 09:47 | 08/04/2025 | 12:49 | 0.094 | 0.0005 | 53 | 9646 | Planned | Planned | OTHER Maintenance
453 |  | INCD-255-N | Transpower Hamilton | Network | HAMCB2902 | 11/02/2026 | 08:27 | 11/02/2026 | 15:33 | 0.0134 | 0.0034 | 344 | 1376 | Planned | Planned | Mixed Asset Replacement
454 |  | INCD-8720-K | Tranpsower Hamilton | Network | HAMCB2902 | 07/11/2025 | 13:00 | 07/11/2025 | 14:07 | 0.0331 | 0.0011 | 110 | 3398 | Planned | Planned | Transformer Upgrade
455 |  | INCD-10403-K | Transpower Hamilton | Network | HAMCB2902 | 08/01/2026 | 09:10 | 08/01/2026 | 15:34 | 0.9031 | 0.0024 | 242 | 92694 | Planned | Planned | Mixed Asset Replacement
456 |  | INCD-4074-K | Transpower Hamilton | Network | HAMCB2902 | 28/06/2025 | 23:39 | 29/06/2025 | 14:24 | 0.1197 | 0.0022 | 224 | 12284 | Unplanned | Defective Equipment | Cable termination fails
457 |  | INCD-8115-K | Chartwell | Network | HAMCB2902 | 09/10/2025 | 21:55 | 09/10/2025 | 21:58 | 0.0034 | 0.0011 | 116 | 348 | Unplanned | Third_party | Car in contact with pole
458 |  | INCD-347-M | Transpower Hamilton | Network | HAMCB2902 | 28/10/2025 | 08:40 | 28/10/2025 | 14:47 | 0.2038 | 0.0006 | 57 | 20919 | Planned | Planned | Mixed Asset Replacement
459 |  | INCD-50-M | Transpower Hamilton | Network | HAMCB2902 | 29/05/2025 | 08:36 | 29/05/2025 | 18:47 | 0.2738 | 0.0004 | 46 | 28106 | Planned | Planned | Transformer Upgrade
460 |  | INCD-3946-K | Transpower Hamilton | Network | HAMCB2902 | 26/06/2025 | 12:22 | 26/06/2025 | 18:00 | 0.4695 | 0.0017 | 172 | 48191 | Unplanned | Defective Equipment | Cable termination fails
461 |  | INCD-8608-K | Transpower Hamilton | Network | HAMCB2902 | 03/11/2025 | 06:00 | 03/11/2025 | 12:42 | 0.2443 | 0.0048 | 492 | 25074 | Planned | Planned | Transformer Upgrade
462 |  | INCD-221-M | Transpower Hamilton | Network | HAMCB2902 | 12/08/2025 | 08:36 | 12/08/2025 | 16:21 | 0.2582 | 0.0006 | 57 | 26505 | Planned | Planned | OTHER Maintenance
463 |  | INCD-225-M | Transpower Hamilton | Network | HAMCB2902 | 19/08/2025 | 09:04 | 19/08/2025 | 10:54 | 0.1155 | 0.0011 | 110 | 11860 | Planned | Planned | Mixed Asset Replacement
464 |  | INCD-7405-K | Transpower Hamilton | Network | HAMCB2902 | 19/09/2025 | 15:18 | 19/09/2025 | 19:23 | 0.2029 | 0.0008 | 85 | 20825 | Unplanned | Third_party | Car in contact with pole
465 |  | INCD-211-M | Transpower Hamilton | Network | HAMCB2902 | 25/07/2025 | 09:13 | 25/07/2025 | 15:45 | 0.1757 | 0.0004 | 46 | 18032 | Planned | Planned | OTHER Maintenance
466 |  | INCD-1519-L | Transpower Hamilton | Private | HAMCB2902 | 27/11/2025 | 13:52 | 27/11/2025 | 14:06 | 0.0235 | 0.0017 | 172 | 2408 | Unplanned | Third_party | Temp Disconnect / safety isolation
467 |  | INCD-45-M | Transpower Hamilton | Network | HAMCB2902 | 16/05/2025 | 08:03 | 16/05/2025 | 17:27 | 0.468 | 0.0008 | 87 | 48040 | Planned | Planned | Mixed Asset Replacement
468 |  | INCD-498-M | Claudelands | Network | HAMCB2902 | 13/01/2026 | 22:01 | 14/01/2026 | 03:20 | 0.0949 | 0.0049 | 501 | 9744 | Planned | Planned | Mixed Asset Replacement
469 |  | INCD-8095-K | Transpower Hamilton | Network | HAMCB2902 | 09/10/2025 | 07:12 | 09/10/2025 | 11:29 | 1.0653 | 0.0047 | 487 | 109344 | Unplanned | Third_party | Car in contact with pole
470 |  | INCD-9268-K | Transpower Hamilton | Private | HAMCB2902 | 27/11/2025 | 16:06 | 27/11/2025 | 16:22 | 0.0268 | 0.0017 | 172 | 2752 | Unplanned | Third_party | Temp Disconnect / safety isolation
471 |  | INCD-9009-K | Transpower Hamilton | Network | HAMCB2902 | 17/11/2025 | 23:00 | 18/11/2025 | 03:18 | 0.2765 | 0.0011 | 110 | 28380 | Unplanned | Defective Equipment | Loss or failure of oil
472 |  | INCD-4-M | Transpower Hamilton | Network | HAMCB2902 | 10/04/2025 | 09:04 | 10/04/2025 | 14:58 | 0.1793 | 0.0005 | 52 | 18408 | Planned | Planned | Conductor Replacement
473 |  | INCD-8139-K | Transpower Hamilton | Network | HAMCB2902 | 10/10/2025 | 17:39 | 10/10/2025 | 19:00 | 0.7797 | 0.0126 | 1296 | 80028 | Unplanned | Defective Equipment | Bus chamber flashovr
474 |  | INCD-192-M | Hoeka | Network | HOECB1 | 24/07/2025 | 10:05 | 24/07/2025 | 17:05 | 0.5606 | 0.0013 | 137 | 57540 | Planned | Planned | Mixed Asset Replacement
475 |  | INCD-9965-K | Hoeka | Network | HOECB1 | 20/12/2025 | 22:32 | 21/12/2025 | 00:20 | 0.0125 | 0.0001 | 12 | 1287 | Unplanned | Unknown | All Ok - Fault cause not established
476 |  | INCD-322-M | Hoeka | Network | HOECB1 | 25/09/2025 | 09:41 | 25/09/2025 | 15:54 | 0.1121 | 0.0003 | 32 | 11504 | Planned | Planned | OTHER Maintenance
477 |  | INCD-10944-K | Hoeka | Network | HOECB1 | 21/01/2026 | 21:56 | 22/01/2026 | 12:49 | 0.6526 | 0.0063 | 648 | 66984 | Unplanned | Vegetation | Tree blown ovr on line (OUT of Zone)
478 |  | INCD-2290-K | Hoeka | Network | HOECB1 | 10/05/2025 | 06:52 | 10/05/2025 | 08:55 | 0.0359 | 0.0003 | 30 | 3689 | Unplanned | Unknown | All Ok - Fault cause not established
479 |  | INCD-2461-L | Hoeka | Network | HOECB1 | 27/03/2026 | 14:08 | 27/03/2026 | 20:20 | 0.0036 | 0 | 1 | 372 | Unplanned | Defective Equipment | Twist crossarm
480 |  | INCD-193-M | Hoeka | Network | HOECB1 | 22/07/2025 | 10:07 | 22/07/2025 | 15:11 | 0.0977 | 0.0003 | 33 | 10032 | Planned | Planned | Crossarm Replacement
481 |  | INCD-12352-K | Hoeka | Network | HOECB1 | 12/03/2026 | 23:59 | 13/03/2026 | 00:16 | 0.109 | 0.0063 | 651 | 11186 | Planned | Planned | OTHER Maintenance
482 |  | INCD-139-M | Hoeka | Network | HOECB1 | 02/07/2025 | 09:40 | 02/07/2025 | 14:31 | 0.3114 | 0.0011 | 110 | 31968 | Planned | Planned | Crossarm Replacement
483 |  | INCD-301-M | Hoeka | Network | HOECB1 | 15/09/2025 | 09:06 | 15/09/2025 | 13:01 | 0.0687 | 0.0003 | 30 | 7050 | Planned | Planned | Mixed Asset Replacement
484 |  | INCD-12383-K | Transpower Hamilton | Network | HOECB1 | 15/03/2026 | 00:04 | 15/03/2026 | 00:07 | 0.0203 | 0.0063 | 651 | 2083 | Planned | Planned | OTHER Maintenance
485 |  | INCD-3071-E | Hoeka | Network | HOECB1 | 02/04/2025 | 08:34 | 02/04/2025 | 15:29 | 0.1092 | 0.0003 | 27 | 11205 | Planned | Planned | Distribution Transformer Replacement
486 |  | INCD-4667-K | Hoeka | Network | HOECB1 | 17/07/2025 | 09:30 | 17/07/2025 | 16:49 | 0.408 | 0.0013 | 133 | 41876 | Planned | Planned | Mixed Asset Replacement
487 |  | INCD-420-M | Hoeka | Network | HOECB1 | 28/11/2025 | 09:47 | 28/11/2025 | 11:49 | 0.0048 | 0 | 4 | 488 | Planned | Planned | Pole Replacement
488 |  | INCD-8114-K | Hoeka | Network | HOECB1 | 09/10/2025 | 17:02 | 09/10/2025 | 21:23 | 0.0178 | 0.0001 | 7 | 1827 | Unplanned | Unknown | All Ok - Fault cause not established
489 |  | INCD-11114-K | Hoeka | Network | HOECB1 | 24/01/2026 | 15:46 | 24/01/2026 | 16:05 | 0.0266 | 0.0063 | 648 | 2735 | Unplanned | Unknown | All Ok - Fault cause not established
490 |  | INCD-11113-K | Hoeka | Network | HOECB1 | 22/01/2026 | 11:13 | 24/01/2026 | 15:46 | 0.0014 | 0 | 1 | 141 | Unplanned | Unknown | All Ok - Fault cause not established
491 |  | INCD-10952-K | Hoeka | Network | HOECB2 | 22/01/2026 | 00:44 | 22/01/2026 | 00:49 | 0.0042 | 0.0008 | 81 | 436 | Unplanned | Vegetation | Wind debris on line (OUT of Zone)
492 |  | INCD-10955-K | Hoeka | Network | HOECB2 | 22/01/2026 | 03:49 | 22/01/2026 | 06:09 | 0.1063 | 0.0008 | 78 | 10907 | Unplanned | Defective Equipment | Jumper fails on thru flt
493 |  | INCD-1170-L | Hoeka | Network | HOECB2 | 28/10/2025 | 16:46 | 28/10/2025 | 19:29 | 0.0614 | 0.0004 | 42 | 6306 | Unplanned | Defective Equipment | Broken binder
494 |  | INCD-10954-K | Hoeka | Network | HOECB2 | 22/01/2026 | 03:20 | 22/01/2026 | 06:20 | 0.0053 | 0 | 3 | 540 | Unplanned | Defective Equipment | Jumper fails on thru flt
495 |  | INCD-12351-K | Hoeka | Network | HOECB2 | 12/03/2026 | 23:59 | 13/03/2026 | 00:03 | 0.0038 | 0.0015 | 157 | 386 | Planned | Planned | OTHER Maintenance
496 |  | INCD-444-M | Hoeka | Network | HOECB2 | 22/11/2025 | 07:30 | 22/11/2025 | 13:37 | 0.2895 | 0.0008 | 81 | 29711 | Planned | Planned | OTHER Maintenance
497 |  | INCD-353-L | Hoeka | Network | HOECB2 | 12/08/2025 | 09:41 | 12/08/2025 | 13:21 | 0.0491 | 0.0002 | 24 | 5040 | Planned | Planned | Mixed Asset Replacement
498 |  | INCD-12382-K | Silverdale | Network | HOECB2 | 14/03/2026 | 23:59 | 15/03/2026 | 00:08 | 0.011 | 0.0015 | 157 | 1134 | Planned | Planned | OTHER Maintenance
499 |  | INCD-12513-K | Hoeka | Network | HOECB3 | 20/03/2026 | 08:30 | 20/03/2026 | 16:56 | 0.6092 | 0.0013 | 134 | 62528 | Planned | Planned | Mixed Asset Replacement
500 |  | INCD-469-M | Hoeka | Network | HOECB3 | 12/12/2025 | 09:11 | 12/12/2025 | 15:42 | 0.1731 | 0.0023 | 231 | 17768 | Planned | Planned | Mixed Asset Replacement
501 |  | INCD-512-M | Hoeka | Network | HOECB3 | 19/12/2025 | 08:36 | 19/12/2025 | 13:13 | 0.1106 | 0.0004 | 41 | 11357 | Planned | Planned | Mixed Asset Replacement
502 |  | INCD-1568-K | Hoeka | Network | HOECB3 | 18/04/2025 | 16:49 | 18/04/2025 | 19:49 | 0.0053 | 0 | 3 | 540 | Unplanned | Defective Equipment | Split crossarm
503 |  | INCD-648-M | Hoeka | Network | HOECB3 | 17/03/2026 | 08:42 | 17/03/2026 | 13:56 | 0.0782 | 0.0003 | 27 | 8031 | Planned | Planned | Mixed Asset Replacement
504 |  | INCD-380-M | Hoeka | Network | HOECB3 | 21/10/2025 | 08:41 | 21/10/2025 | 11:11 | 0.0058 | 0 | 4 | 600 | Planned | Planned | Crossarm Replacement
505 |  | INCD-239-M | Hoeka | Network | HOECB3 | 31/07/2025 | 08:30 | 31/07/2025 | 12:20 | 0.0134 | 0.0001 | 6 | 1380 | Planned | Planned | Crossarm Replacement
506 |  | INCD-1733-L | Hoeka | Private | HOECB3 | 21/01/2026 | 13:27 | 21/01/2026 | 13:38 | 0.0016 | 0.0001 | 15 | 165 | Unplanned | Defective Equipment | LVC - WEL & Customer
507 |  | INCD-373-M | Hoeka | Network | HOECB3 | 23/10/2025 | 08:41 | 23/10/2025 | 10:36 | 0.0101 | 0.0001 | 9 | 1035 | Planned | Planned | Crossarm Replacement
508 |  | INCD-12624-K | Hoeka | Network | HOECB3 | 24/03/2026 | 08:57 | 24/03/2026 | 09:22 | 0.2104 | 0.0086 | 878 | 21599 | Unplanned | Defective Equipment | Flickers misaligned
509 |  | INCD-12382-K | Silverdale | Network | HOECB3 | 14/03/2026 | 23:59 | 15/03/2026 | 00:08 | 0.0513 | 0.0085 | 877 | 5268 | Planned | Planned | OTHER Maintenance
510 |  | INCD-12351-K | Hoeka | Network | HOECB3 | 12/03/2026 | 23:59 | 13/03/2026 | 00:03 | 0.0148 | 0.0085 | 877 | 1514 | Planned | Planned | OTHER Maintenance
511 |  | INCD-8396-K | Hoeka | Network | HOECB4 | 23/10/2025 | 22:45 | 24/10/2025 | 01:05 | 0.1468 | 0.0024 | 249 | 15073 | Unplanned | Unknown | All Ok - Fault cause not established
512 |  | INCD-566-M | Hoeka | Network | HOECB4 | 29/12/2025 | 08:36 | 29/12/2025 | 09:58 | 0.0008 | 0 | 1 | 82 | Planned | Planned | 11kV Fuse Replacement
513 |  | INCD-12383-K | Transpower Hamilton | Network | HOECB4 | 15/03/2026 | 00:04 | 15/03/2026 | 00:07 | 0.0078 | 0.0024 | 250 | 800 | Planned | Planned | OTHER Maintenance
514 |  | INCD-12352-K | Hoeka | Network | HOECB4 | 12/03/2026 | 23:59 | 13/03/2026 | 00:16 | 0.0419 | 0.0024 | 250 | 4296 | Planned | Planned | OTHER Maintenance
515 |  | INCD-6338-K | Hoeka | Network | HOECB4 | 30/08/2025 | 06:27 | 30/08/2025 | 08:29 | 0.0036 | 0 | 3 | 366 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
516 |  | INCD-3318-K | Hoeka | Network | HOECB4 | 06/06/2025 | 10:46 | 06/06/2025 | 16:26 | 0.2146 | 0.0019 | 200 | 22029 | Unplanned | Third_party | Car in contact with pole
517 |  | INCD-1714-K | Hoeka | Network | HOECB4 | 24/04/2025 | 19:16 | 24/04/2025 | 20:22 | 0.0197 | 0.0003 | 31 | 2021 | Unplanned | Unknown | All Ok - Fault cause not established
518 |  | INCD-431-M | Hoeka | Network | HOECB4 | 15/11/2025 | 09:02 | 15/11/2025 | 16:09 | 0.0541 | 0.0001 | 13 | 5551 | Planned | Planned | New Connections
519 |  | INCD-164-M | Hoeka | Network | HOECB4 | 11/07/2025 | 10:12 | 11/07/2025 | 16:08 | 0.0173 | 0 | 5 | 1780 | Planned | Planned | Crossarm Replacement
520 |  | INCD-603-M | Hoeka | Network | HOECB4 | 16/02/2026 | 09:59 | 16/02/2026 | 11:14 | 0.0022 | 0 | 3 | 225 | Planned | Planned | Mixed Asset Replacement
521 |  | INCD-12699-K | Hoeka | Network | HOECB6 | 27/03/2026 | 00:45 | 27/03/2026 | 01:17 | 0.0413 | 0.0013 | 131 | 4238 | Unplanned | Vegetation | Wind debris on line (IN Zone)
522 |  | INCD-9321-K | Hoeka | Network | HOECB6 | 01/12/2025 | 06:31 | 01/12/2025 | 10:05 | 0.1607 | 0.0008 | 79 | 16499 | Unplanned | Defective Equipment | Line break at twist joint
523 |  | INCD-9707-K | Hoeka | Private | HOECB6 | 13/12/2025 | 11:29 | 13/12/2025 | 11:53 | 0.0021 | 0.0001 | 9 | 216 | Unplanned | Third_party | Temp Disconnect / safety isolation
524 |  | INCD-9872-K | Hoeka | Network | HOECB6 | 18/12/2025 | 11:50 | 18/12/2025 | 15:51 | 0.0804 | 0.0006 | 60 | 8249 | Unplanned | Third_party | Car in contact with pole
525 |  | INCD-344-M | Hoeka | Network | HOECB6 | 09/10/2025 | 09:45 | 09/10/2025 | 13:15 | 0.0143 | 0.0001 | 7 | 1470 | Planned | Planned | New Connections
526 |  | INCD-3111-E | Hoeka | Network | HOECB6 | 04/04/2025 | 09:23 | 04/04/2025 | 15:15 | 0.12 | 0.0003 | 35 | 12320 | Planned | Planned | Crossarm Replacement
527 |  | INCD-7152-K | Hoeka | Network | HOECB6 | 15/09/2025 | 08:24 | 15/09/2025 | 16:38 | 0.5407 | 0.0058 | 600 | 55499 | Unplanned | Third_party | Car in contact with pole
528 |  | INCD-1663-L | Hoeka | Network | HOECB6 | 18/12/2025 | 11:31 | 18/12/2025 | 17:39 | 0.0394 | 0.0001 | 11 | 4048 | Unplanned | Third_party | Car in contact with pole
529 |  | INCD-12624-K | Hoeka | Network | HOECB6 | 24/03/2026 | 08:57 | 24/03/2026 | 09:22 | 0.0951 | 0.0058 | 600 | 9761 | Unplanned | Defective Equipment | Flickers misaligned
530 |  | INCD-162-M | Hoeka | Network | HOECB6 | 10/07/2025 | 10:04 | 10/07/2025 | 16:08 | 0.2652 | 0.0008 | 78 | 27222 | Planned | Planned | Mixed Asset Replacement
531 |  | INCD-10998-K | Hoeka | Network | HOECB6 | 22/01/2026 | 10:36 | 22/01/2026 | 16:00 | 0.1733 | 0.0011 | 114 | 17786 | Unplanned | Vegetation | Wind debris on line (OUT of Zone)
532 |  | INCD-12351-K | Hoeka | Network | HOECB6 | 12/03/2026 | 23:59 | 13/03/2026 | 00:03 | 0.021 | 0.0058 | 600 | 2160 | Planned | Planned | OTHER Maintenance
533 |  | INCD-165-M | Hoeka | Network | HOECB6 | 11/07/2025 | 10:00 | 11/07/2025 | 15:54 | 0.1534 | 0.0007 | 71 | 15748 | Planned | Planned | Mixed Asset Replacement
534 |  | INCD-220-M | Hoeka | Network | HOECB6 | 05/08/2025 | 09:35 | 05/08/2025 | 14:43 | 0.021 | 0.0001 | 7 | 2156 | Planned | Planned | Mixed Asset Replacement
535 |  | INCD-7959-K | Hoeka | Network | HOECB6 | 05/10/2025 | 02:42 | 05/10/2025 | 04:24 | 0.0735 | 0.0007 | 74 | 7548 | Unplanned | Unknown | All Ok - Fault cause not established
536 |  | INCD-8174-K | Hoeka | Network | HOECB6 | 13/10/2025 | 13:43 | 13/10/2025 | 17:54 | 0.8971 | 0.0065 | 670 | 92084 | Unplanned | Third_party | Car in contact with pole
537 |  | INCD-5325-K | Hoeka | Network | HOECB6 | 03/08/2025 | 13:37 | 03/08/2025 | 18:01 | 0.5796 | 0.0058 | 599 | 59492 | Unplanned | Defective Equipment | Line break at twist joint
538 |  | INCD-11786-K | Hoeka | Network | HOECB6 | 16/02/2026 | 14:16 | 16/02/2026 | 16:04 | 0.1084 | 0.001 | 103 | 11124 | Unplanned | Defective Equipment | Split crossarm
539 |  | INCD-205-M | Hoeka | Network | HOECB6 | 01/08/2025 | 09:40 | 01/08/2025 | 14:31 | 0.2038 | 0.0007 | 74 | 20918 | Planned | Planned | Mixed Asset Replacement
540 |  | INCD-12382-K | Silverdale | Network | HOECB6 | 14/03/2026 | 23:59 | 15/03/2026 | 00:08 | 0.0416 | 0.0058 | 600 | 4270 | Planned | Planned | OTHER Maintenance
541 |  | INCD-5763-K | Hoeka | Private | HOECB6 | 14/08/2025 | 11:10 | 14/08/2025 | 11:29 | 0.0019 | 0.0001 | 10 | 190 | Unplanned | Defective Equipment | LVC - WEL & Customer
542 |  | INCD-136-N | Hoeka | Network | HOECB6 | 07/11/2025 | 09:38 | 07/11/2025 | 13:16 | 0.0667 | 0.0003 | 35 | 6848 | Planned | Planned | Crossarm Replacement
543 |  | INCD-5090-K | Hoeka | Network | HOECB6 | 27/07/2025 | 17:34 | 28/07/2025 | 00:01 | 0.2016 | 0.0011 | 112 | 20690 | Unplanned | Wildlife | Bird lne clash/break
544 |  | INCD-8979-K | Horotiu | Network | HORCB3 | 17/11/2025 | 08:24 | 17/11/2025 | 15:31 | 0.0042 | 0 | 1 | 427 | Planned | Planned | OTHER Maintenance
545 |  | INCD-8459-K | Horotiu | Network | HORCB3 | 28/10/2025 | 07:04 | 28/10/2025 | 16:24 | 0.0315 | 0.0002 | 19 | 3231 | Unplanned | Lightning | Lightning damage
546 |  | INCD-6422-K | Horotiu | Private | HORCB3 | 31/08/2025 | 18:56 | 31/08/2025 | 19:28 | 0.0595 | 0.0022 | 225 | 6107 | Unplanned | Third_party | Temp Disconnect / safety isolation
547 |  | INCD-5166-K | Ngaruawahia | Network | HORCB3 | 29/07/2025 | 09:03 | 29/07/2025 | 17:13 | 0.0127 | 0 | 3 | 1305 | Planned | Planned | ABS Replacement
548 |  | INCD-305-M | Horotiu | Network | HORCB3 | 08/10/2025 | 09:14 | 08/10/2025 | 16:06 | 0.1222 | 0.0003 | 32 | 12538 | Planned | Planned | Mixed Asset Replacement
549 |  | INCD-8601-K | Horotiu | Network | HORCB3 | 02/11/2025 | 18:04 | 02/11/2025 | 23:46 | 0.0033 | 0 | 1 | 342 | Unplanned | Defective Equipment | Intnl insulation failure
550 |  | INCD-409-M | Horotiu | Network | HORCB3 | 21/11/2025 | 09:00 | 21/11/2025 | 15:21 | 0.1164 | 0.0003 | 32 | 11945 | Planned | Planned | Mixed Asset Replacement
551 |  | INCD-561-M | Horotiu | Network | HORCB3 | 23/01/2026 | 09:04 | 23/01/2026 | 13:52 | 0.1599 | 0.0006 | 57 | 16416 | Planned | Planned | OTHER Maintenance
552 |  | INCD-57-M | Horotiu | Network | HORCB5 | 23/05/2025 | 08:33 | 23/05/2025 | 13:20 | 0.1007 | 0.0004 | 36 | 10332 | Planned | Planned | Crossarm Replacement
553 |  | INCD-8864-K | Horotiu | Network | HORCB5 | 13/11/2025 | 09:02 | 13/11/2025 | 10:22 | 0.0023 | 0 | 3 | 240 | Planned | Planned | OTHER Maintenance
554 |  | INCD-10389-K | Horotiu | Network | HORCB5 | 08/01/2026 | 02:28 | 08/01/2026 | 05:51 | 0.0712 | 0.0004 | 36 | 7308 | Unplanned | Unknown | All Ok - Fault cause not established
555 |  | INCD-958-K | Horotiu | Network | HORCB5 | 06/04/2025 | 21:18 | 06/04/2025 | 23:02 | 0.003 | 0 | 3 | 312 | Unplanned | Wildlife | Rodent on HV terminals
556 |  | INCD-1338-L | Horotiu | Network | HORCB5 | 05/11/2025 | 05:35 | 05/11/2025 | 12:26 | 0.1336 | 0.0004 | 36 | 13717 | Unplanned | Third_party | Car in contact with pole
557 |  | INCD-46-M | Horotiu | Network | HORCB5 | 20/05/2025 | 08:34 | 20/05/2025 | 11:45 | 0.0782 | 0.0004 | 42 | 8022 | Planned | Planned | Mixed Asset Replacement
558 |  | INCD-135-M | Horotiu | Network | HORCB5 | 24/06/2025 | 08:45 | 24/06/2025 | 15:05 | 0.0185 | 0 | 5 | 1900 | Planned | Planned | Crossarm Replacement
559 |  | INCD-3480-K | Horotiu | Network | HORCB5 | 10/06/2025 | 16:54 | 10/06/2025 | 19:47 | 0.0152 | 0.0001 | 9 | 1557 | Unplanned | Defective Equipment | Mechanism seized
560 |  | INCD-58-M | Horotiu | Network | HORCB5 | 27/05/2025 | 08:37 | 27/05/2025 | 14:45 | 0.0856 | 0.0002 | 24 | 8787 | Planned | Planned | Crossarm Replacement
561 |  | INCD-136-M | Horotiu | Network | HORCB5 | 25/06/2025 | 08:35 | 25/06/2025 | 14:43 | 0.1073 | 0.0003 | 30 | 11010 | Planned | Planned | Crossarm Replacement
562 |  | INCD-58-N | Horotiu | Network | HORCB5 | 18/08/2025 | 08:32 | 18/08/2025 | 11:17 | 0.0048 | 0 | 3 | 495 | Planned | Planned | Crossarm Replacement
563 |  | INCD-12034-K | Horotiu | Network | HORCB5 | 24/02/2026 | 08:45 | 24/02/2026 | 08:59 | 0.0109 | 0.0041 | 417 | 1116 | Unplanned | Defective Equipment | Contact problem
564 |  | INCD-6069-K | Horotiu | Network | HORCB5 | 21/08/2025 | 18:04 | 21/08/2025 | 23:34 | 0.0945 | 0.0007 | 76 | 9702 | Unplanned | Defective Equipment | Mechanism seized
565 |  | INCD-12033-K | Horotiu | Network | HORCB5 | 24/02/2026 | 08:09 | 24/02/2026 | 12:04 | 0.2335 | 0.001 | 102 | 23965 | Unplanned | Defective Equipment | Contact problem
566 |  | INCD-285-M | Horotiu | Network | HORCB5 | 05/09/2025 | 08:56 | 05/09/2025 | 11:55 | 0.0628 | 0.0004 | 36 | 6444 | Planned | Planned | Pole Replacement
567 |  | INCD-247-M | Horotiu | Network | HORCB5 | 02/09/2025 | 08:33 | 02/09/2025 | 10:15 | 0.001 | 0 | 1 | 102 | Planned | Planned | Crossarm Replacement
568 |  | INCD-462-L | Horotiu | Network | HORCB5 | 30/07/2025 | 15:30 | 31/07/2025 | 13:58 | 0.0131 | 0 | 1 | 1348 | Unplanned | Defective Equipment | Faulty joint/connection
569 |  | INCD-153-M | Horotiu | Network | HORCB5 | 05/08/2025 | 08:36 | 05/08/2025 | 15:31 | 0.4438 | 0.0011 | 113 | 45557 | Planned | Planned | Mixed Asset Replacement
570 |  | INCD-405-M | Horotiu | Network | HORCB5 | 18/11/2025 | 09:05 | 18/11/2025 | 13:43 | 0.1114 | 0.0004 | 43 | 11436 | Planned | Planned | Crossarm Replacement
571 |  | INCD-11888-K | Ngaruawahia | Network | HORCB5 | 19/02/2026 | 09:31 | 19/02/2026 | 16:57 | 0.0059 | 0 | 2 | 606 | Planned | Planned | Mixed Asset Replacement
572 |  | INCD-284-M | Horotiu | Network | HORCB5 | 10/09/2025 | 09:05 | 10/09/2025 | 13:19 | 0.0223 | 0.0001 | 9 | 2286 | Planned | Planned | Mixed Asset Replacement
573 |  | INCD-152-M | Horotiu | Network | HORCB5 | 24/07/2025 | 08:30 | 24/07/2025 | 15:32 | 0.441 | 0.0011 | 113 | 45264 | Planned | Planned | Crossarm Replacement
574 |  | INCD-10160-K | Horotiu | Network | HORCB5 | 29/12/2025 | 15:42 | 30/12/2025 | 05:09 | 0.0708 | 0.0001 | 9 | 7263 | Unplanned | Unknown | All Ok - Fault cause not established
575 |  | INCD-246-M | Horotiu | Network | HORCB5 | 02/09/2025 | 08:47 | 02/09/2025 | 11:15 | 0.1096 | 0.0007 | 76 | 11248 | Planned | Planned | Crossarm Replacement
576 |  | INCD-244-M | Horotiu | Network | HORCB5 | 21/08/2025 | 08:32 | 21/08/2025 | 14:37 | 0.2134 | 0.0006 | 60 | 21900 | Planned | Planned | Crossarm Replacement
577 |  | INCD-583-M | Horotiu | Network | HORCB6 | 05/02/2026 | 09:43 | 05/02/2026 | 13:52 | 0.4436 | 0.0019 | 194 | 45531 | Planned | Planned | Crossarm Replacement
578 |  | INCD-82-M | Horotiu | Network | HORCB6 | 28/05/2025 | 10:00 | 28/05/2025 | 13:03 | 0.0815 | 0.0005 | 47 | 8362 | Planned | Planned | Crossarm Replacement
579 |  | INCD-4184-K | Horotiu | Network | HORCB6 | 04/07/2025 | 15:37 | 04/07/2025 | 20:15 | 0.0081 | 0 | 3 | 834 | Unplanned | Lightning | Lightning damage
580 |  | INCD-335-M | Horotiu | Network | HORCB6 | 02/10/2025 | 20:59 | 02/10/2025 | 21:25 | 0.0005 | 0 | 2 | 52 | Planned | Planned | OTHER Maintenance
581 |  | INCD-7781-K | Horotiu | Network | HORCB6 | 01/10/2025 | 05:32 | 01/10/2025 | 06:06 | 0.0003 | 0 | 1 | 34 | Planned | Planned | Mixed Asset Replacement
582 |  | INCD-9369-K | Horotiu | Network | HORCB6 | 03/12/2025 | 18:00 | 03/12/2025 | 20:43 | 0.0143 | 0.0001 | 9 | 1466 | Unplanned | Unknown | All Ok - Fault cause not established
583 |  | INCD-7783-K | Horotiu | Network | HORCB6 | 01/10/2025 | 06:26 | 01/10/2025 | 07:00 | 0.0007 | 0 | 2 | 68 | Planned | Planned | Mixed Asset Replacement
584 |  | INCD-7506-K | Horotiu | Network | HORCB6 | 23/09/2025 | 07:27 | 23/09/2025 | 11:18 | 0.5579 | 0.0072 | 744 | 57262 | Unplanned | Third_party | Car in contact with pole
585 |  | INCD-12695-K | Horotiu | Network | HORCB6 | 26/03/2026 | 21:50 | 27/03/2026 | 03:29 | 0.1691 | 0.0099 | 1013 | 17352 | Unplanned | Defective Equipment | Pins fulls out
586 |  | INCD-5166-K | Ngaruawahia | Network | HORCB6 | 29/07/2025 | 09:03 | 29/07/2025 | 17:13 | 0.0335 | 0.0001 | 8 | 3439 | Planned | Planned | ABS Replacement
587 |  | INCD-5940-K | Horotiu | Network | HORCB6 | 19/08/2025 | 09:03 | 19/08/2025 | 13:38 | 0.1309 | 0.0005 | 51 | 13433 | Planned | Planned | Distribution Transformer Replacement
588 |  | INCD-7790-K | Horotiu | Network | HORCB6 | 01/10/2025 | 10:10 | 01/10/2025 | 17:29 | 2.2566 | 0.0054 | 557 | 231627 | Planned | Planned | Mixed Asset Replacement
589 |  | INCD-426-M | Horotiu | Network | HORCB6 | 20/11/2025 | 09:30 | 20/11/2025 | 14:06 | 0.1207 | 0.0005 | 48 | 12394 | Planned | Planned | Mixed Asset Replacement
590 |  | INCD-8001-K | Horotiu | Network | HORCB6 | 02/10/2025 | 18:59 | 02/10/2025 | 19:37 | 0.0004 | 0 | 1 | 38 | Planned | Planned | Conductor Replacement
591 |  | INCD-3646-K | Horotiu | Network | HORCB7 | 14/06/2025 | 08:17 | 14/06/2025 | 17:20 | 0.0053 | 0 | 1 | 543 | Planned | Planned | RMU Replacement
592 |  | INCD-2495-K | Hospital | Network | HOSCB11 | 15/05/2025 | 06:35 | 15/05/2025 | 11:30 | 0.1868 | 0.0006 | 65 | 19175 | Unplanned | Defective Equipment | Jumpers come off
593 |  | INCD-2315-K | Te Kauwhata | Network | HPTCB2 | 11/05/2025 | 07:54 | 11/05/2025 | 08:59 | 0.0012 | 0 | 3 | 128 | Unplanned | Unknown | All Ok - Fault cause not established
594 |  | INCD-532-M | SpringHill Rd | Network | HPTCB2 | 13/01/2026 | 10:30 | 20/01/2026 | 16:05 | 0.0143 | 0 | 3 | 1472 | Planned | Planned | Mixed Asset Replacement
595 |  | INCD-137-M | Hampton Downs | Network | HPTCB2 | 24/06/2025 | 08:03 | 24/06/2025 | 16:06 | 0.0089 | 0 | 3 | 916 | Planned | Planned | Mixed Asset Replacement
596 |  | INCD-2315-K | Te Kauwhata | Network | HPTCB3 | 11/05/2025 | 07:54 | 11/05/2025 | 08:59 | 0.0232 | 0.0004 | 37 | 2386 | Unplanned | Unknown | All Ok - Fault cause not established
597 |  | INCD-4558-K | Hampton Downs | Network | HPTCB3 | 14/07/2025 | 17:58 | 14/07/2025 | 22:06 | 0.0087 | 0 | 4 | 890 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
598 |  | INCD-137-M | Hampton Downs | Network | HPTCB3 | 24/06/2025 | 08:03 | 24/06/2025 | 16:06 | 0.1627 | 0.0004 | 37 | 16701 | Planned | Planned | Mixed Asset Replacement
599 |  | INCD-438-M | Hampton Downs | Network | HPTCB3 | 04/12/2025 | 09:30 | 04/12/2025 | 13:52 | 0.0332 | 0.0001 | 13 | 3406 | Planned | Planned | OTHER Maintenance
600 |  | INCD-532-M | SpringHill Rd | Network | HPTCB3 | 13/01/2026 | 10:30 | 20/01/2026 | 16:05 | 0.1769 | 0.0004 | 37 | 18161 | Planned | Planned | Mixed Asset Replacement
601 |  | INCD-532-M | SpringHill Rd | Network | HPTCB4 | 13/01/2026 | 10:30 | 20/01/2026 | 16:05 | 0.0048 | 0 | 1 | 493 | Planned | Planned | Mixed Asset Replacement
602 |  | INCD-2315-K | Te Kauwhata | Network | HPTCB4 | 11/05/2025 | 07:54 | 11/05/2025 | 08:59 | 0.0006 | 0 | 1 | 64 | Unplanned | Unknown | All Ok - Fault cause not established
603 |  | INCD-137-M | Hampton Downs | Network | HPTCB4 | 24/06/2025 | 08:03 | 24/06/2025 | 16:06 | 0.0044 | 0 | 1 | 452 | Planned | Planned | Mixed Asset Replacement
604 |  | INCD-4560-K | Hampton Downs | Network | HPTCB4 | 14/07/2025 | 22:51 | 15/07/2025 | 01:28 | 0.0015 | 0 | 1 | 157 | Unplanned | Unknown | All Ok - Fault cause not established
605 |  | INCD-4023-K | Hampton Downs | Network | HPTCB4 | 29/06/2025 | 07:38 | 29/06/2025 | 10:27 | 0.0016 | 0 | 1 | 169 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
606 |  | INCD-2300-K | Te Kauwhata | Network | HPTCB5 | 10/05/2025 | 10:48 | 10/05/2025 | 12:29 | 0.002 | 0 | 2 | 202 | Unplanned | Unknown | All Ok - Fault cause not established
607 |  | INCD-9180-K | Hampton Downs | Network | HPTCB5 | 22/11/2025 | 10:32 | 22/11/2025 | 16:11 | 0.8644 | 0.0047 | 484 | 88727 | Unplanned | Lightning | Spontaneous failure
608 |  | INCD-11120-K | Hampton Downs | Network | HPTCB5 | 24/01/2026 | 18:40 | 24/01/2026 | 19:01 | 0.0814 | 0.004 | 409 | 8352 | Unplanned | Vegetation | Tree contact high wind (OUT of Zone)
609 |  | INCD-26-N | Hampton Downs | Network | HPTCB5 | 07/07/2025 | 00:07 | 07/07/2025 | 02:35 | 0.036 | 0.0002 | 25 | 3700 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
610 |  | INCD-5445-K | Hampton Downs | Network | HPTCB5 | 06/08/2025 | 14:07 | 06/08/2025 | 17:53 | 0.0044 | 0 | 2 | 452 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
611 |  | INCD-265-N | Hampton Downs | Network | HPTCB5 | 15/02/2026 | 08:29 | 15/02/2026 | 17:24 | 1.0899 | 0.0025 | 256 | 111872 | Planned | Planned | Mixed Asset Replacement
612 |  | INCD-687-M | Hampton Downs | Network | HPTCB5 | 27/03/2026 | 08:36 | 27/03/2026 | 12:23 | 0.4226 | 0.0019 | 194 | 43378 | Planned | Planned | ABS Replacement
613 |  | INCD-2242-K | Te Kauwhata | Network | HPTCB5 | 08/05/2025 | 17:01 | 08/05/2025 | 19:01 | 0.0058 | 0 | 5 | 600 | Unplanned | Unknown | All Ok - Fault cause not established
614 |  | INCD-11117-K | Hampton Downs | Network | HPTCB5 | 24/01/2026 | 16:15 | 24/01/2026 | 16:30 | 0.0609 | 0.004 | 409 | 6251 | Unplanned | Unknown | All Ok - Fault cause not established
615 |  | INCD-532-M | SpringHill Rd | Network | HPTCB5 | 13/01/2026 | 10:30 | 20/01/2026 | 16:05 | 0.5387 | 0.0011 | 110 | 55295 | Planned | Planned | Mixed Asset Replacement
616 |  | INCD-12810-K | Hampton Downs | Network | HPTCB5 | 31/03/2026 | 09:10 | 31/03/2026 | 10:58 | 0.0074 | 0.0001 | 7 | 757 | Unplanned | Defective Equipment | Faulty joint/connection
617 |  | INCD-345-M | Hampton Downs | Network | HPTCB5 | 16/10/2025 | 10:03 | 16/10/2025 | 15:42 | 0.0545 | 0.0002 | 17 | 5592 | Planned | Planned | Mixed Asset Replacement
618 |  | INCD-11115-K | Hampton Downs | Network | HPTCB5 | 16/01/2026 | 16:52 | 24/01/2026 | 16:08 | 0.0004 | 0 | 2 | 36 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
619 |  | INCD-6214-K | Hampton Downs | Network | HPTCB5 | 26/08/2025 | 10:08 | 26/08/2025 | 15:46 | 0.1317 | 0.0004 | 40 | 13520 | Planned | Planned | Mixed Asset Replacement
620 |  | INCD-123-N | Hampton Downs | Network | HPTCB5 | 13/10/2025 | 08:56 | 13/10/2025 | 16:31 | 0.1395 | 0.0006 | 62 | 14320 | Planned | Planned | Mixed Asset Replacement
621 |  | INCD-270-N | Hampton Downs | Network | HPTCB5 | 19/03/2026 | 09:07 | 19/03/2026 | 11:30 | 0.0014 | 0 | 1 | 143 | Planned | Planned | OTHER Maintenance
622 |  | INCD-6071-K | Hampton Downs | Network | HPTCB5 | 21/08/2025 | 17:00 | 21/08/2025 | 20:46 | 0.0198 | 0.0001 | 9 | 2034 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
623 |  | INCD-7951-K | Hampton Downs | Network | HPTCB5 | 04/10/2025 | 16:52 | 04/10/2025 | 21:00 | 0.0097 | 0 | 4 | 992 | Unplanned | Lightning | Lightning damage
624 |  | INCD-137-M | Hampton Downs | Network | HPTCB5 | 24/06/2025 | 08:03 | 24/06/2025 | 16:06 | 0.8089 | 0.0018 | 183 | 83026 | Planned | Planned | Mixed Asset Replacement
625 |  | INCD-2315-K | Te Kauwhata | Network | HPTCB5 | 11/05/2025 | 07:54 | 11/05/2025 | 08:59 | 0.2086 | 0.0034 | 345 | 21413 | Unplanned | Unknown | All Ok - Fault cause not established
626 |  | INCD-6883-K | Kent St | Network | KENCB12 | 09/09/2025 | 09:15 | 09/09/2025 | 09:33 | 0.0193 | 0.0015 | 149 | 1979 | Unplanned | Defective Equipment | Cable joint fails
627 |  | INCD-10744-K | Kent St | Network | KENCB12 | 17/01/2026 | 10:42 | 17/01/2026 | 11:42 | 0.0894 | 0.0015 | 153 | 9180 | Unplanned | Defective Equipment | Cable fails unknown
628 |  | INCD-357-M | Kent | Network | KENCB14 | 19/10/2025 | 08:06 | 19/10/2025 | 16:39 | 0.035 | 0.0001 | 7 | 3591 | Planned | Planned | Subdivision
629 |  | INCD-11872-K | Kent St | Network | KENCB14 | 18/02/2026 | 00:20 | 18/02/2026 | 00:22 | 0.0057 | 0.0034 | 350 | 583 | Unplanned | Defective Equipment | Cable fails unknown
630 |  | INCD-6883-K | Kent St | Network | KENCB14 | 09/09/2025 | 09:15 | 09/09/2025 | 09:33 | 0.0464 | 0.0034 | 350 | 4766 | Unplanned | Defective Equipment | Cable joint fails
631 |  | INCD-7919-K | Kent St | Private | KENCB2 | 04/10/2025 | 07:14 | 04/10/2025 | 08:42 | 0.0343 | 0.0004 | 40 | 3520 | Unplanned | Third_party | Temp Disconnect / safety isolation
632 |  | INCD-626-M | Kent | Network | KENCB2 | 17/03/2026 | 00:12 | 17/03/2026 | 00:39 | 0.0105 | 0.0004 | 40 | 1080 | Planned | Planned | Mixed Asset Replacement
633 |  | INCD-6883-K | Kent St | Network | KENCB2 | 09/09/2025 | 09:15 | 09/09/2025 | 09:33 | 0.0525 | 0.003 | 312 | 5392 | Unplanned | Defective Equipment | Cable joint fails
634 |  | INCD-6883-K | Kent St | Network | KENCB3 | 09/09/2025 | 09:15 | 09/09/2025 | 09:33 | 0.1033 | 0.0061 | 629 | 10603 | Unplanned | Defective Equipment | Cable joint fails
635 |  | INCD-1379-K | Kent St | Network | KENCB3 | 17/04/2025 | 09:01 | 17/04/2025 | 14:36 | 0.2056 | 0.0006 | 63 | 21105 | Planned | Planned | Distribution Transformer Replacement
636 |  | INCD-6883-K | Kent St | Network | KENCB4 | 09/09/2025 | 09:15 | 09/09/2025 | 09:33 | 0.1372 | 0.0083 | 853 | 14084 | Unplanned | Defective Equipment | Cable joint fails
637 |  | INCD-11837-K | Kent St | Network | KENCB4 | 17/02/2026 | 23:15 | 18/02/2026 | 00:46 | 0.4418 | 0.0083 | 855 | 45345 | Unplanned | Defective Equipment | Cable fails unknown
638 |  | INCD-11872-K | Kent St | Network | KENCB4 | 18/02/2026 | 00:20 | 18/02/2026 | 00:22 | 0.0093 | 0.0056 | 571 | 952 | Unplanned | Defective Equipment | Cable fails unknown
639 |  | INCD-11991-K | Kent St | Network | KENCB4 | 22/02/2026 | 21:19 | 22/02/2026 | 22:01 | 0.0004 | 0 | 1 | 42 | Unplanned | Defective Equipment | Cable termination fails
640 |  | INCD-12082-K | Kent St | Network | KENCB4 | 26/02/2026 | 19:04 | 26/02/2026 | 19:18 | 0.0001 | 0 | 1 | 14 | Unplanned | Defective Equipment | Cable fails unknown
641 |  | INCD-11960-K | Kent St | Network | KENCB4 | 21/02/2026 | 10:59 | 21/02/2026 | 11:33 | 0.0003 | 0 | 1 | 34 | Unplanned | Defective Equipment | Cable fails unknown
642 |  | INCD-12802-K | Kent St | Network | KENCB4 | 30/03/2026 | 22:55 | 30/03/2026 | 23:53 | 0.0267 | 0.0005 | 48 | 2742 | Unplanned | Defective Equipment | Loss or failure of oil
643 |  | INCD-6883-K | Kent St | Network | KENCB7 | 09/09/2025 | 09:15 | 09/09/2025 | 09:33 | 0.0378 | 0.0024 | 243 | 3880 | Unplanned | Defective Equipment | Cable joint fails
644 |  | INCD-6883-K | Kent St | Network | KENCB9 | 09/09/2025 | 09:15 | 09/09/2025 | 09:33 | 0.0393 | 0.003 | 313 | 4032 | Unplanned | Defective Equipment | Cable joint fails
645 |  | INCD-6883-K | Kent St | Network | KILCB6 | 09/09/2025 | 09:15 | 09/09/2025 | 09:33 | 0.1371 | 0.0078 | 798 | 14071 | Unplanned | Defective Equipment | Cable joint fails
646 |  | INCD-390-L | Killarney Rd | Network | KILCB6 | 10/07/2025 | 13:33 | 10/07/2025 | 13:38 | 0.0032 | 0.0006 | 66 | 330 | Unplanned | Defective Equipment | Trip mechanism fails
647 |  | INCD-11452-K | Pukete | Network | KOHCB4 | 04/02/2026 | 09:15 | 04/02/2026 | 09:55 | 0.0035 | 0.0001 | 9 | 360 | Planned | Planned | OTHER Maintenance
648 |  | INCD-342-M | Pukete | Network | KOHCB4 | 18/09/2025 | 09:50 | 18/09/2025 | 17:31 | 0.0033 | 0.0001 | 9 | 342 | Planned | Planned | OTHER Maintenance
649 |  | INCD-4710-K | Pukete | Network | KOHCB4 | 18/07/2025 | 10:16 | 18/07/2025 | 16:36 | 0.0074 | 0 | 2 | 760 | Unplanned | Third_party | Cable isolated - safety reasons
650 |  | INCD-379-M | Pukete | Network | KOHCB4 | 27/11/2025 | 08:03 | 27/11/2025 | 17:09 | 0.0798 | 0.0001 | 15 | 8190 | Planned | Planned | Mixed Asset Replacement
651 |  | INCD-341-M | Pukete | Network | KOHCB4 | 17/09/2025 | 08:56 | 17/09/2025 | 14:22 | 0.0093 | 0.0003 | 34 | 950 | Planned | Planned | OTHER Maintenance
652 |  | INCD-11457-K | Pukete | Network | KOHCB4 | 04/02/2026 | 10:30 | 04/02/2026 | 10:55 | 0.0002 | 0 | 1 | 25 | Planned | Planned | OTHER Maintenance
653 |  | INCD-635-M | Horotiu | Network | KOHCB6 | 08/03/2026 | 08:02 | 08/03/2026 | 12:44 | 0.0027 | 0 | 1 | 282 | Planned | Planned | OTHER Maintenance
654 |  | INCD-161-M | Horotiu | Network | KOHCB6 | 11/07/2025 | 09:20 | 11/07/2025 | 11:21 | 0.0342 | 0.0003 | 29 | 3509 | Planned | Planned | Crossarm Replacement
655 |  | INCD-10951-K | Horotiu | Network | KOHCB6 | 21/01/2026 | 22:00 | 22/01/2026 | 00:00 | 0.0058 | 0 | 5 | 600 | Unplanned | Unknown | All Ok - Fault cause not established
656 |  | INCD-7136-K | Horotiu | Network | KOHCB6 | 14/09/2025 | 12:11 | 14/09/2025 | 13:41 | 0.014 | 0.0002 | 16 | 1440 | Unplanned | Defective Equipment | Unsafe/Damaged pillar
657 |  | INCD-8746-K | Horotiu | Network | KOHCB6 | 09/11/2025 | 09:49 | 09/11/2025 | 11:15 | 0.0717 | 0.005 | 511 | 7358 | Unplanned | Unknown | All Ok - Fault cause not established
658 |  | INCD-389-L | Horotiu | Network | KOHCB6 | 10/07/2025 | 12:19 | 10/07/2025 | 15:38 | 0.0116 | 0.0001 | 6 | 1194 | Unplanned | Defective Equipment | Intnl insulation failure
659 |  | INCD-6494-K | Horotiu | Network | KOHCB6 | 01/09/2025 | 12:05 | 01/09/2025 | 15:53 | 0.0914 | 0.0005 | 49 | 9385 | Unplanned | Defective Equipment | Broken binder
660 |  | INCD-470-M | Horotiu | Network | KOHCB6 | 18/12/2025 | 09:33 | 18/12/2025 | 16:25 | 0.0465 | 0.0001 | 12 | 4776 | Planned | Planned | Mixed Asset Replacement
661 |  | INCD-7664-K | Horotiu | Network | KOHCB6 | 27/09/2025 | 11:26 | 27/09/2025 | 14:31 | 0.0108 | 0.0001 | 6 | 1110 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
662 |  | INCD-24-M | Horotiu | Network | KOHCB6 | 24/04/2025 | 09:12 | 24/04/2025 | 13:33 | 0.0127 | 0 | 5 | 1305 | Planned | Planned | ABS Replacement
663 |  | INCD-1736-K | Horotiu | Network | KOHCB6 | 26/04/2025 | 07:57 | 26/04/2025 | 09:22 | 0.0132 | 0.0002 | 16 | 1360 | Unplanned | Defective Equipment | Contact problem
664 |  | INCD-2091-K | Horotiu | Network | KOHCB6 | 05/05/2025 | 20:22 | 06/05/2025 | 01:49 | 0.131 | 0.0009 | 95 | 13448 | Unplanned | Defective Equipment | Mechanism seized
665 |  | INCD-203-M | Horotiu | Network | KOHCB6 | 01/08/2025 | 08:37 | 01/08/2025 | 16:00 | 0.3426 | 0.001 | 101 | 35161 | Planned | Planned | New Connections
666 |  | INCD-10690-K | Latham Court | Network | LATCB1 | 15/01/2026 | 22:36 | 16/01/2026 | 05:32 | 0.5634 | 0.0014 | 139 | 57824 | Unplanned | Defective Equipment | Loss or failure of oil
667 |  | INCD-4088-K | Latham Court | Network | LATCB1 | 02/07/2025 | 09:05 | 02/07/2025 | 10:42 | 0.1367 | 0.0016 | 162 | 14034 | Planned | Planned | RMU Replacement
668 |  | INCD-4037-K | Latham Court | Network | LATCB1 | 30/06/2025 | 05:01 | 30/06/2025 | 05:21 | 0.0086 | 0.0004 | 44 | 880 | Planned | Planned | RMU Replacement
669 |  | INCD-3642-K | Latham | Network | LATCB1 | 13/06/2025 | 21:03 | 13/06/2025 | 21:18 | 0.0006 | 0 | 4 | 60 | Planned | Planned | RMU Replacement
670 |  | INCD-4112-K | Latham | Network | LATCB1 | 03/07/2025 | 05:04 | 03/07/2025 | 07:56 | 0.1787 | 0.0016 | 162 | 18344 | Planned | Planned | RMU Replacement
671 |  | INCD-4053-K | Latham | Network | LATCB1 | 01/07/2025 | 05:01 | 01/07/2025 | 06:01 | 0.0492 | 0.0011 | 111 | 5051 | Planned | Planned | RMU Replacement
672 |  | INCD-12067-K | Latham Court | Network | LATCB1 | 25/02/2026 | 18:48 | 25/02/2026 | 19:45 | 0.3944 | 0.0104 | 1064 | 40485 | Unplanned | Defective Equipment | Cable fails unknown
673 |  | INCD-402-L | Latham Court | Network | LATCB1 | 09/07/2025 | 15:01 | 09/07/2025 | 15:37 | 0.0288 | 0.0008 | 82 | 2952 | Planned | Planned | Mixed Asset Replacement
674 |  | INCD-4239-K | Latham | Network | LATCB1 | 07/07/2025 | 09:03 | 07/07/2025 | 17:49 | 0.4202 | 0.0008 | 82 | 43132 | Planned | Planned | Mixed Asset Replacement
675 |  | INCD-248-M | Latham | Network | LATCB1 | 16/07/2025 | 09:02 | 16/07/2025 | 09:49 | 0.0366 | 0.0008 | 80 | 3759 | Planned | Planned | Mixed Asset Replacement
676 |  | INCD-5-N | Latham | Network | LATCB1 | 02/07/2025 | 05:02 | 02/07/2025 | 05:29 | 0.0176 | 0.0007 | 67 | 1809 | Planned | Planned | RMU Replacement
677 |  | INCD-3780-K | Latham | Network | LATCB1 | 17/06/2025 | 23:07 | 17/06/2025 | 23:22 | 0.0016 | 0.0001 | 11 | 165 | Planned | Planned | RMU Replacement
678 |  | INCD-3608-K | Latham Court | Network | LATCB1 | 13/06/2025 | 06:03 | 13/06/2025 | 06:42 | 0.0015 | 0 | 4 | 156 | Planned | Planned | RMU Replacement
679 |  | INCD-404-M | Latham | Network | LATCB1 | 22/11/2025 | 18:03 | 22/11/2025 | 20:03 | 0.0023 | 0 | 2 | 240 | Planned | Planned | OTHER Maintenance
680 |  | INCD-399-M | Latham | Network | LATCB1 | 13/11/2025 | 09:25 | 13/11/2025 | 13:12 | 0.3074 | 0.0014 | 139 | 31553 | Planned | Planned | OTHER Maintenance
681 |  | INCD-3644-K | Latham Court | Private | LATCB1 | 13/06/2025 | 23:01 | 13/06/2025 | 23:22 | 0.0023 | 0.0001 | 11 | 231 | Unplanned | Third_party | Temp Disconnect / safety isolation
682 |  | INCD-402-M | Latham | Network | LATCB2 | 11/11/2025 | 09:08 | 11/11/2025 | 15:40 | 0.8555 | 0.0022 | 224 | 87808 | Planned | Planned | Mixed Asset Replacement
683 |  | INCD-9238-K | Latham | Network | LATCB2 | 25/11/2025 | 09:12 | 25/11/2025 | 09:37 | 0.0278 | 0.0011 | 114 | 2850 | Unplanned | Defective Equipment | Broken insulator/bush
684 |  | INCD-9171-K | Latham Court | Network | LATCB2 | 22/11/2025 | 01:33 | 22/11/2025 | 08:42 | 0.6413 | 0.0034 | 349 | 65826 | Unplanned | Defective Equipment | Broken insulator/bush
685 |  | INCD-454-M | Latham | Network | LATCB2 | 09/12/2025 | 09:16 | 09/12/2025 | 12:57 | 0.1033 | 0.0005 | 48 | 10608 | Planned | Planned | OTHER Maintenance
686 |  | INCD-4039-K | Latham Court | Network | LATCB2 | 30/06/2025 | 08:07 | 30/06/2025 | 13:47 | 0.2948 | 0.0009 | 89 | 30260 | Planned | Planned | Distribution Transformer Replacement
687 |  | INCD-12467-K | Latham | Network | LATCB2 | 18/03/2026 | 09:12 | 18/03/2026 | 14:52 | 0.3341 | 0.001 | 101 | 34296 | Planned | Planned | OTHER Maintenance
688 |  | INCD-12067-K | Latham Court | Network | LATCB2 | 25/02/2026 | 18:48 | 25/02/2026 | 19:45 | 0.6053 | 0.0131 | 1341 | 62127 | Unplanned | Defective Equipment | Cable fails unknown
689 |  | INCD-2700-K | Latham Court | Network | LATCB2 | 21/05/2025 | 09:51 | 21/05/2025 | 10:39 | 0.0005 | 0 | 1 | 47 | Unplanned | Defective Equipment | Wear or shear of pins
690 |  | INCD-9796-K | Latham | Network | LATCB2 | 17/12/2025 | 07:32 | 17/12/2025 | 13:38 | 0.1712 | 0.0005 | 48 | 17568 | Planned | Planned | Transformer Upgrade
691 |  | INCD-4142-K | Latham | Network | LATCB2 | 03/07/2025 | 16:04 | 03/07/2025 | 16:45 | 0.0356 | 0.0009 | 89 | 3649 | Planned | Planned | Distribution Transformer Replacement
692 |  | INCD-453-M | Latham | Network | LATCB2 | 09/12/2025 | 09:19 | 09/12/2025 | 13:06 | 0.2234 | 0.001 | 101 | 22927 | Planned | Planned | OTHER Maintenance
693 |  | INCD-1441-L | Latham | Network | LATCB2 | 24/11/2025 | 10:45 | 24/11/2025 | 14:31 | 0.1079 | 0.0005 | 49 | 11074 | Unplanned | Defective Equipment | Broken insulator/bush
694 |  | INCD-12067-K | Latham Court | Network | LATCB3 | 25/02/2026 | 18:48 | 25/02/2026 | 19:45 | 0.4767 | 0.0089 | 910 | 48928 | Unplanned | Defective Equipment | Cable fails unknown
695 |  | INCD-2699-K | Latham Court | Network | LATCB3 | 21/05/2025 | 09:51 | 21/05/2025 | 14:04 | 0.659 | 0.0088 | 907 | 67641 | Unplanned | Defective Equipment | Wear or shear of pins
696 |  | INCD-3412-K | Latham | Network | LATCB3 | 25/06/2025 | 09:02 | 25/06/2025 | 13:48 | 0.457 | 0.0016 | 164 | 46904 | Planned | Planned | Mixed Asset Replacement
697 |  | INCD-3208-K | Latham Court | Network | LATCB3 | 04/06/2025 | 09:03 | 04/06/2025 | 11:10 | 0.0557 | 0.0004 | 45 | 5715 | Planned | Planned | Crossarm Replacement
698 |  | INCD-2353-K | Latham Court | Network | LATCB5 | 07/05/2025 | 17:35 | 07/05/2025 | 18:22 | 0.0179 | 0.0004 | 39 | 1833 | Planned | Planned | Conductor Replacement
699 |  | INCD-65-L | Latham | Network | LATCB5 | 13/05/2025 | 08:08 | 13/05/2025 | 09:08 | 0.1127 | 0.0022 | 229 | 11565 | Planned | Planned | Conductor Replacement
700 |  | INCD-12067-K | Latham Court | Network | LATCB5 | 25/02/2026 | 18:48 | 25/02/2026 | 19:45 | 0.5218 | 0.016 | 1641 | 53557 | Unplanned | Defective Equipment | Cable fails unknown
701 |  | INCD-2700-K | Latham Court | Network | LATCB5 | 21/05/2025 | 09:51 | 21/05/2025 | 10:39 | 0.3937 | 0.0083 | 855 | 40413 | Unplanned | Defective Equipment | Wear or shear of pins
702 |  | INCD-8-M | Latham | Network | LATCB5 | 15/04/2025 | 09:30 | 15/04/2025 | 16:08 | 1.1085 | 0.0028 | 286 | 113776 | Planned | Planned | Conductor Replacement
703 |  | INCD-70-L | Latham | Network | LATCB5 | 13/05/2025 | 18:09 | 13/05/2025 | 18:54 | 0.1004 | 0.0022 | 229 | 10305 | Planned | Planned | Mixed Asset Replacement
704 |  | INCD-6-M | Latham | Network | LATCB5 | 02/04/2025 | 09:31 | 02/04/2025 | 17:32 | 1.5244 | 0.0033 | 335 | 156473 | Planned | Planned | Conductor Replacement
705 |  | INCD-55-L | Latham | Network | LATCB5 | 06/05/2025 | 09:34 | 06/05/2025 | 18:07 | 1.2172 | 0.0026 | 263 | 124936 | Planned | Planned | Conductor Replacement
706 |  | INCD-4118-K | Latham | Network | LATCB5 | 03/07/2025 | 09:39 | 03/07/2025 | 15:42 | 1.2977 | 0.0039 | 400 | 133198 | Planned | Planned | Conductor Replacement
707 |  | INCD-516-L | Latham Court | Network | LATCB5 | 08/08/2025 | 13:40 | 08/08/2025 | 17:17 | 0.0719 | 0.0003 | 34 | 7378 | Unplanned | Defective Equipment | Contact problem
708 |  | INCD-1982-K | Latham | Network | LATCB5 | 20/05/2025 | 09:08 | 20/05/2025 | 16:13 | 0.1443 | 0.0039 | 398 | 14812 | Planned | Planned | Conductor Replacement
709 |  | INCD-67-L | Latham | Network | LATCB5 | 13/05/2025 | 09:37 | 13/05/2025 | 16:10 | 0.1302 | 0.0003 | 34 | 13362 | Planned | Planned | Conductor Replacement
710 |  | INCD-91-M | Latham | Network | LATCB5 | 21/05/2025 | 11:05 | 21/05/2025 | 17:00 | 0.7653 | 0.0024 | 243 | 78548 | Planned | Planned | Mixed Asset Replacement
711 |  | INCD-8724-K | Latham Court | Private | LATCB5 | 07/11/2025 | 17:45 | 07/11/2025 | 18:00 | 0.0034 | 0.0002 | 23 | 345 | Unplanned | Defective Equipment | LVC - WEL & Customer
712 |  | INCD-7-M | Latham | Network | LATCB5 | 10/04/2025 | 09:39 | 10/04/2025 | 17:08 | 1.2342 | 0.0028 | 291 | 126677 | Planned | Planned | Conductor Replacement
713 |  | INCD-257-M | Latham | Network | LATCB5 | 21/08/2025 | 09:40 | 21/08/2025 | 14:52 | 0.5202 | 0.0017 | 177 | 53397 | Planned | Planned | Conductor Replacement
714 |  | INCD-8714-K | Latham Court | Private | LATCB5 | 07/11/2025 | 11:18 | 07/11/2025 | 11:35 | 0.0185 | 0.0011 | 112 | 1904 | Unplanned | Defective Equipment | LVC - WEL & Customer
715 |  | INCD-37-M | Latham | Network | LATCB5 | 29/04/2025 | 09:46 | 29/04/2025 | 16:50 | 0.9359 | 0.0022 | 229 | 96059 | Planned | Planned | Conductor Replacement
716 |  | INCD-5499-K | Latham Court | Network | LATCB5 | 08/08/2025 | 08:12 | 08/08/2025 | 11:05 | 0.4586 | 0.0145 | 1489 | 47068 | Unplanned | Defective Equipment | faulty line connection
717 |  | INCD-21-M | Latham | Network | LATCB6 | 06/04/2025 | 09:02 | 06/04/2025 | 14:43 | 0.0854 | 0.0003 | 26 | 8762 | Planned | Planned | RMU Replacement
718 |  | INCD-22-M | Latham | Network | LATCB6 | 15/04/2025 | 05:02 | 15/04/2025 | 05:53 | 0.011 | 0.0003 | 26 | 1131 | Planned | Planned | RMU Replacement
719 |  | INCD-12306-K | Latham Court | Network | LATCB6 | 10/03/2026 | 22:01 | 11/03/2026 | 04:45 | 0.1036 | 0.0003 | 27 | 10636 | Planned | Planned | RMU Replacement
720 |  | INCD-12067-K | Latham Court | Network | LATCB6 | 25/02/2026 | 18:48 | 25/02/2026 | 19:45 | 0.0436 | 0.0009 | 94 | 4474 | Unplanned | Defective Equipment | Cable fails unknown
721 |  | INCD-12067-K | Latham Court | Network | LATCB7 | 25/02/2026 | 18:48 | 25/02/2026 | 19:45 | 0.0039 | 0.0001 | 7 | 399 | Unplanned | Defective Equipment | Cable fails unknown
722 |  | INCD-12067-K | Latham Court | Network | LATCB8 | 25/02/2026 | 18:48 | 25/02/2026 | 19:45 | 0.0563 | 0.0021 | 218 | 5777 | Unplanned | Defective Equipment | Cable fails unknown
723 |  | INCD-9308-K | MAF | Network | MAFCB1 | 30/11/2025 | 08:02 | 30/11/2025 | 09:23 | 0.0008 | 0 | 1 | 81 | Planned | Planned | OTHER Maintenance
724 |  | INCD-10219-K | MAF | Network | MAFCB3 | 31/12/2025 | 15:57 | 31/12/2025 | 21:17 | 0.0031 | 0 | 1 | 320 | Unplanned | Defective Equipment | Cable fails unknown
725 |  | INCD-10302-K | MAF | Network | MAFCB3 | 02/01/2026 | 17:27 | 02/01/2026 | 17:32 | 0 | 0 | 1 | 5 | Unplanned | Defective Equipment | Cable fails unknown
726 |  | INCD-10251-K | MAF | Network | MAFCB3 | 02/01/2026 | 16:31 | 02/01/2026 | 17:32 | 0.0012 | 0 | 3 | 127 | Unplanned | Defective Equipment | Cable fails unknown
727 |  | INCD-10301-K | MAF | Network | MAFCB3 | 02/01/2026 | 17:10 | 02/01/2026 | 18:32 | 0.0008 | 0 | 1 | 82 | Unplanned | Defective Equipment | Cable fails unknown
728 |  | INCD-157-M | MAF | Network | MAFCB3 | 12/07/2025 | 09:49 | 12/07/2025 | 15:47 | 0.0088 | 0 | 3 | 906 | Planned | Planned | Mixed Asset Replacement
729 |  | INCD-9311-K | MAF | Network | MAFCB4 | 30/11/2025 | 13:50 | 30/11/2025 | 14:52 | 0.0006 | 0 | 1 | 63 | Planned | Planned | OTHER Maintenance
730 |  | INCD-157-M | MAF | Network | MAFCB6 | 12/07/2025 | 09:49 | 12/07/2025 | 15:47 | 0.0096 | 0 | 4 | 987 | Planned | Planned | Mixed Asset Replacement
731 |  | INCD-6883-K | Kent St | Network | MASCB12 | 09/09/2025 | 09:15 | 09/09/2025 | 09:33 | 0.2053 | 0.0116 | 1195 | 21072 | Unplanned | Defective Equipment | Cable joint fails
732 |  | INCD-11872-K | Kent St | Network | MASCB13 | 18/02/2026 | 00:20 | 18/02/2026 | 00:22 | 0.0001 | 0.0001 | 7 | 12 | Unplanned | Defective Equipment | Cable fails unknown
733 |  | INCD-12620-K | Massey St | Network | MASCB13 | 20/03/2026 | 15:35 | 20/03/2026 | 17:01 | 0.1818 | 0.0021 | 217 | 18662 | Planned | Planned | OTHER Maintenance
734 |  | INCD-12512-K | Massey St | Network | MASCB13 | 20/03/2026 | 08:25 | 20/03/2026 | 10:11 | 0.2235 | 0.0021 | 217 | 22937 | Planned | Planned | OTHER Maintenance
735 |  | INCD-6883-K | Kent St | Network | MASCB13 | 09/09/2025 | 09:15 | 09/09/2025 | 09:33 | 0.1196 | 0.0068 | 698 | 12280 | Unplanned | Defective Equipment | Cable joint fails
736 |  | INCD-6883-K | Kent St | Network | MASCB18 | 09/09/2025 | 09:15 | 09/09/2025 | 09:33 | 0.0148 | 0.0008 | 86 | 1516 | Unplanned | Defective Equipment | Cable joint fails
737 |  | INCD-1744-K | Weavers | Network | NGACB2 | 26/04/2025 | 16:02 | 26/04/2025 | 16:44 | 0.2544 | 0.0061 | 631 | 26113 | Unplanned | Third_party | Car in contact with pole
738 |  | INCD-3999-K | Whatawhata | Network | NGACB2 | 28/06/2025 | 00:00 | 28/06/2025 | 00:12 | 0.004 | 0.0003 | 35 | 409 | Planned | Planned | OTHER Maintenance
739 |  | INCD-4084-K | Te Uku Wind Farm | Network | NGACB2 | 02/07/2025 | 00:34 | 02/07/2025 | 00:46 | 0.0043 | 0.0003 | 35 | 440 | Planned | Planned | OTHER Maintenance
740 |  | INCD-9541-K | Ngaruawahia | Network | NGACB2 | 09/12/2025 | 09:31 | 09/12/2025 | 16:59 | 0.6952 | 0.0017 | 170 | 71353 | Planned | Planned | Mixed Asset Replacement
741 |  | INCD-6417-K | Ngaruawahia | Network | NGACB2 | 31/08/2025 | 18:21 | 01/09/2025 | 04:41 | 0.0784 | 0.0001 | 13 | 8052 | Unplanned | Defective Equipment | Faulty joint/connection
742 |  | INCD-5156-K | Ngaruawahia | Network | NGACB2 | 29/07/2025 | 07:33 | 29/07/2025 | 11:45 | 0.154 | 0.0033 | 341 | 15810 | Unplanned | Defective Equipment | Burning crossarm
743 |  | INCD-16-M | Raglan | Network | NGACB2 | 18/04/2025 | 14:51 | 18/04/2025 | 23:45 | 0.011 | 0.0007 | 70 | 1133 | Planned | Planned | OTHER Maintenance
744 |  | INCD-8781-K | Weavers | Network | NGACB2 | 11/11/2025 | 07:37 | 11/11/2025 | 07:45 | 0.0451 | 0.0065 | 667 | 4625 | Unplanned | Wildlife | Bird betw line & pole
745 |  | INCD-618-M | Ngaruawahia | Network | NGACB2 | 09/03/2026 | 09:31 | 09/03/2026 | 14:50 | 0.1988 | 0.0006 | 64 | 20402 | Planned | Planned | Crossarm Replacement
746 |  | INCD-12280-K | Te Uku | Network | NGACB2 | 09/03/2026 | 12:41 | 09/03/2026 | 12:50 | 0.0017 | 0.0002 | 20 | 178 | Unplanned | Human error | Tree felled into line (WEL)
747 |  | INCD-1437-K | Weavers | Network | NGACB2 | 17/04/2025 | 12:32 | 17/04/2025 | 13:10 | 0.2343 | 0.0061 | 631 | 24052 | Unplanned | Adverse weather | Line clash high wind
748 |  | INCD-445-M | Ngariuawahia | Network | NGACB2 | 01/12/2025 | 09:25 | 01/12/2025 | 13:58 | 0.1854 | 0.0007 | 73 | 19029 | Planned | Planned | 11kV Fuse Replacement
749 |  | INCD-81-L | Ngaruawahia | Network | NGACB2 | 04/06/2025 | 15:03 | 04/06/2025 | 16:23 | 0.0031 | 0 | 4 | 320 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
750 |  | INCD-8575-K | Ngaruawahia | Network | NGACB2 | 01/11/2025 | 13:54 | 01/11/2025 | 15:49 | 0.0011 | 0 | 1 | 115 | Unplanned | Unknown | All Ok - Fault cause not established
751 |  | INCD-8540-K | Te Uku | Network | NGACB2 | 30/10/2025 | 09:04 | 30/10/2025 | 15:00 | 0.0521 | 0.0001 | 15 | 5350 | Planned | Planned | Mixed Asset Replacement
752 |  | INCD-8362-K | Te Uku | Network | NGACB2 | 22/10/2025 | 07:21 | 22/10/2025 | 09:35 | 0.0441 | 0.0003 | 35 | 4523 | Unplanned | Unknown | All Ok - Fault cause not established
753 |  | INCD-12046-K | Ngaruawahia | Network | NGACB2 | 24/02/2026 | 16:26 | 24/02/2026 | 20:42 | 0.01 | 0 | 4 | 1024 | Unplanned | Defective Equipment | Contact problem
754 |  | INCD-643-M | Ngaruawahia | Network | NGACB2 | 13/03/2026 | 09:38 | 13/03/2026 | 13:22 | 0.0109 | 0 | 5 | 1120 | Planned | Planned | Mixed Asset Replacement
755 |  | INCD-8505-K | Te Uku | Network | NGACB2 | 29/10/2025 | 09:10 | 29/10/2025 | 15:35 | 0.075 | 0.0002 | 20 | 7700 | Planned | Planned | Mixed Asset Replacement
756 |  | INCD-8732-K | Ngaruawahia | Network | NGACB2 | 08/11/2025 | 09:48 | 08/11/2025 | 15:05 | 0.4706 | 0.0042 | 431 | 48308 | Unplanned | Defective Equipment | Contact problem
757 |  | INCD-4957-K | Ngaruawahia | Network | NGACB2 | 24/07/2025 | 07:32 | 24/07/2025 | 14:19 | 1.3949 | 0.0123 | 1264 | 143173 | Unplanned | Defective Equipment | Line break at twist joint
758 |  | INCD-2283-K | Ngaruawahia | Network | NGACB2 | 01/05/2025 | 09:50 | 09/05/2025 | 22:27 | 0.003 | 0 | 4 | 312 | Unplanned | Unknown | All Ok - Fault cause not established
759 |  | INCD-12500-K | Horotiu | Network | NGACB2 | 20/03/2026 | 02:21 | 20/03/2026 | 02:35 | 0.0558 | 0.0065 | 667 | 5725 | Unplanned | Unknown | All Ok - Fault cause not established
760 |  | INCD-1927-K | Ngaruawahia | Network | NGACB2 | 01/05/2025 | 07:56 | 01/05/2025 | 08:11 | 0.0641 | 0.0061 | 631 | 6584 | Unplanned | Vegetation | Tree known grows in line (IN Zone)
761 |  | INCD-9058-K | Ngaruawahia | Network | NGACB2 | 19/11/2025 | 09:07 | 19/11/2025 | 16:05 | 0.1345 | 0.0004 | 37 | 13810 | Planned | Planned | ABS Replacement
762 |  | INCD-262-M | Ngaruawahia | Network | NGACB2 | 22/08/2025 | 09:13 | 22/08/2025 | 14:18 | 0.0386 | 0.0001 | 13 | 3965 | Planned | Planned | Crossarm Replacement
763 |  | INCD-8539-K | Ngaruawahia | Network | NGACB2 | 30/10/2025 | 09:04 | 30/10/2025 | 15:00 | 0.1703 | 0.0005 | 49 | 17476 | Planned | Planned | Mixed Asset Replacement
764 |  | INCD-83-M | Ngaruawahia | Network | NGACB2 | 12/06/2025 | 09:12 | 12/06/2025 | 15:20 | 0.0511 | 0.0001 | 15 | 5245 | Planned | Planned | Distribution Transformer Replacement
765 |  | INCD-2284-K | Ngaruawahia | Network | NGACB2 | 09/05/2025 | 22:27 | 09/05/2025 | 23:43 | 0.1684 | 0.0061 | 631 | 17283 | Unplanned | Vegetation | Tree blown ovr on line (OUT of Zone)
766 |  | INCD-8772-K | Ngaruawahia | Network | NGACB3 | 09/11/2025 | 11:12 | 09/11/2025 | 11:39 | 0.0129 | 0.0005 | 49 | 1323 | Unplanned | Defective Equipment | Cable termination fails
767 |  | INCD-1437-K | Weavers | Network | NGACB3 | 17/04/2025 | 12:32 | 17/04/2025 | 13:10 | 0.3341 | 0.0089 | 912 | 34295 | Unplanned | Adverse weather | Line clash high wind
768 |  | INCD-8781-K | Weavers | Network | NGACB3 | 11/11/2025 | 07:37 | 11/11/2025 | 07:45 | 0.0719 | 0.009 | 921 | 7383 | Unplanned | Wildlife | Bird betw line & pole
769 |  | INCD-8771-K | Ngaruawahia | Network | NGACB3 | 09/11/2025 | 11:12 | 09/11/2025 | 11:38 | 0.0099 | 0.0004 | 39 | 1014 | Unplanned | Defective Equipment | Cable termination fails
770 |  | INCD-5166-K | Ngaruawahia | Network | NGACB3 | 29/07/2025 | 09:03 | 29/07/2025 | 17:13 | 0.0802 | 0.0002 | 17 | 8228 | Planned | Planned | ABS Replacement
771 |  | INCD-1744-K | Weavers | Network | NGACB3 | 26/04/2025 | 16:02 | 26/04/2025 | 16:44 | 0.3637 | 0.0089 | 912 | 37329 | Unplanned | Third_party | Car in contact with pole
772 |  | INCD-321-M | Ngaruawahia | Network | NGACB3 | 03/10/2025 | 08:31 | 03/10/2025 | 13:37 | 0.1775 | 0.0006 | 63 | 18221 | Planned | Planned | Mixed Asset Replacement
773 |  | INCD-12500-K | Horotiu | Network | NGACB3 | 20/03/2026 | 02:21 | 20/03/2026 | 02:35 | 0.0861 | 0.0091 | 934 | 8842 | Unplanned | Unknown | All Ok - Fault cause not established
774 |  | INCD-210-K | Ngaruawahia | Network | NGACB3 | 14/04/2025 | 08:08 | 14/04/2025 | 18:07 | 0.1197 | 0.0006 | 64 | 12284 | Planned | Planned | Mixed Asset Replacement
775 |  | INCD-634-M | Ngaruawahia | Network | NGACB3 | 07/03/2026 | 08:29 | 07/03/2026 | 12:01 | 0.1818 | 0.0009 | 88 | 18656 | Planned | Planned | OTHER Maintenance
776 |  | INCD-8704-K | Ngaruawahia | Network | NGACB3 | 06/11/2025 | 18:54 | 07/11/2025 | 00:21 | 0.2636 | 0.0009 | 88 | 27053 | Unplanned | Defective Equipment | Cable termination fails
777 |  | INCD-1437-K | Weavers | Network | NGACB5 | 17/04/2025 | 12:32 | 17/04/2025 | 13:10 | 0.2167 | 0.0057 | 587 | 22238 | Unplanned | Adverse weather | Line clash high wind
778 |  | INCD-1249-K | Horotiu | Private | NGACB5 | 14/04/2025 | 11:06 | 14/04/2025 | 19:33 | 0.0049 | 0 | 1 | 507 | Unplanned | Third_party | Temp Disconnect / safety isolation
779 |  | INCD-6395-K | Horotiu | Network | NGACB5 | 31/08/2025 | 17:25 | 31/08/2025 | 22:29 | 0.2849 | 0.0017 | 178 | 29242 | Unplanned | Vegetation | Tree blown ovr on line (OUT of Zone)
780 |  | INCD-8781-K | Weavers | Network | NGACB5 | 11/11/2025 | 07:37 | 11/11/2025 | 07:45 | 0.0848 | 0.0098 | 1001 | 8709 | Unplanned | Wildlife | Bird betw line & pole
781 |  | INCD-281-M | Ngaruawahia | Network | NGACB5 | 26/08/2025 | 08:42 | 26/08/2025 | 19:29 | 0.3848 | 0.0006 | 64 | 39494 | Planned | Planned | New Connections
782 |  | INCD-1465-K | Horotiu | Network | NGACB5 | 17/04/2025 | 14:27 | 17/04/2025 | 16:54 | 0.0014 | 0 | 1 | 147 | Unplanned | Vegetation | Wind debris on line (OUT of Zone)
783 |  | INCD-559-L | Ngaruawahia | Network | NGACB5 | 01/09/2025 | 15:31 | 01/09/2025 | 16:38 | 0.0547 | 0.0008 | 84 | 5613 | Unplanned | Vegetation | Tree blown ovr on line (OUT of Zone)
784 |  | INCD-269-M | Horotiu | Network | NGACB5 | 31/07/2025 | 10:00 | 31/07/2025 | 16:28 | 0.3057 | 0.0008 | 84 | 31373 | Planned | Planned | Pole Replacement
785 |  | INCD-1189-K | Horotiu | Private | NGACB5 | 11/04/2025 | 11:20 | 11/04/2025 | 16:25 | 0.003 | 0 | 1 | 305 | Unplanned | Third_party | Temp Disconnect / safety isolation
786 |  | INCD-3456-K | Horotiu | Private | NGACB5 | 10/06/2025 | 12:06 | 10/06/2025 | 16:07 | 0.0023 | 0 | 1 | 241 | Unplanned | Third_party | Temp Disconnect / safety isolation
787 |  | INCD-7257-K | Ngaruawahia | Network | NGACB5 | 17/09/2025 | 08:45 | 17/09/2025 | 19:40 | 0.0201 | 0 | 3 | 2058 | Planned | Planned | RMU Replacement
788 |  | INCD-12500-K | Horotiu | Network | NGACB5 | 20/03/2026 | 02:21 | 20/03/2026 | 02:35 | 0.1002 | 0.0098 | 1008 | 10282 | Unplanned | Unknown | All Ok - Fault cause not established
789 |  | INCD-1744-K | Weavers | Network | NGACB5 | 26/04/2025 | 16:02 | 26/04/2025 | 16:44 | 0.2352 | 0.0057 | 587 | 24145 | Unplanned | Third_party | Car in contact with pole
790 |  | INCD-12500-K | Horotiu | Network | NGACB6 | 20/03/2026 | 02:21 | 20/03/2026 | 02:35 | 0.0129 | 0.0009 | 96 | 1326 | Unplanned | Unknown | All Ok - Fault cause not established
791 |  | INCD-12655-K | Ngaruawahia | Network | NGACB6 | 26/03/2026 | 08:17 | 26/03/2026 | 12:39 | 0.1384 | 0.0009 | 96 | 14202 | Unplanned | Defective Equipment | Line break at twist joint
792 |  | INCD-4006-K | Ngaruawahia | Network | NGACB6 | 28/06/2025 | 07:49 | 28/06/2025 | 08:27 | 0.0116 | 0.0003 | 32 | 1194 | Unplanned | Unknown | All Ok - Fault cause not established
793 |  | INCD-1444-L | Ngaruawahia | Network | NGACB6 | 17/11/2025 | 03:26 | 17/11/2025 | 10:47 | 0.0129 | 0 | 3 | 1323 | Unplanned | Defective Equipment | Intnl insulation failure
794 |  | INCD-8456-K | Ngaruawahia | Network | NGACB6 | 28/10/2025 | 06:10 | 28/10/2025 | 07:51 | 0.0037 | 0 | 4 | 378 | Unplanned | Lightning | Lightning damage
795 |  | INCD-8967-K | Ngaruawahia | Network | NGACB6 | 16/11/2025 | 19:53 | 17/11/2025 | 14:50 | 0.288 | 0.0009 | 95 | 29565 | Unplanned | Third_party | Car in contact with pole
796 |  | INCD-1744-K | Weavers | Network | NGACB6 | 26/04/2025 | 16:02 | 26/04/2025 | 16:44 | 0.037 | 0.0009 | 95 | 3797 | Unplanned | Third_party | Car in contact with pole
797 |  | INCD-11888-K | Ngaruawahia | Network | NGACB6 | 19/02/2026 | 09:31 | 19/02/2026 | 16:57 | 0.1943 | 0.0005 | 49 | 19941 | Planned | Planned | Mixed Asset Replacement
798 |  | INCD-10516-K | Ngaruawahia | Network | NGACB6 | 12/01/2026 | 06:45 | 12/01/2026 | 09:27 | 0.0063 | 0 | 4 | 648 | Unplanned | Unknown | All Ok - Fault cause not established
799 |  | INCD-1437-K | Weavers | Network | NGACB6 | 17/04/2025 | 12:32 | 17/04/2025 | 13:10 | 0.0072 | 0.0009 | 95 | 739 | Unplanned | Adverse weather | Line clash high wind
800 |  | INCD-8781-K | Weavers | Network | NGACB6 | 11/11/2025 | 07:37 | 11/11/2025 | 07:45 | 0.0064 | 0.0009 | 95 | 659 | Unplanned | Wildlife | Bird betw line & pole
801 |  | INCD-6883-K | Kent St | Network | NORCB1 | 09/09/2025 | 09:15 | 09/09/2025 | 09:33 | 0.1333 | 0.0076 | 776 | 13683 | Unplanned | Defective Equipment | Cable joint fails
802 |  | INCD-3956-K | Avalon Dr | Network | NORCB1 | 26/06/2025 | 23:55 | 27/06/2025 | 06:15 | 0.0111 | 0 | 3 | 1139 | Unplanned | Third_party | Car in contact with pole
803 |  | INCD-395-M | Norton Rd | Network | NORCB1 | 05/11/2025 | 09:03 | 05/11/2025 | 13:14 | 0.4133 | 0.0016 | 169 | 42419 | Planned | Planned | Crossarm Replacement
804 |  | INCD-4075-K | Avalon Dr | Network | NORCB1 | 28/06/2025 | 05:07 | 28/06/2025 | 05:54 | 0.0014 | 0 | 3 | 141 | Unplanned | Third_party | Car in contact with pole
805 |  | INCD-331-M | Norton | Network | NORCB1 | 30/09/2025 | 09:13 | 30/09/2025 | 15:19 | 0.2496 | 0.0007 | 70 | 25620 | Planned | Planned | Pole Replacement
806 |  | INCD-6883-K | Kent St | Network | NORCB3 | 09/09/2025 | 09:15 | 09/09/2025 | 09:33 | 0.0174 | 0.001 | 101 | 1781 | Unplanned | Defective Equipment | Cable joint fails
807 |  | INCD-6883-K | Kent St | Network | NORCB4 | 09/09/2025 | 09:15 | 09/09/2025 | 09:33 | 0.0029 | 0.0002 | 17 | 300 | Unplanned | Defective Equipment | Cable joint fails
808 |  | INCD-6883-K | Kent St | Network | NORCB5 | 09/09/2025 | 09:15 | 09/09/2025 | 09:33 | 0.0588 | 0.0033 | 342 | 6031 | Unplanned | Defective Equipment | Cable joint fails
809 |  | INCD-12115-K | Peachgrove Rd | Network | PCHCB6 | 01/03/2026 | 08:17 | 01/03/2026 | 15:27 | 0.1631 | 0.0004 | 39 | 16739 | Planned | Planned | OTHER Maintenance
810 |  | INCD-621-M | Peacockes | Network | PEACB11 | 15/02/2026 | 08:08 | 15/02/2026 | 17:11 | 0.0053 | 0 | 1 | 543 | Planned | Planned | OTHER Maintenance
811 |  | INCD-680-L | Peacockes Rd | Network | PEACB11 | 07/10/2025 | 06:51 | 07/10/2025 | 09:54 | 0.0036 | 0 | 2 | 366 | Unplanned | Wildlife | Bird betw line & pole
812 |  | INCD-1591-K | Peacockes Rd | Network | PEACB11 | 19/04/2025 | 13:56 | 19/04/2025 | 14:38 | 0 | 0 | 1 | 4 | Unplanned | Vegetation | Wind debris on line (OUT of Zone)
813 |  | INCD-166-M | Peacockes | Network | PEACB12 | 18/07/2025 | 08:54 | 18/07/2025 | 16:06 | 0.1852 | 0.0004 | 44 | 19008 | Planned | Planned | OTHER Maintenance
814 |  | INCD-260-M | Peacockes | Network | PEACB12 | 29/08/2025 | 10:00 | 29/08/2025 | 12:35 | 0.1194 | 0.0008 | 83 | 12260 | Planned | Planned | Mixed Asset Replacement
815 |  | INCD-10649-K | Peacockes | Network | PEACB12 | 15/01/2026 | 03:23 | 15/01/2026 | 04:59 | 0.0655 | 0.0007 | 70 | 6720 | Unplanned | Unknown | All Ok - Fault cause not established
816 |  | INCD-8232-K | Peacockes | Private | PEACB12 | 15/10/2025 | 11:38 | 15/10/2025 | 11:55 | 0.0003 | 0 | 2 | 34 | Unplanned | Defective Equipment | LVC - WEL & Customer
817 |  | INCD-3582-K | Peacockes | Network | PEACB12 | 25/07/2025 | 10:08 | 25/07/2025 | 14:34 | 0.0207 | 0.0001 | 8 | 2128 | Planned | Planned | Crossarm Replacement
818 |  | INCD-149-M | Peacockes | Network | PEACB12 | 03/07/2025 | 09:00 | 03/07/2025 | 13:25 | 0.1202 | 0.001 | 104 | 12336 | Planned | Planned | ABS Replacement
819 |  | INCD-1591-K | Peacockes Rd | Network | PEACB12 | 19/04/2025 | 13:56 | 19/04/2025 | 14:38 | 0.1222 | 0.0085 | 873 | 12538 | Unplanned | Vegetation | Wind debris on line (OUT of Zone)
820 |  | INCD-96-M | Peacockes | Network | PEACB12 | 27/06/2025 | 08:32 | 27/06/2025 | 13:35 | 0.0531 | 0.0002 | 18 | 5454 | Planned | Planned | Mixed Asset Replacement
821 |  | INCD-683-M | Peacockes | Network | PEACB12 | 30/03/2026 | 12:37 | 30/03/2026 | 15:33 | 0.1457 | 0.0008 | 85 | 14960 | Planned | Planned | Crossarm Replacement
822 |  | INCD-8235-K | Peacockes Rd | Private | PEACB12 | 15/10/2025 | 13:33 | 15/10/2025 | 13:50 | 0.0005 | 0 | 3 | 51 | Unplanned | Defective Equipment | LVC - WEL & Customer
823 |  | INCD-11914-K | Peacockes | Network | PEACB12 | 19/02/2026 | 15:17 | 19/02/2026 | 16:15 | 0.0107 | 0.0002 | 19 | 1102 | Unplanned | Defective Equipment | Wear or shear of pins
824 |  | INCD-219-M | Peacockes | Network | PEACB12 | 08/08/2025 | 10:04 | 08/08/2025 | 16:30 | 0.1508 | 0.0004 | 41 | 15478 | Planned | Planned | Mixed Asset Replacement
825 |  | INCD-2351-K | Wallace Rd | Network | PEACB12 | 09/05/2025 | 22:57 | 09/05/2025 | 22:58 | 0.0019 | 0.0012 | 121 | 190 | Unplanned | Defective Equipment | Wear or shear of pins
826 |  | INCD-304-M | Peacockes | Network | PEACB12 | 18/09/2025 | 09:41 | 18/09/2025 | 15:55 | 0.1603 | 0.0004 | 44 | 16456 | Planned | Planned | Crossarm Replacement
827 |  | INCD-12133-K | Peacockes Rd | Network | PEACB12 | 02/03/2026 | 09:34 | 02/03/2026 | 13:12 | 0.0128 | 0.0001 | 6 | 1313 | Planned | Planned | Pole Replacement
828 |  | INCD-647-M | Peacockes | Network | PEACB12 | 25/02/2026 | 08:03 | 25/02/2026 | 10:42 | 0.0294 | 0.0002 | 19 | 3021 | Planned | Planned | New Connections
829 |  | INCD-2352-K | Peacockes Rd | Network | PEACB12 | 09/05/2025 | 22:57 | 09/05/2025 | 23:19 | 0.0135 | 0.0006 | 63 | 1382 | Unplanned | Defective Equipment | Wear or shear of pins
830 |  | INCD-7831-K | Peacockes Rd | Network | PEACB12 | 03/10/2025 | 02:21 | 03/10/2025 | 05:13 | 0.127 | 0.0022 | 228 | 13039 | Unplanned | Defective Equipment | faulty line connection
831 |  | INCD-5900-K | Peacockes Rd | Network | PEACB12 | 18/08/2025 | 00:22 | 18/08/2025 | 12:23 | 0.0126 | 0.0004 | 38 | 1295 | Unplanned | Defective Equipment | Broken Neutral
832 |  | INCD-3107-E | Peacockes | Network | PEACB12 | 01/04/2025 | 09:06 | 01/04/2025 | 12:47 | 0.0151 | 0.0001 | 7 | 1547 | Planned | Planned | Mixed Asset Replacement
833 |  | INCD-6609-K | Peacockes | Network | PEACB12 | 03/09/2025 | 10:01 | 03/09/2025 | 16:18 | 0.0653 | 0.0023 | 235 | 6701 | Planned | Planned | Mixed Asset Replacement
834 |  | INCD-677-L | Peacockes | Network | PEACB12 | 03/10/2025 | 11:57 | 03/10/2025 | 13:51 | 0.0455 | 0.0004 | 41 | 4674 | Unplanned | Defective Equipment | faulty line connection
835 |  | INCD-521-L | Peacockes Rd | Network | PEACB12 | 18/08/2025 | 00:22 | 18/08/2025 | 00:33 | 0.0254 | 0.0022 | 228 | 2607 | Unplanned | Unknown | All Ok - Fault cause not established
836 |  | INCD-6045-K | Peacockes Rd | Network | PEACB12 | 21/08/2025 | 10:48 | 21/08/2025 | 11:08 | 0.0032 | 0.0002 | 17 | 328 | Unplanned | Defective Equipment | Cable fails unknown
837 |  | INCD-289-M | Peacockes | Network | PEACB12 | 11/09/2025 | 09:51 | 11/09/2025 | 18:06 | 0.1591 | 0.0003 | 33 | 16335 | Planned | Planned | Mixed Asset Replacement
838 |  | INCD-233-M | Peacockes | Network | PEACB12 | 15/08/2025 | 10:09 | 15/08/2025 | 16:27 | 0.3058 | 0.0008 | 84 | 31384 | Planned | Planned | Mixed Asset Replacement
839 |  | INCD-446-M | Peacockes | Network | PEACB12 | 02/12/2025 | 09:25 | 02/12/2025 | 11:24 | 0.0267 | 0.0002 | 23 | 2737 | Planned | Planned | OTHER Maintenance
840 |  | INCD-529-M | Peacockes | Network | PEACB12 | 16/01/2026 | 09:46 | 16/01/2026 | 14:39 | 0.2241 | 0.0008 | 84 | 23004 | Planned | Planned | Mixed Asset Replacement
841 |  | INCD-7512-K | Peacockes Rd | Network | PEACB12 | 23/09/2025 | 10:05 | 23/09/2025 | 16:18 | 0.7792 | 0.0039 | 396 | 79984 | Planned | Planned | Crossarm Replacement
842 |  | INCD-523-L | Peacockes Rd | Network | PEACB12 | 18/08/2025 | 00:22 | 18/08/2025 | 00:41 | 0.0507 | 0.0026 | 271 | 5199 | Unplanned | Unknown | All Ok - Fault cause not established
843 |  | INCD-2280-K | Peacockes Rd | Network | PEACB12 | 09/05/2025 | 18:59 | 10/05/2025 | 03:27 | 0.3808 | 0.0028 | 290 | 39091 | Unplanned | Defective Equipment | Wear or shear of pins
844 |  | INCD-522-L | Peacockes Rd | Network | PEACB12 | 18/08/2025 | 00:22 | 18/08/2025 | 00:32 | 0.0136 | 0.0013 | 135 | 1393 | Unplanned | Unknown | All Ok - Fault cause not established
845 |  | INCD-2347-K | Peacockes | Network | PEACB12 | 12/05/2025 | 09:20 | 12/05/2025 | 11:34 | 0.0039 | 0 | 3 | 402 | Planned | Planned | Mixed Asset Replacement
846 |  | INCD-8675-K | Peacockes | Private | PEACB12 | 05/11/2025 | 08:51 | 05/11/2025 | 10:24 | 0.0127 | 0.0001 | 14 | 1302 | Unplanned | Third_party | Part power
847 |  | INCD-390-M | Peacockes | Network | PEACB12 | 30/10/2025 | 10:00 | 30/10/2025 | 13:25 | 0.4111 | 0.0022 | 228 | 42198 | Planned | Planned | Mixed Asset Replacement
848 |  | INCD-6796-K | Peacockes Rd | Network | PEACB12 | 07/09/2025 | 09:39 | 07/09/2025 | 17:11 | 0.2498 | 0.0008 | 84 | 25640 | Unplanned | Third_party | Car in contact with pole
849 |  | INCD-299-M | Peacockes | Network | PEACB12 | 09/09/2025 | 09:33 | 09/09/2025 | 16:15 | 0.0807 | 0.0002 | 21 | 8286 | Planned | Planned | Mixed Asset Replacement
850 |  | INCD-2988-K | Peacockes | Network | PEACB13 | 29/05/2025 | 08:38 | 29/05/2025 | 16:05 | 0.5574 | 0.0012 | 128 | 57216 | Planned | Planned | Mixed Asset Replacement
851 |  | INCD-2975-K | Peacockes Rd | Network | PEACB13 | 29/05/2025 | 00:06 | 29/05/2025 | 02:20 | 0.3625 | 0.004 | 407 | 37209 | Planned | Planned | OTHER Maintenance
852 |  | INCD-3062-K | Peacockes | Network | PEACB13 | 30/05/2025 | 00:01 | 30/05/2025 | 01:39 | 0.2312 | 0.004 | 407 | 23735 | Planned | Planned | OTHER Maintenance
853 |  | INCD-305-N | Peacockes | Network | PEACB13 | 28/03/2026 | 08:47 | 28/03/2026 | 16:08 | 0.5303 | 0.0019 | 194 | 54429 | Planned | Planned | ABS Replacement
854 |  | INCD-2988-K | Peacockes | Network | PEACB14 | 29/05/2025 | 08:38 | 29/05/2025 | 16:05 | 0.2177 | 0.0005 | 50 | 22350 | Planned | Planned | Mixed Asset Replacement
855 |  | INCD-2865-K | Peacockes Rd | Network | PEACB14 | 26/05/2025 | 09:04 | 26/05/2025 | 14:55 | 0.2599 | 0.0007 | 76 | 26676 | Planned | Planned | Mixed Asset Replacement
856 |  | INCD-436-M | Peacockes | Network | PEACB14 | 06/12/2025 | 08:01 | 06/12/2025 | 10:57 | 0.1303 | 0.0007 | 76 | 13376 | Planned | Planned | OTHER Maintenance
857 |  | INCD-3062-K | Peacockes | Network | PEACB14 | 30/05/2025 | 00:01 | 30/05/2025 | 01:39 | 0.0674 | 0.0007 | 76 | 6916 | Planned | Planned | OTHER Maintenance
858 |  | INCD-2975-K | Peacockes Rd | Network | PEACB14 | 29/05/2025 | 00:06 | 29/05/2025 | 02:20 | 0.0992 | 0.0007 | 76 | 10184 | Planned | Planned | OTHER Maintenance
859 |  | INCD-1825-L | Peacockes | Network | PEACB16 | 21/03/2026 | 09:00 | 21/03/2026 | 15:40 | 0.0147 | 0.0021 | 216 | 1512 | Planned | Planned | OTHER Maintenance
860 |  | INCD-10892-K | Peacockes | Network | PEACB16 | 21/01/2026 | 09:28 | 21/01/2026 | 09:45 | 0.0216 | 0.0017 | 175 | 2221 | Planned | Planned | Conductor Replacement
861 |  | INCD-12012-K | Peacockes | Network | PEACB16 | 21/03/2026 | 09:00 | 21/03/2026 | 15:18 | 0.0656 | 0.0034 | 350 | 6738 | Planned | Planned | OTHER Maintenance
862 |  | INCD-217-M | Peacockes | Network | PEACB16 | 25/07/2025 | 08:38 | 25/07/2025 | 13:39 | 0.0205 | 0.0001 | 7 | 2107 | Planned | Planned | New Connections
863 |  | INCD-11275-K | Peacockes Rd | Network | PEACB16 | 29/01/2026 | 09:23 | 29/01/2026 | 10:34 | 1.0526 | 0.0185 | 1896 | 108046 | Unplanned | Lightning | Spontaneous failure
864 |  | INCD-7290-K | Peacockes Rd | Network | PEACB16 | 17/09/2025 | 14:57 | 17/09/2025 | 19:04 | 0.0938 | 0.0004 | 39 | 9633 | Unplanned | Defective Equipment | Faulty joint/connection
865 |  | INCD-8342-K | Peacockes Rd | Network | PEACB16 | 21/10/2025 | 09:30 | 21/10/2025 | 15:52 | 1.0364 | 0.0028 | 288 | 106381 | Planned | Planned | Mixed Asset Replacement
866 |  | INCD-1730-L | Peacockes Rd | Network | PEACB16 | 21/01/2026 | 09:09 | 21/01/2026 | 09:19 | 0.017 | 0.0017 | 175 | 1750 | Planned | Unknown | OTHER Maintenance
867 |  | INCD-447-M | Peacockes | Network | PEACB16 | 27/11/2025 | 09:03 | 27/11/2025 | 15:35 | 0.0126 | 0.0021 | 216 | 1296 | Planned | Planned | Mixed Asset Replacement
868 |  | INCD-9642-K | Peacockes Rd | Network | PEACB16 | 11/12/2025 | 13:39 | 11/12/2025 | 14:34 | 0.1446 | 0.0163 | 1674 | 14843 | Unplanned | Unknown | All Ok - Fault cause not established
869 |  | INCD-392-M | Peacockes | Network | PEACB16 | 14/11/2025 | 13:01 | 14/11/2025 | 15:59 | 0.1826 | 0.0017 | 175 | 18745 | Planned | Planned | Distribution Transformer Replacement
870 |  | INCD-12463-K | Peacockes | Network | PEACB16 | 18/03/2026 | 08:31 | 18/03/2026 | 12:04 | 0.5693 | 0.0028 | 289 | 58439 | Planned | Planned | ABS Replacement
871 |  | INCD-8767-K | Peacockes | Network | PEACB16 | 10/11/2025 | 09:14 | 10/11/2025 | 14:54 | 0.2602 | 0.0017 | 175 | 26709 | Planned | Planned | Distribution Transformer Replacement
872 |  | INCD-1814-K | Peacockes Rd | Network | PEACB16 | 28/04/2025 | 12:49 | 28/04/2025 | 15:00 | 0.0509 | 0.0004 | 40 | 5229 | Unplanned | Unknown | All Ok - Fault cause not established
873 |  | INCD-6645-K | Peacockes Rd | Network | PEACB17 | 03/09/2025 | 19:29 | 03/09/2025 | 19:31 | 0.0042 | 0.0021 | 214 | 428 | Unplanned | Defective Equipment | Fuse blown on overload
874 |  | INCD-6655-K | Peacockes Rd | Network | PEACB17 | 03/09/2025 | 23:23 | 03/09/2025 | 23:29 | 0.0125 | 0.0021 | 214 | 1284 | Unplanned | Defective Equipment | Fuse blown on overload
875 |  | INCD-8769-K | Peacockes | Network | PEACB17 | 10/12/2025 | 09:00 | 10/12/2025 | 15:17 | 0.1105 | 0.0042 | 428 | 11342 | Planned | Planned | Mixed Asset Replacement
876 |  | INCD-8163-K | Peacockes Rd | Network | PEACB17 | 13/10/2025 | 05:09 | 13/10/2025 | 12:27 | 0.8628 | 0.0119 | 1226 | 88562 | Unplanned | Defective Equipment | Incorr Protect setting ld
877 |  | INCD-3878-K | Peacockes Rd | Network | PEACB17 | 21/06/2025 | 06:50 | 21/06/2025 | 14:31 | 0.9499 | 0.0094 | 968 | 97499 | Unplanned | Third_party | Car in contact with pole
878 |  | INCD-427-M | Peacockes | Network | PEACB17 | 27/11/2025 | 21:04 | 28/11/2025 | 02:24 | 0.0187 | 0.0001 | 6 | 1920 | Planned | Planned | OTHER Maintenance
879 |  | INCD-7244-K | Peacockes | Network | PEACB17 | 16/09/2025 | 16:08 | 16/09/2025 | 16:37 | 0.0297 | 0.001 | 105 | 3045 | Planned | Planned | Recloser & Sectionaliser replacement
880 |  | INCD-9274-K | Peacockes Rd | Private | PEACB17 | 27/11/2025 | 22:03 | 27/11/2025 | 22:16 | 0.0027 | 0.0002 | 21 | 273 | Unplanned | Defective Equipment | LVC - WEL & Customer
881 |  | INCD-8212-K | Peacockes | Network | PEACB17 | 14/10/2025 | 20:42 | 14/10/2025 | 21:02 | 0.0012 | 0.0001 | 6 | 120 | Unplanned | Defective Equipment | Cable fails unknown
882 |  | INCD-7196-K | Peacockes Rd | Network | PEACB17 | 16/09/2025 | 07:13 | 16/09/2025 | 07:47 | 0.0348 | 0.001 | 105 | 3570 | Planned | Planned | Recloser & Sectionaliser replacement
883 |  | INCD-523-L | Peacockes Rd | Network | PEACB17 | 18/08/2025 | 00:22 | 18/08/2025 | 00:41 | 0.0903 | 0.0047 | 483 | 9266 | Unplanned | Unknown | All Ok - Fault cause not established
884 |  | INCD-7207-K | Peacockes Rd | Network | PEACB17 | 16/09/2025 | 09:02 | 16/09/2025 | 15:31 | 0.811 | 0.0021 | 214 | 83246 | Planned | Planned | Recloser & Sectionaliser replacement
885 |  | INCD-450-M | Peacockes | Network | PEACB18 | 28/11/2025 | 09:06 | 28/11/2025 | 10:45 | 0.0048 | 0 | 5 | 495 | Planned | Planned | Crossarm Replacement
886 |  | INCD-127-M | Peacockes | Network | PEACB18 | 26/06/2025 | 09:31 | 26/06/2025 | 16:19 | 0.226 | 0.0006 | 59 | 23193 | Planned | Planned | Mixed Asset Replacement
887 |  | INCD-6046-K | Peacockes Rd | Network | PEACB18 | 21/08/2025 | 10:48 | 21/08/2025 | 12:02 | 0.0237 | 0.001 | 104 | 2433 | Unplanned | Defective Equipment | Cable fails unknown
888 |  | INCD-595-M | Peacockes | Network | PEACB18 | 17/02/2026 | 09:05 | 17/02/2026 | 15:50 | 0.0477 | 0.0001 | 13 | 4900 | Planned | Planned | Distribution Transformer Replacement
889 |  | INCD-101-M | Peacockes | Network | PEACB18 | 06/06/2025 | 10:08 | 06/06/2025 | 13:02 | 0.0119 | 0.0001 | 7 | 1218 | Planned | Planned | Crossarm Replacement
890 |  | INCD-12634-K | Pukete | Network | PUKCB10 | 25/03/2026 | 08:30 | 25/03/2026 | 16:02 | 0.2018 | 0.0005 | 48 | 20718 | Planned | Planned | ABS Replacement
891 |  | INCD-403-M | Pukete | Network | PUKCB2 | 19/11/2025 | 09:22 | 19/11/2025 | 10:19 | 0.0205 | 0.0004 | 37 | 2109 | Planned | Planned | OTHER Maintenance
892 |  | INCD-6041-K | Pukete | Network | PUKCB2 | 21/08/2025 | 09:52 | 21/08/2025 | 16:38 | 0.0923 | 0.0002 | 24 | 9478 | Planned | Planned | Pole Replacement
893 |  | INCD-1664-L | Pukete | Network | PUKCB2 | 18/12/2025 | 06:05 | 18/12/2025 | 17:29 | 0.0067 | 0 | 1 | 684 | Planned | Planned | OTHER Maintenance
894 |  | INCD-9217-K | Pukete | Network | PUKCB2 | 24/11/2025 | 09:07 | 24/11/2025 | 10:57 | 0.0064 | 0.0001 | 6 | 660 | Unplanned | Defective Equipment | Cond not fully in sleeve
895 |  | INCD-4844-K | Pukete | Network | PUKCB2 | 22/07/2025 | 07:38 | 22/07/2025 | 16:16 | 0.0051 | 0 | 1 | 519 | Planned | Planned | OTHER Maintenance
896 |  | INCD-430-L | Pukete | Network | PUKCB4 | 12/07/2025 | 15:51 | 12/07/2025 | 16:15 | 0.0002 | 0 | 1 | 24 | Unplanned | Defective Equipment | Cable termination fails
897 |  | INCD-1607-L | Pukete | Network | PUKCB4 | 04/12/2025 | 06:42 | 04/12/2025 | 07:34 | 0.003 | 0.0001 | 6 | 312 | Planned | Planned | Transformer Upgrade
898 |  | INCD-8700-K | Pukete | Network | PUKCB4 | 11/12/2025 | 06:40 | 11/12/2025 | 17:20 | 0.0099 | 0.0001 | 12 | 1014 | Planned | Planned | Transformer Upgrade
899 |  | INCD-4426-K | Pukete | Network | PUKCB4 | 11/07/2025 | 07:14 | 11/07/2025 | 12:09 | 0.0284 | 0.0011 | 116 | 2913 | Unplanned | Defective Equipment | Cable termination fails
900 |  | INCD-342-M | Pukete | Network | PUKCB4 | 18/09/2025 | 09:50 | 18/09/2025 | 17:31 | 0.0044 | 0.0001 | 12 | 456 | Planned | Planned | OTHER Maintenance
901 |  | INCD-429-L | Pukete | Network | PUKCB4 | 12/07/2025 | 12:39 | 12/07/2025 | 13:54 | 0.0007 | 0 | 1 | 75 | Unplanned | Defective Equipment | Cable termination fails
902 |  | INCD-3999-K | Whatawhata | Network | RAGCB2 | 28/06/2025 | 00:00 | 28/06/2025 | 00:12 | 0.0905 | 0.0077 | 794 | 9290 | Planned | Planned | OTHER Maintenance
903 |  | INCD-8231-K | Raglan | Network | RAGCB2 | 15/10/2025 | 09:51 | 15/10/2025 | 17:58 | 0.2788 | 0.0021 | 212 | 28617 | Planned | Planned | Pole Replacement
904 |  | INCD-362-M | Raglan | Network | RAGCB2 | 23/10/2025 | 09:39 | 23/10/2025 | 15:42 | 0.1023 | 0.0032 | 328 | 10496 | Planned | Planned | OTHER Maintenance
905 |  | INCD-16-M | Raglan | Network | RAGCB2 | 18/04/2025 | 14:51 | 18/04/2025 | 23:45 | 0.1847 | 0.0154 | 1582 | 18963 | Planned | Planned | OTHER Maintenance
906 |  | INCD-361-M | Raglan | Network | RAGCB2 | 22/10/2025 | 09:38 | 22/10/2025 | 15:28 | 0.0784 | 0.0002 | 23 | 8050 | Planned | Planned | Mixed Asset Replacement
907 |  | INCD-5734-K | Raglan | Network | RAGCB2 | 14/08/2025 | 05:19 | 14/08/2025 | 07:36 | 0.0307 | 0.0002 | 23 | 3151 | Unplanned | Defective Equipment | Wear or shear of pins
908 |  | INCD-8198-K | Raglan | Network | RAGCB2 | 14/10/2025 | 09:36 | 14/10/2025 | 10:10 | 0.0222 | 0.0007 | 67 | 2278 | Planned | Planned | Pole Replacement
909 |  | INCD-8206-K | Raglan | Network | RAGCB2 | 14/10/2025 | 15:00 | 14/10/2025 | 15:18 | 0.0117 | 0.0007 | 67 | 1206 | Planned | Planned | Pole Replacement
910 |  | INCD-8093-K | Raglan | Network | RAGCB2 | 08/10/2025 | 15:59 | 08/10/2025 | 16:03 | 0.0317 | 0.0077 | 794 | 3255 | Unplanned | Human error | Unintentionally Disabled
911 |  | INCD-10141-K | Raglan | Network | RAGCB2 | 29/12/2025 | 16:10 | 29/12/2025 | 23:09 | 0.5181 | 0.0012 | 127 | 53181 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
912 |  | INCD-4084-K | Te Uku Wind Farm | Network | RAGCB2 | 02/07/2025 | 00:34 | 02/07/2025 | 00:46 | 0.0972 | 0.0077 | 794 | 9978 | Planned | Planned | OTHER Maintenance
913 |  | INCD-11521-K | Raglan | Network | RAGCB3 | 06/02/2026 | 09:56 | 06/02/2026 | 10:17 | 0.0151 | 0.0007 | 75 | 1547 | Unplanned | Unknown | All Ok - Fault cause not established
914 |  | INCD-10206-K | Raglan | Network | RAGCB3 | 30/12/2025 | 16:57 | 31/12/2025 | 10:01 | 0.02 | 0 | 2 | 2048 | Unplanned | Unknown | All Ok - Fault cause not established
915 |  | INCD-16-M | Raglan | Network | RAGCB3 | 18/04/2025 | 14:51 | 18/04/2025 | 23:45 | 0.0179 | 0.0015 | 150 | 1837 | Planned | Planned | OTHER Maintenance
916 |  | INCD-3999-K | Whatawhata | Network | RAGCB3 | 28/06/2025 | 00:00 | 28/06/2025 | 00:12 | 0.0085 | 0.0007 | 75 | 877 | Planned | Planned | OTHER Maintenance
917 |  | INCD-4084-K | Te Uku Wind Farm | Network | RAGCB3 | 02/07/2025 | 00:34 | 02/07/2025 | 00:46 | 0.0092 | 0.0007 | 75 | 942 | Planned | Planned | OTHER Maintenance
918 |  | INCD-4084-K | Te Uku Wind Farm | Network | RAGCB4 | 02/07/2025 | 00:34 | 02/07/2025 | 00:46 | 0.0802 | 0.0064 | 655 | 8231 | Planned | Planned | OTHER Maintenance
919 |  | INCD-16-M | Raglan | Network | RAGCB4 | 18/04/2025 | 14:51 | 18/04/2025 | 23:45 | 0.158 | 0.0127 | 1308 | 16219 | Planned | Planned | OTHER Maintenance
920 |  | INCD-6883-K | Kent St | Network | RAGCB4 | 09/09/2025 | 09:15 | 09/09/2025 | 09:33 | 0.0002 | 0 | 1 | 18 | Unplanned | Defective Equipment | Cable joint fails
921 |  | INCD-3999-K | Whatawhata | Network | RAGCB4 | 28/06/2025 | 00:00 | 28/06/2025 | 00:12 | 0.0747 | 0.0064 | 655 | 7663 | Planned | Planned | OTHER Maintenance
922 |  | INCD-1770-L | Raglan | Network | RAGCB4 | 29/01/2026 | 00:17 | 29/01/2026 | 01:12 | 0.0857 | 0.0016 | 160 | 8800 | Unplanned | Defective Equipment | Bus chamber flashovr
923 |  | INCD-11194-K | Raglan | Network | RAGCB4 | 27/01/2026 | 10:08 | 27/01/2026 | 17:50 | 0.7524 | 0.0064 | 656 | 77233 | Unplanned | Defective Equipment | Bus chamber flashovr
924 |  | INCD-10158-K | Raglan | Network | RAGCB4 | 29/12/2025 | 21:13 | 30/12/2025 | 00:12 | 0.2193 | 0.0016 | 161 | 22506 | Unplanned | Defective Equipment | Connect/jumper loose
925 |  | INCD-1769-L | Raglan | Network | RAGCB4 | 29/01/2026 | 01:26 | 30/01/2026 | 01:46 | 0.1907 | 0.0013 | 132 | 19576 | Unplanned | Defective Equipment | Bus chamber flashovr
926 |  | INCD-16-M | Raglan | Network | RAGCB5 | 18/04/2025 | 14:51 | 18/04/2025 | 23:45 | 0.0374 | 0.003 | 308 | 3837 | Planned | Planned | OTHER Maintenance
927 |  | INCD-5079-K | Raglan | Network | RAGCB5 | 27/07/2025 | 10:46 | 27/07/2025 | 13:08 | 0.0565 | 0.0004 | 41 | 5796 | Unplanned | Unknown | All Ok - Fault cause not established
928 |  | INCD-6378-K | Raglan | Network | RAGCB5 | 31/08/2025 | 16:46 | 01/09/2025 | 05:41 | 0.2338 | 0.0003 | 31 | 24003 | Unplanned | Adverse weather | Line clash high wind
929 |  | INCD-3999-K | Whatawhata | Network | RAGCB5 | 28/06/2025 | 00:00 | 28/06/2025 | 00:12 | 0.0176 | 0.0015 | 154 | 1802 | Planned | Planned | OTHER Maintenance
930 |  | INCD-6474-K | Raglan | Network | RAGCB5 | 01/09/2025 | 09:39 | 01/09/2025 | 09:58 | 0.0076 | 0.0004 | 41 | 779 | Unplanned | Unknown | All Ok - Fault cause not established
931 |  | INCD-4084-K | Te Uku Wind Farm | Network | RAGCB5 | 02/07/2025 | 00:34 | 02/07/2025 | 00:46 | 0.0189 | 0.0015 | 154 | 1935 | Planned | Planned | OTHER Maintenance
932 |  | INCD-1446-L | Raglan | Network | RAGCB6 | 28/10/2025 | 10:13 | 28/10/2025 | 11:17 | 0.0006 | 0 | 1 | 64 | Planned | Planned | OTHER Maintenance
933 |  | INCD-150-M | Raglan | Network | RAGCB6 | 14/07/2025 | 08:34 | 14/07/2025 | 13:40 | 0.0328 | 0.0001 | 11 | 3366 | Planned | Planned | Crossarm Replacement
934 |  | INCD-11194-K | Raglan | Network | RAGCB6 | 27/01/2026 | 10:08 | 27/01/2026 | 17:50 | 0.0786 | 0.0054 | 557 | 8067 | Unplanned | Defective Equipment | Bus chamber flashovr
935 |  | INCD-525-M | Raglan | Network | RAGCB6 | 10/01/2026 | 08:14 | 10/01/2026 | 14:53 | 0.0039 | 0 | 1 | 399 | Planned | Planned | Distribution Transformer Replacement
936 |  | INCD-11025-K | Raglan | Network | RAGCB6 | 22/01/2026 | 12:28 | 22/01/2026 | 15:47 | 0.0291 | 0.0001 | 15 | 2985 | Unplanned | Unknown | All Ok - Fault cause not established
937 |  | INCD-4084-K | Te Uku Wind Farm | Network | RAGCB6 | 02/07/2025 | 00:34 | 02/07/2025 | 00:46 | 0.125 | 0.0099 | 1021 | 12831 | Planned | Planned | OTHER Maintenance
938 |  | INCD-4434-K | Raglan | Network | RAGCB6 | 11/07/2025 | 08:32 | 11/07/2025 | 11:19 | 0.6158 | 0.004 | 410 | 63207 | Planned | Planned | Mixed Asset Replacement
939 |  | INCD-6911-K | Raglan | Network | RAGCB6 | 09/09/2025 | 15:06 | 09/09/2025 | 20:54 | 0.0237 | 0.0001 | 7 | 2436 | Unplanned | Third_party | Cable hit by digger
940 |  | INCD-3999-K | Whatawhata | Network | RAGCB6 | 28/06/2025 | 00:00 | 28/06/2025 | 00:12 | 0.1164 | 0.0099 | 1021 | 11946 | Planned | Planned | OTHER Maintenance
941 |  | INCD-6970-K | Raglan | Network | RAGCB6 | 10/09/2025 | 20:51 | 10/09/2025 | 21:28 | 0.0025 | 0.0001 | 7 | 259 | Unplanned | Third_party | Cable hit by digger
942 |  | INCD-4839-K | Raglan | Network | RAGCB6 | 21/07/2025 | 20:19 | 21/07/2025 | 23:24 | 0.0252 | 0.0001 | 14 | 2590 | Unplanned | Unknown | All Ok - Fault cause not established
943 |  | INCD-8275-K | Raglan | Network | RAGCB6 | 17/10/2025 | 09:45 | 17/10/2025 | 13:09 | 0.1903 | 0.0009 | 96 | 19531 | Planned | Planned | Crossarm Replacement
944 |  | INCD-260-N | Raglan | Network | RAGCB6 | 18/02/2026 | 08:43 | 18/02/2026 | 15:57 | 1.0199 | 0.0025 | 256 | 104682 | Planned | Planned | Mixed Asset Replacement
945 |  | INCD-197-M | Rural Bank | Network | RURCB10 | 02/07/2025 | 01:00 | 02/07/2025 | 04:34 | 0.0563 | 0.0003 | 27 | 5778 | Planned | Planned | OTHER Maintenance
946 |  | INCD-1400-L | Sandwich | Network | SANCB1 | 08/11/2025 | 07:33 | 08/11/2025 | 16:08 | 0.005 | 0 | 1 | 515 | Planned | Planned | OTHER Maintenance
947 |  | INCD-6108-K | Sandwich Rd | Network | SANCB1 | 23/08/2025 | 07:11 | 23/08/2025 | 09:55 | 0.0016 | 0 | 1 | 164 | Unplanned | Lightning | Spontaneous failure
948 |  | INCD-3021-K | Sandwich Rd | Private | SANCB2 | 29/05/2025 | 14:51 | 29/05/2025 | 16:02 | 0.0429 | 0.0006 | 62 | 4402 | Unplanned | Defective Equipment | LVC - WEL & Customer
949 |  | INCD-630-M | Sandwich | Network | SANCB2 | 15/02/2026 | 13:05 | 15/02/2026 | 13:43 | 0.023 | 0.0006 | 62 | 2356 | Planned | Planned | RMU Replacement
950 |  | INCD-11670-K | Sandwich Rd | Network | SANCB2 | 12/02/2026 | 07:02 | 12/02/2026 | 09:42 | 0.2276 | 0.0021 | 211 | 23360 | Planned | Planned | New Connections
951 |  | INCD-274-N | Sandwich | Network | SANCB2 | 13/03/2026 | 08:26 | 13/03/2026 | 15:32 | 0.0117 | 0.0018 | 184 | 1196 | Planned | Planned | Mixed Asset Replacement
952 |  | INCD-271-M | Sandwich | Network | SANCB2 | 28/08/2025 | 09:02 | 28/08/2025 | 17:12 | 0.4771 | 0.0016 | 165 | 48972 | Planned | Planned | Recloser & Sectionaliser replacement
953 |  | INCD-94-M | Sandwich | Network | SANCB3 | 16/06/2025 | 09:01 | 16/06/2025 | 10:03 | 0.0888 | 0.0014 | 147 | 9114 | Planned | Planned | OTHER Maintenance
954 |  | INCD-462-M | Sandwich | Network | SANCB3 | 09/12/2025 | 08:33 | 09/12/2025 | 16:25 | 0.3633 | 0.0008 | 79 | 37288 | Planned | Planned | Mixed Asset Replacement
955 |  | INCD-2043-L | Sandwich Rd | Private | SANCB3 | 10/03/2026 | 14:20 | 10/03/2026 | 14:28 | 0.008 | 0.001 | 103 | 824 | Unplanned | Third_party | Temp Disconnect / safety isolation
956 |  | INCD-286-M | Sandwich | Network | SANCB3 | 20/08/2025 | 08:40 | 20/08/2025 | 15:43 | 0.2143 | 0.0005 | 52 | 21996 | Planned | Planned | Mixed Asset Replacement
957 |  | INCD-6766-K | Sandwich Rd | Network | SANCB3 | 06/09/2025 | 04:31 | 06/09/2025 | 05:24 | 0.3505 | 0.0218 | 2235 | 35979 | Unplanned | Vegetation | Wind debris on line (OUT of Zone)
958 |  | INCD-7730-K | Sandwich Rd | Network | SANCB4 | 30/09/2025 | 05:04 | 30/09/2025 | 06:19 | 0.0132 | 0.0002 | 18 | 1350 | Planned | Planned | RMU Replacement
959 |  | INCD-679-M | Sandwich | Network | SANCB4 | 22/03/2026 | 09:09 | 22/03/2026 | 16:08 | 1.2083 | 0.0029 | 296 | 124024 | Planned | Planned | Mixed Asset Replacement
960 |  | INCD-291-M | Sandwich | Network | SANCB4 | 29/09/2025 | 15:03 | 29/09/2025 | 17:52 | 0.0016 | 0 | 1 | 169 | Planned | Planned | RMU Replacement
961 |  | INCD-446-L | Sandwich Rd | Network | SANCB4 | 28/07/2025 | 08:52 | 28/07/2025 | 14:57 | 0.476 | 0.0029 | 296 | 48853 | Unplanned | Third_party | Car in contact with pole
962 |  | INCD-213-M | Sandwich | Network | SANCB4 | 07/08/2025 | 20:10 | 07/08/2025 | 23:06 | 0.0016 | 0 | 1 | 169 | Planned | Planned | OTHER Maintenance
963 |  | INCD-307-M | Sandwich | Network | SANCB4 | 28/09/2025 | 09:18 | 28/09/2025 | 14:55 | 0.0033 | 0 | 1 | 337 | Planned | Planned | Crossarm Replacement
964 |  | INCD-5103-K | Sandwich Rd | Network | SANCB4 | 28/07/2025 | 07:24 | 28/07/2025 | 07:52 | 0.3104 | 0.0114 | 1170 | 31863 | Unplanned | Third_party | Car in contact with pole
965 |  | INCD-7780-K | Sandwich | Network | SANCB4 | 01/10/2025 | 05:01 | 01/10/2025 | 05:35 | 0.006 | 0.0002 | 18 | 612 | Planned | Planned | RMU Replacement
966 |  | INCD-41-M | Sandwich | Network | SANCB5 | 05/05/2025 | 20:09 | 05/05/2025 | 21:05 | 0.0027 | 0 | 5 | 280 | Planned | Planned | OTHER Maintenance
967 |  | INCD-307-M | Sandwich | Network | SANCB5 | 28/09/2025 | 09:18 | 28/09/2025 | 14:55 | 0.1798 | 0.0005 | 56 | 18452 | Planned | Planned | Crossarm Replacement
968 |  | INCD-6628-K | Sandwich Rd | Network | SANCB5 | 03/09/2025 | 15:03 | 03/09/2025 | 23:00 | 0.5504 | 0.0019 | 190 | 56492 | Unplanned | Third_party | Hit by car
969 |  | INCD-213-M | Sandwich | Network | SANCB5 | 07/08/2025 | 20:10 | 07/08/2025 | 23:06 | 0.0777 | 0.0005 | 47 | 7978 | Planned | Planned | OTHER Maintenance
970 |  | INCD-6829-K | Sandwich Rd | Network | SANCB5 | 06/09/2025 | 12:36 | 06/09/2025 | 14:15 | 0.1476 | 0.0015 | 153 | 15147 | Unplanned | Third_party | Hit by car
971 |  | INCD-1950-K | Sandwich | Network | SANCB6 | 18/06/2025 | 09:33 | 18/06/2025 | 15:05 | 0.257 | 0.0036 | 368 | 26384 | Planned | Planned | Conductor Replacement
972 |  | INCD-21-L | Sandwich Rd | Network | SANCB6 | 09/04/2025 | 16:51 | 09/04/2025 | 17:54 | 0.0215 | 0.0003 | 35 | 2205 | Planned | Planned | Conductor Replacement
973 |  | INCD-28-M | Sandwich | Network | SANCB6 | 08/04/2025 | 09:31 | 08/04/2025 | 17:29 | 0.9601 | 0.0022 | 229 | 98543 | Planned | Planned | Conductor Replacement
974 |  | INCD-20-L | Sandwich Rd | Network | SANCB6 | 09/04/2025 | 16:51 | 09/04/2025 | 17:50 | 0.0207 | 0.0004 | 36 | 2124 | Planned | Planned | Conductor Replacement
975 |  | INCD-8302-K | Sandwich | Network | SANCB7 | 19/10/2025 | 08:09 | 19/10/2025 | 11:10 | 0.0018 | 0 | 1 | 181 | Unplanned | Defective Equipment | Loss or failure of oil
976 |  | INCD-8157-K | Sandwich | Network | SANCB7 | 12/10/2025 | 08:53 | 12/10/2025 | 19:30 | 0.0062 | 0 | 1 | 637 | Planned | Planned | OTHER Maintenance
977 |  | INCD-1855-K | Sandwich | Network | SANCB7 | 29/04/2025 | 15:39 | 29/04/2025 | 16:12 | 0.0658 | 0.002 | 205 | 6755 | Unplanned | Third_party | High vehicle contact
978 |  | INCD-7661-K | Crawford Rd | Network | SANCB7 | 27/09/2025 | 09:26 | 28/09/2025 | 15:18 | 0.0506 | 0 | 3 | 5196 | Unplanned | Defective Equipment | Cable fails unknown
979 |  | INCD-1070-K | Silverdale | Network | SILCB1 | 09/04/2025 | 08:45 | 09/04/2025 | 16:06 | 0.1289 | 0.0003 | 30 | 13230 | Planned | Planned | New Connections
980 |  | INCD-10870-K | Silverdale | Network | SILCB2 | 20/01/2026 | 18:59 | 20/01/2026 | 20:10 | 0.0484 | 0.0007 | 70 | 4970 | Unplanned | Defective Equipment | Cable short to fuse fram
981 |  | INCD-10802-K | Silverdale | Network | SILCB2 | 19/01/2026 | 11:23 | 19/01/2026 | 12:21 | 0.6483 | 0.0114 | 1169 | 66542 | Unplanned | Wildlife | Bird betw line & pole
982 |  | INCD-235-M | Silverdale | Network | SILCB2 | 24/08/2025 | 09:16 | 24/08/2025 | 15:30 | 0.1607 | 0.0004 | 45 | 16494 | Planned | Planned | Mixed Asset Replacement
983 |  | INCD-223-M | Silverdale | Network | SILCB4 | 01/08/2025 | 09:16 | 01/08/2025 | 15:53 | 0.0193 | 0 | 5 | 1985 | Planned | Planned | OTHER Maintenance
984 |  | INCD-329-M | Silverdale | Network | SILCB5 | 29/09/2025 | 10:07 | 29/09/2025 | 12:00 | 0.1083 | 0.001 | 99 | 11121 | Planned | Planned | OTHER Maintenance
985 |  | INCD-12379-K | Silverdale | Network | SILCB5 | 14/03/2026 | 15:57 | 14/03/2026 | 17:18 | 0.3241 | 0.0045 | 462 | 33263 | Unplanned | Unknown | Fire Risk Mitigation Patrol - Sucessfully reclosed
986 |  | INCD-12148-K | Silverdale | Network | SILCB5 | 03/03/2026 | 04:13 | 03/03/2026 | 05:16 | 0.0321 | 0.0006 | 61 | 3294 | Planned | Planned | Mixed Asset Replacement
987 |  | INCD-12437-K | Silverdale | Network | SILCB5 | 16/03/2026 | 09:07 | 16/03/2026 | 15:25 | 0.5139 | 0.0015 | 157 | 52746 | Planned | Planned | Mixed Asset Replacement
988 |  | INCD-610-M | Transpower Hamilton | Network | SILCB5 | 12/03/2026 | 09:15 | 12/03/2026 | 13:31 | 0.1329 | 0.0005 | 55 | 13640 | Planned | Planned | Mixed Asset Replacement
989 |  | INCD-12621-K | Silverdale | Network | SILCB5 | 18/03/2026 | 13:03 | 18/03/2026 | 13:40 | 0.035 | 0.0009 | 97 | 3589 | Planned | Planned | Mixed Asset Replacement
990 |  | INCD-12157-K | Silverdale | Network | SILCB5 | 03/03/2026 | 09:02 | 03/03/2026 | 17:41 | 1.0507 | 0.0027 | 273 | 107849 | Planned | Planned | Mixed Asset Replacement
991 |  | INCD-3649-K | Simsey | Network | SIMCB2 | 14/06/2025 | 10:37 | 14/06/2025 | 10:50 | 0.0001 | 0 | 1 | 13 | Planned | Planned | OTHER Maintenance
992 |  | INCD-3650-K | Simsey | Network | SIMCB2 | 14/06/2025 | 12:13 | 14/06/2025 | 12:15 | 0 | 0 | 1 | 2 | Planned | Planned | OTHER Maintenance
993 |  | INCD-3653-K | Simsey | Network | SIMCB2 | 14/06/2025 | 13:48 | 14/06/2025 | 13:58 | 0.0001 | 0 | 1 | 10 | Planned | Planned | OTHER Maintenance
994 |  | INCD-3647-K | Simsey | Network | SIMCB2 | 14/06/2025 | 08:19 | 14/06/2025 | 08:37 | 0.0002 | 0 | 1 | 18 | Planned | Planned | OTHER Maintenance
995 |  | INCD-6774-K | Simsey | Private | SIMCB2 | 06/09/2025 | 08:11 | 06/09/2025 | 15:00 | 0.004 | 0 | 1 | 409 | Planned | Planned | External Customer
996 |  | INCD-66-L | Steele Park | Network | STECB3 | 13/05/2025 | 08:32 | 14/05/2025 | 15:58 | 0.8085 | 0.0004 | 44 | 82984 | Planned | Planned | OTHER Maintenance
997 |  | INCD-7763-K | Steele Park | Network | STECB3 | 23/09/2025 | 16:41 | 23/09/2025 | 16:48 | 0.0143 | 0.002 | 209 | 1463 | Planned | Planned | Mixed Asset Replacement
998 |  | INCD-12183-K | Steele Park | Network | STECB3 | 04/03/2026 | 08:16 | 04/03/2026 | 09:07 | 0.1038 | 0.002 | 209 | 10659 | Planned | Planned | OTHER Maintenance
999 |  | INCD-1513-L | Steele Park | Network | STECB3 | 19/12/2025 | 08:09 | 19/12/2025 | 13:04 | 0.2558 | 0.0009 | 89 | 26255 | Planned | Planned | OTHER Maintenance
1000 |  | INCD-8634-K | Steele Park | Network | STECB3 | 03/11/2025 | 11:56 | 03/11/2025 | 12:12 | 0.0131 | 0.0016 | 168 | 1344 | Unplanned | Defective Equipment | Cable fails unknown
1001 |  | INCD-642-L | Steele Park | Network | STECB3 | 23/09/2025 | 08:33 | 23/09/2025 | 08:48 | 0.0305 | 0.002 | 209 | 3135 | Planned | Planned | Mixed Asset Replacement
1002 |  | INCD-12618-K | Steele Park | Network | STECB3 | 04/03/2026 | 15:04 | 04/03/2026 | 15:57 | 0.1079 | 0.002 | 209 | 11077 | Planned | Planned | OTHER Maintenance
1003 |  | INCD-258-M | Steele Park | Network | STECB7 | 10/08/2025 | 08:04 | 10/08/2025 | 16:27 | 0.0007 | 0 | 4 | 72 | Planned | Planned | Mixed Asset Replacement
1004 |  | INCD-12085-K | Steele Park | Network | STECB8 | 27/02/2026 | 08:15 | 27/02/2026 | 08:39 | 0.0264 | 0.0011 | 113 | 2712 | Planned | Planned | OTHER Maintenance
1005 |  | INCD-39-M | Steele Park | Network | STECB8 | 08/05/2025 | 20:24 | 09/05/2025 | 03:24 | 0.0368 | 0.0001 | 9 | 3780 | Planned | Planned | OTHER Maintenance
1006 |  | INCD-1910-L | Steele Park | Network | STECB8 | 27/02/2026 | 09:09 | 27/02/2026 | 09:17 | 0.0088 | 0.0011 | 113 | 904 | Planned | Planned | OTHER Maintenance
1007 |  | INCD-261-M | Tasman | Network | TASCB3 | 30/08/2025 | 08:03 | 30/08/2025 | 10:17 | 0.0013 | 0 | 1 | 134 | Planned | Planned | OTHER Maintenance
1008 |  | INCD-11090-K | Foreman Rd | Network | TASCB3 | 24/01/2026 | 08:03 | 24/01/2026 | 15:34 | 0.0395 | 0.0001 | 9 | 4059 | Planned | Planned | OTHER Maintenance
1009 |  | INCD-2201-K | Foreman Rd | Network | TASCB3 | 07/05/2025 | 20:20 | 08/05/2025 | 00:32 | 0.0221 | 0.0001 | 9 | 2268 | Unplanned | Defective Equipment | Fuse blow from overload
1010 |  | INCD-3568-K | Pukete | Network | TASCB4 | 12/06/2025 | 09:04 | 12/06/2025 | 11:54 | 0.068 | 0.0008 | 84 | 6980 | Planned | Planned | Distribution Transformer Replacement
1011 |  | INCD-3397-K | Pukete | Network | TASCB4 | 09/06/2025 | 09:06 | 09/06/2025 | 12:13 | 0.1025 | 0.0008 | 84 | 10516 | Planned | Planned | Distribution Transformer Replacement
1012 |  | INCD-4433-K | Pukete | Network | TASCB4 | 11/07/2025 | 08:29 | 11/07/2025 | 08:33 | 0.0128 | 0.0032 | 330 | 1314 | Planned | Planned | New Connections
1013 |  | INCD-429-M | Pukete | Network | TASCB4 | 20/11/2025 | 08:18 | 20/11/2025 | 15:42 | 0.8781 | 0.002 | 203 | 90132 | Planned | Planned | OTHER Maintenance
1014 |  | INCD-4463-K | Pukete | Network | TASCB4 | 11/07/2025 | 15:01 | 11/07/2025 | 15:03 | 0.0091 | 0.0032 | 330 | 935 | Planned | Planned | New Connections
1015 |  | INCD-342-M | Pukete | Network | TASCB4 | 18/09/2025 | 09:50 | 18/09/2025 | 17:31 | 0.0671 | 0.0019 | 197 | 6890 | Planned | Planned | OTHER Maintenance
1016 |  | INCD-8528-K | Pukete | Network | TASCB4 | 30/10/2025 | 07:44 | 30/10/2025 | 16:32 | 0.7965 | 0.0033 | 334 | 81754 | Planned | Planned | Mixed Asset Replacement
1017 |  | INCD-9668-K | Tasman | Network | TASCB4 | 12/12/2025 | 09:09 | 12/12/2025 | 10:23 | 0.0114 | 0.0005 | 49 | 1168 | Planned | Planned | OTHER Maintenance
1018 |  | INCD-521-M | Tasman | Network | TASCB5 | 09/01/2026 | 09:23 | 09/01/2026 | 11:59 | 0.0137 | 0.0001 | 9 | 1404 | Planned | Planned | Crossarm Replacement
1019 |  | INCD-12479-K | Tasman | Network | TASCB5 | 18/03/2026 | 22:39 | 19/03/2026 | 01:43 | 0.0086 | 0.0001 | 9 | 882 | Unplanned | Defective Equipment | Fuse blow from overload
1020 |  | INCD-10419-K | Tasman | Private | TASCB6 | 09/01/2026 | 07:43 | 09/01/2026 | 10:48 | 0.0018 | 0 | 1 | 185 | Unplanned | Third_party | Discon of premise
1021 |  | INCD-12479-K | Tasman | Network | TASCB6 | 18/03/2026 | 22:39 | 19/03/2026 | 01:43 | 0.0132 | 0.0002 | 22 | 1352 | Unplanned | Defective Equipment | Fuse blow from overload
1022 |  | INCD-12461-K | Tasman | Network | TASCB6 | 18/03/2026 | 05:10 | 18/03/2026 | 10:07 | 0.0405 | 0.0001 | 14 | 4158 | Unplanned | Defective Equipment | Fuse blow from overload
1023 |  | INCD-8128-K | Te Kauwhata | Network | TEKCB2 | 10/10/2025 | 09:07 | 10/10/2025 | 13:22 | 0.0248 | 0.0001 | 10 | 2550 | Planned | Planned | OTHER Maintenance
1024 |  | INCD-137-M | Hampton Downs | Network | TEKCB2 | 24/06/2025 | 08:03 | 24/06/2025 | 16:06 | 1.3449 | 0.0029 | 302 | 138046 | Planned | Planned | Mixed Asset Replacement
1025 |  | INCD-4719-K | Te Kauwhata | Network | TEKCB2 | 18/07/2025 | 11:27 | 18/07/2025 | 11:55 | 0.0003 | 0 | 1 | 28 | Unplanned | Defective Equipment | Cable fails unknown
1026 |  | INCD-10811-K | Te Kauwhata | Network | TEKCB2 | 19/01/2026 | 22:01 | 19/01/2026 | 22:58 | 0.0472 | 0.0008 | 85 | 4845 | Unplanned | Vegetation | Wind debris on line (OUT of Zone)
1027 |  | INCD-10812-K | Te Kauwhata | Network | TEKCB2 | 19/01/2026 | 22:01 | 19/01/2026 | 22:17 | 0.0068 | 0.0042 | 434 | 694 | Unplanned | Vegetation | Wind debris on line (OUT of Zone)
1028 |  | INCD-1768-L | Te Kauwhata | Network | TEKCB2 | 24/01/2026 | 08:23 | 24/01/2026 | 09:57 | 0.0784 | 0.0008 | 85 | 8049 | Unplanned | Unknown | All Ok - Fault cause not established
1029 |  | INCD-5345-K | Te Kauwhata | Network | TEKCB3 | 04/08/2025 | 09:34 | 04/08/2025 | 15:30 | 0.0277 | 0.0001 | 8 | 2848 | Planned | Planned | OTHER Maintenance
1030 |  | INCD-10812-K | Te Kauwhata | Network | TEKCB3 | 19/01/2026 | 22:01 | 19/01/2026 | 22:17 | 0.0253 | 0.0158 | 1622 | 2595 | Unplanned | Vegetation | Wind debris on line (OUT of Zone)
1031 |  | INCD-5754-K | Te Kauwhata | Network | TEKCB3 | 14/08/2025 | 09:49 | 14/08/2025 | 12:21 | 0.0118 | 0.0001 | 8 | 1216 | Planned | Planned | 11kV Fuse Replacement
1032 |  | INCD-527-L | Te Kauwhata | Network | TEKCB3 | 20/08/2025 | 09:34 | 20/08/2025 | 15:07 | 0.026 | 0.0001 | 8 | 2664 | Planned | Planned | ABS Replacement
1033 |  | INCD-5664-K | Te Kauwhata | Network | TEKCB5 | 12/08/2025 | 09:58 | 12/08/2025 | 12:48 | 0.005 | 0 | 3 | 510 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
1034 |  | INCD-10320-K | Te Kauwhata | Network | TEKCB5 | 05/01/2026 | 16:36 | 06/01/2026 | 02:31 | 0.0116 | 0 | 2 | 1190 | Unplanned | Defective Equipment | Intnl insulation failure
1035 |  | INCD-10803-K | Te Kauwhata | Network | TEKCB5 | 19/01/2026 | 09:54 | 19/01/2026 | 11:46 | 0.0044 | 0 | 4 | 448 | Unplanned | Unknown | All Ok - Fault cause not established
1036 |  | INCD-10082-K | Te Kauwhata | Network | TEKCB5 | 28/12/2025 | 19:23 | 28/12/2025 | 20:13 | 0.0701 | 0.0014 | 144 | 7200 | Unplanned | Third_party | Car in contact with pole
1037 |  | INCD-448-M | Te Kauwhata | Network | TEKCB5 | 04/12/2025 | 09:16 | 04/12/2025 | 13:01 | 0.0903 | 0.0005 | 47 | 9270 | Planned | Planned | OTHER Maintenance
1038 |  | INCD-8185-K | Te Kauwhata | Network | TEKCB5 | 13/10/2025 | 20:33 | 13/10/2025 | 20:52 | 0.0007 | 0 | 4 | 76 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
1039 |  | INCD-4529-K | Te Kauwhata | Network | TEKCB5 | 14/07/2025 | 08:04 | 14/07/2025 | 11:58 | 0.0091 | 0 | 4 | 936 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
1040 |  | INCD-4024-K | Te Kauwhata | Network | TEKCB5 | 29/06/2025 | 09:22 | 29/06/2025 | 11:09 | 0.0031 | 0 | 3 | 321 | Unplanned | Unknown | All Ok - Fault cause not established
1041 |  | INCD-4194-K | Te Kauwhata | Network | TEKCB5 | 04/07/2025 | 17:47 | 04/07/2025 | 21:51 | 0.0095 | 0 | 4 | 976 | Unplanned | Unknown | All Ok - Fault cause not established
1042 |  | INCD-245-M | Te Kauwhata | Network | TEKCB5 | 07/07/2025 | 08:51 | 07/07/2025 | 14:35 | 0.0134 | 0 | 4 | 1376 | Unplanned | Unknown | All Ok - Fault cause not established
1043 |  | INCD-4499-K | Te Kauwhata | Network | TEKCB5 | 13/07/2025 | 00:33 | 13/07/2025 | 02:44 | 0.0102 | 0.0001 | 8 | 1048 | Unplanned | Unknown | All Ok - Fault cause not established
1044 |  | INCD-1403-L | Te Kauwhata | Network | TEKCB5 | 09/11/2025 | 09:22 | 09/11/2025 | 12:30 | 0.0055 | 0 | 3 | 564 | Unplanned | Unknown | All Ok - Fault cause not established
1045 |  | INCD-12346-K | Te Kauwhata | Network | TEKCB5 | 12/03/2026 | 16:02 | 12/03/2026 | 17:42 | 0.001 | 0 | 1 | 100 | Unplanned | Unknown | All Ok - Fault cause not established
1046 |  | INCD-7675-K | Te Kauwhata | Network | TEKCB5 | 28/09/2025 | 08:55 | 28/09/2025 | 10:55 | 0.0012 | 0 | 1 | 120 | Unplanned | Unknown | All Ok - Fault cause not established
1047 |  | INCD-6576-K | Te Kauwhata | Network | TEKCB5 | 02/09/2025 | 14:56 | 02/09/2025 | 17:36 | 0.0062 | 0 | 4 | 640 | Unplanned | Unknown | All Ok - Fault cause not established
1048 |  | INCD-10293-K | Weavers | Network | TEKCB5 | 29/12/2025 | 00:27 | 29/12/2025 | 00:45 | 0.0064 | 0.0004 | 36 | 656 | Unplanned | Third_party | Car in contact with pole
1049 |  | INCD-4759-K | Te Kauwhata | Network | TEKCB5 | 19/07/2025 | 15:51 | 19/07/2025 | 18:24 | 0.006 | 0 | 4 | 612 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
1050 |  | INCD-518-L | Te Kauwhata | Network | TEKCB5 | 11/08/2025 | 09:34 | 11/08/2025 | 12:24 | 0.0066 | 0 | 4 | 680 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
1051 |  | INCD-8369-K | Te Kauwhata | Network | TEKCB5 | 22/10/2025 | 11:33 | 22/10/2025 | 12:52 | 0.0952 | 0.0016 | 161 | 9774 | Unplanned | Defective Equipment | Cable termination fails
1052 |  | INCD-2058-K | Te Kauwhata | Network | TEKCB5 | 05/05/2025 | 08:36 | 05/05/2025 | 10:24 | 0.0032 | 0 | 3 | 324 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
1053 |  | INCD-4213-K | Te Kauwhata | Network | TEKCB5 | 06/07/2025 | 09:53 | 06/07/2025 | 11:43 | 0.0043 | 0 | 4 | 440 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
1054 |  | INCD-4425-K | Te Kauwhata | Network | TEKCB5 | 10/07/2025 | 19:24 | 10/07/2025 | 21:21 | 0.0386 | 0.0016 | 165 | 3964 | Unplanned | Unknown | All Ok - Fault cause not established
1055 |  | INCD-5772-K | Te Kauwhata | Network | TEKCB5 | 14/08/2025 | 10:18 | 14/08/2025 | 13:52 | 0.0063 | 0 | 3 | 642 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
1056 |  | INCD-9379-K | Te Kauwhata | Network | TEKCB5 | 03/12/2025 | 18:01 | 04/12/2025 | 01:50 | 0.0228 | 0 | 5 | 2345 | Unplanned | Lightning | Lightning damage
1057 |  | INCD-9970-K | Te Kauwhata | Network | TEKCB5 | 21/12/2025 | 09:00 | 21/12/2025 | 10:45 | 0.0092 | 0.0001 | 9 | 945 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
1058 |  | INCD-10686-K | Te Kauwhata | Network | TEKCB5 | 15/01/2026 | 12:04 | 15/01/2026 | 20:11 | 0.0142 | 0 | 3 | 1461 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
1059 |  | INCD-675-M | Te Kauwhata | Network | TEKCB5 | 25/03/2026 | 09:06 | 25/03/2026 | 14:01 | 0.0698 | 0.0003 | 26 | 7166 | Planned | Planned | Mixed Asset Replacement
1060 |  | INCD-10081-K | Te Kauwhata | Network | TEKCB5 | 28/12/2025 | 19:22 | 29/12/2025 | 01:13 | 0.3065 | 0.0016 | 160 | 31455 | Unplanned | Third_party | Car in contact with pole
1061 |  | INCD-1613-L | Te Kauwhata | Network | TEKCB5 | 08/12/2025 | 11:02 | 08/12/2025 | 13:28 | 0.0114 | 0.0001 | 8 | 1168 | Unplanned | Defective Equipment | Wear or shear of pins
1062 |  | INCD-10386-K | Te Kauwhata | Network | TEKCB5 | 08/01/2026 | 00:59 | 08/01/2026 | 02:24 | 0.0602 | 0.0007 | 73 | 6184 | Unplanned | Defective Equipment | Stay wire/ line clash
1063 |  | INCD-9060-K | Te Kauwhata | Network | TEKCB5 | 18/11/2025 | 19:07 | 19/11/2025 | 11:23 | 0.019 | 0 | 2 | 1952 | Unplanned | Defective Equipment | Stay wire/ line clash
1064 |  | INCD-49-M | Te Kauwhata | Network | TEKCB5 | 26/05/2025 | 09:06 | 26/05/2025 | 17:31 | 0.2312 | 0.0005 | 47 | 23735 | Planned | Planned | New Connections
1065 |  | INCD-9045-K | Te Kauwhata | Network | TEKCB5 | 18/11/2025 | 15:51 | 18/11/2025 | 18:28 | 0.0061 | 0 | 4 | 628 | Unplanned | Defective Equipment | Stay wire/ line clash
1066 |  | INCD-5342-K | Te Kauwhata | Network | TEKCB5 | 04/08/2025 | 09:10 | 04/08/2025 | 11:26 | 0.0954 | 0.0007 | 72 | 9788 | Planned | Planned | OTHER Maintenance
1067 |  | INCD-6043-K | Te Kauwhata | Network | TEKCB5 | 21/08/2025 | 10:01 | 21/08/2025 | 13:11 | 0.0111 | 0.0001 | 6 | 1140 | Planned | Planned | New Connections
1068 |  | INCD-10269-K | Te Kauwhata | Network | TEKCB5 | 03/01/2026 | 17:35 | 04/01/2026 | 10:12 | 0.1493 | 0.0006 | 58 | 15323 | Unplanned | Lightning | Lightning damage
1069 |  | INCD-1796-K | Te Kauwhata | Network | TEKCB5 | 28/04/2025 | 07:43 | 28/04/2025 | 10:36 | 0.0067 | 0 | 4 | 692 | Unplanned | Unknown | All Ok - Fault cause not established
1070 |  | INCD-5341-K | Te Kauwhata | Network | TEKCB5 | 04/08/2025 | 09:08 | 04/08/2025 | 11:37 | 0.0015 | 0 | 1 | 149 | Unplanned | Defective Equipment | Conduct worn on insulr
1071 |  | INCD-242-M | Te Kauwhata | Network | TEKCB6 | 11/08/2025 | 09:15 | 11/08/2025 | 11:25 | 0.0089 | 0.0001 | 7 | 910 | Planned | Planned | OTHER Maintenance
1072 |  | INCD-10812-K | Te Kauwhata | Network | TEKCB6 | 19/01/2026 | 22:01 | 19/01/2026 | 22:17 | 0 | 0 | 2 | 3 | Unplanned | Vegetation | Wind debris on line (OUT of Zone)
1073 |  | INCD-12173-K | Te Kauwhata | Network | TEKCB6 | 03/03/2026 | 21:28 | 03/03/2026 | 22:42 | 0.0087 | 0.0001 | 12 | 888 | Unplanned | Unknown | All Ok - Fault cause not established
1074 |  | INCD-5215-K | Te Kauwhata | Network | TEKCB6 | 30/07/2025 | 08:10 | 30/07/2025 | 10:30 | 0.0027 | 0 | 2 | 280 | Unplanned | Unknown | All Ok - Fault cause not established
1075 |  | INCD-1914-L | Te Kauwhata | Network | TEKCB6 | 04/03/2026 | 09:39 | 04/03/2026 | 10:36 | 0.0067 | 0.0001 | 12 | 684 | Unplanned | Unknown | All Ok - Fault cause not established
1076 |  | INCD-7943-K | Te Kauwhata | Network | TEKCB6 | 04/10/2025 | 10:27 | 05/10/2025 | 09:53 | 0.0137 | 0 | 1 | 1406 | Unplanned | Lightning | Lightning damage
1077 |  | INCD-9700-K | Te Kauwhata | Network | TEKCB6 | 12/12/2025 | 22:07 | 13/12/2025 | 00:14 | 0.0049 | 0 | 4 | 508 | Unplanned | Unknown | All Ok - Fault cause not established
1078 |  | INCD-3292-K | Te Kauwhata | Network | TEKCB6 | 05/06/2025 | 18:02 | 05/06/2025 | 22:29 | 0.2055 | 0.0008 | 79 | 21093 | Unplanned | Defective Equipment | Faulty joint/connection
1079 |  | INCD-5118-K | Te Kauwhata | Network | TEKCB6 | 28/07/2025 | 09:03 | 28/07/2025 | 11:38 | 0.1105 | 0.0007 | 73 | 11341 | Planned | Planned | OTHER Maintenance
1080 |  | INCD-25-N | Te Kauwhata | Network | TEKCB6 | 06/07/2025 | 21:59 | 07/07/2025 | 01:42 | 0.0043 | 0 | 2 | 446 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
1081 |  | INCD-7936-K | Te Kauwhata | Network | TEKCB6 | 04/10/2025 | 10:39 | 04/10/2025 | 21:24 | 0.0063 | 0 | 1 | 645 | Unplanned | Lightning | Lightning damage
1082 |  | INCD-2313-K | Te Kauwhata | Network | TEKCB6 | 11/05/2025 | 03:02 | 11/05/2025 | 05:19 | 0.0027 | 0 | 2 | 274 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
1083 |  | INCD-1036-L | Te Kauwhata | Network | TEKCB6 | 17/10/2025 | 13:37 | 17/10/2025 | 15:23 | 0.0021 | 0 | 2 | 212 | Unplanned | Third_party | Vehicle hits lines
1084 |  | INCD-10453-K | Weavers | Network | TEKCB6 | 11/01/2026 | 02:07 | 11/01/2026 | 16:22 | 0.0037 | 0 | 1 | 384 | Unplanned | Defective Equipment | Line break at twist joint
1085 |  | INCD-4493-K | Te Kauwhata | Network | TEKCB6 | 12/07/2025 | 17:31 | 12/07/2025 | 19:22 | 0.0129 | 0.0001 | 12 | 1322 | Unplanned | Unknown | All Ok - Fault cause not established
1086 |  | INCD-17-M | Te Kauwhata | Network | TEKCB6 | 06/05/2025 | 08:38 | 06/05/2025 | 14:50 | 0.1492 | 0.0004 | 45 | 15312 | Planned | Planned | New Connections
1087 |  | INCD-10512-K | Te Kauwhta | Network | TEKCB6 | 12/01/2026 | 00:14 | 12/01/2026 | 01:52 | 0.0038 | 0 | 4 | 392 | Unplanned | Unknown | All Ok - Fault cause not established
1088 |  | INCD-4204-K | Te Kauwhata | Network | TEKCB6 | 05/07/2025 | 17:46 | 05/07/2025 | 22:45 | 0.0058 | 0 | 2 | 598 | Unplanned | Wildlife | Bird betw line & pole
1089 |  | INCD-393-M | Te Uku | Network | TEUCB11 | 31/10/2025 | 08:36 | 31/10/2025 | 11:04 | 0.0014 | 0 | 1 | 148 | Planned | Planned | Mixed Asset Replacement
1090 |  | INCD-12870-K | Te Uku | Network | TEUCB11 | 27/03/2026 | 14:08 | 27/03/2026 | 15:47 | 0.0048 | 0 | 5 | 495 | Unplanned | Defective Equipment | Insulator split
1091 |  | INCD-3037-K | Te Uku | Network | TEUCB11 | 29/05/2025 | 18:53 | 30/05/2025 | 10:34 | 0.213 | 0.0011 | 110 | 21864 | Unplanned | Adverse weather | High wind lne break
1092 |  | INCD-3495-K | Te Uku | Network | TEUCB11 | 11/06/2025 | 01:15 | 11/06/2025 | 03:45 | 0.054 | 0.0008 | 77 | 5547 | Unplanned | Unknown | All Ok - Fault cause not established
1093 |  | INCD-11369-K | Te Uku | Network | TEUCB11 | 01/02/2026 | 07:51 | 01/02/2026 | 10:16 | 0.0085 | 0.0001 | 6 | 870 | Unplanned | Unknown | All Ok - Fault cause not established
1094 |  | INCD-3017-K | Te Uku | Network | TEUCB11 | 29/05/2025 | 14:11 | 31/05/2025 | 12:19 | 0.1377 | 0.002 | 207 | 14134 | Unplanned | Lightning | Lightning damage
1095 |  | INCD-138-N | Te Uku | Network | TEUCB11 | 15/01/2026 | 09:02 | 15/01/2026 | 16:53 | 0.8879 | 0.0022 | 224 | 91138 | Planned | Planned | Mixed Asset Replacement
1096 |  | INCD-3559-K | Te Uku | Network | TEUCB11 | 11/06/2025 | 01:15 | 12/06/2025 | 13:36 | 0.1845 | 0.0031 | 318 | 18936 | Unplanned | Defective Equipment | Chips or missing bits
1097 |  | INCD-4084-K | Te Uku Wind Farm | Network | TEUCB11 | 02/07/2025 | 00:34 | 02/07/2025 | 00:46 | 0.0939 | 0.0075 | 767 | 9639 | Planned | Planned | OTHER Maintenance
1098 |  | INCD-12647-K | Te Uku | Network | TEUCB11 | 25/03/2026 | 20:07 | 25/03/2026 | 21:36 | 0.0017 | 0 | 2 | 178 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
1099 |  | INCD-3110-K | Te Uku | Network | TEUCB11 | 30/05/2025 | 12:37 | 30/05/2025 | 17:15 | 0.0054 | 0 | 2 | 556 | Unplanned | Unknown | All Ok - Fault cause not established
1100 |  | INCD-7601-K | Te Uku | Network | TEUCB11 | 25/09/2025 | 07:52 | 25/09/2025 | 14:19 | 0.0527 | 0.0001 | 14 | 5413 | Unplanned | Defective Equipment | Connect/jumper loose
1101 |  | INCD-8329-K | Te Uku | Network | TEUCB11 | 20/10/2025 | 16:59 | 20/10/2025 | 23:49 | 0.1142 | 0.0053 | 539 | 11725 | Unplanned | Third_party | Vehicle hits lines
1102 |  | INCD-12872-K | Te Uku | Network | TEUCB11 | 27/03/2026 | 14:30 | 27/03/2026 | 15:47 | 0.006 | 0.0001 | 8 | 616 | Unplanned | Defective Equipment | Insulator split
1103 |  | INCD-1153-L | Te Uku | Network | TEUCB11 | 28/10/2025 | 08:34 | 28/10/2025 | 10:45 | 0.0026 | 0 | 2 | 262 | Unplanned | Lightning | Lightning damage
1104 |  | INCD-7660-K | Te Uku | Network | TEUCB11 | 27/09/2025 | 09:31 | 27/09/2025 | 12:47 | 0.0057 | 0 | 3 | 587 | Unplanned | Wildlife | Snails on HV bushings
1105 |  | INCD-119-N | Te Uku | Network | TEUCB11 | 31/08/2025 | 20:09 | 01/09/2025 | 14:30 | 0.0215 | 0 | 2 | 2202 | Unplanned | Unknown | All Ok - Fault cause not established
1106 |  | INCD-12869-K | Te Uku | Network | TEUCB11 | 28/03/2026 | 09:58 | 02/04/2026 | 13:55 | 0.2173 | 0 | 3 | 22309 | Unplanned | Defective Equipment | Line break at twist joint
1107 |  | INCD-10095-K | Te Uku | Network | TEUCB11 | 29/12/2025 | 14:20 | 30/12/2025 | 03:10 | 0.0599 | 0.0001 | 8 | 6153 | Unplanned | Unknown | All Ok - Fault cause not established
1108 |  | INCD-8464-K | Te Uku | Network | TEUCB11 | 28/10/2025 | 05:56 | 28/10/2025 | 09:13 | 0.0038 | 0 | 2 | 394 | Unplanned | Unknown | All Ok - Fault cause not established
1109 |  | INCD-2825-K | Te Uku | Network | TEUCB11 | 24/05/2025 | 02:48 | 24/05/2025 | 03:57 | 0.0155 | 0.0002 | 23 | 1592 | Unplanned | Defective Equipment | Line break at twist joint
1110 |  | INCD-8689-K | Te Uku | Network | TEUCB11 | 06/11/2025 | 03:37 | 06/11/2025 | 16:13 | 0.5926 | 0.0175 | 1796 | 60822 | Unplanned | Defective Equipment | Wear or shear of pins
1111 |  | INCD-1710-K | Te Uku | Network | TEUCB11 | 24/04/2025 | 16:35 | 24/04/2025 | 18:12 | 0.0047 | 0 | 5 | 485 | Unplanned | Lightning | Spontaneous failure
1112 |  | INCD-3114-E | Te Uku | Network | TEUCB11 | 11/04/2025 | 09:35 | 11/04/2025 | 13:39 | 0.0071 | 0 | 3 | 732 | Planned | Planned | Transformer Upgrade
1113 |  | INCD-118-N | Te Uku | Network | TEUCB11 | 01/09/2025 | 08:58 | 01/09/2025 | 20:08 | 0.0457 | 0.0001 | 7 | 4690 | Unplanned | Adverse weather | High wind lne break
1114 |  | INCD-12686-K | Te Uku | Network | TEUCB11 | 26/03/2026 | 17:03 | 27/03/2026 | 13:39 | 0.3747 | 0.0043 | 441 | 38459 | Unplanned | Defective Equipment | Split crossarm
1115 |  | INCD-3103-K | Te Uku | Network | TEUCB11 | 30/05/2025 | 08:45 | 31/05/2025 | 00:10 | 0.018 | 0 | 2 | 1850 | Unplanned | Defective Equipment | Intnl insulation failure
1116 |  | INCD-6761-K | Te Uku | Network | TEUCB11 | 05/09/2025 | 23:48 | 06/09/2025 | 00:59 | 0.0165 | 0.0002 | 24 | 1696 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
1117 |  | INCD-92-L | Te Uku | Network | TEUCB11 | 12/06/2025 | 08:52 | 12/06/2025 | 09:23 | 0.0012 | 0 | 4 | 124 | Unplanned | Lightning | Lightning damage
1118 |  | INCD-12363-K | Te Uku | Network | TEUCB11 | 13/03/2026 | 09:16 | 13/03/2026 | 13:34 | 0.0025 | 0 | 1 | 258 | Unplanned | Defective Equipment | Intnl insulation failure
1119 |  | INCD-16-M | Raglan | Network | TEUCB11 | 18/04/2025 | 14:51 | 18/04/2025 | 23:45 | 0.2254 | 0.0149 | 1528 | 23139 | Planned | Planned | OTHER Maintenance
1120 |  | INCD-3999-K | Whatawhata | Network | TEUCB11 | 28/06/2025 | 00:00 | 28/06/2025 | 00:12 | 0.0874 | 0.0075 | 767 | 8974 | Planned | Planned | OTHER Maintenance
1121 |  | INCD-11293-K | Te Uku | Network | TEUCB11 | 29/01/2026 | 12:50 | 29/01/2026 | 13:34 | 0.0013 | 0 | 3 | 132 | Unplanned | Wildlife | Possum across structure
1122 |  | INCD-12676-K | Te Uku | Network | TEUCB11 | 26/03/2026 | 14:59 | 26/03/2026 | 15:36 | 0.0325 | 0.0053 | 539 | 3339 | Unplanned | Vegetation | Wind debris on line (OUT of Zone)
1123 |  | INCD-137-N | Te Uku | Network | TEUCB11 | 27/11/2025 | 09:12 | 27/11/2025 | 16:07 | 0.0336 | 0.0002 | 24 | 3448 | Planned | Planned | Pole Replacement
1124 |  | INCD-1697-K | Te Uku | Network | TEUCB11 | 24/04/2025 | 06:08 | 24/04/2025 | 19:08 | 0.0152 | 0 | 2 | 1560 | Unplanned | Lightning | Spontaneous failure
1125 |  | INCD-772-K | Te Uku | Network | TEUCB11 | 01/04/2025 | 09:04 | 01/04/2025 | 14:37 | 0.2339 | 0.0007 | 74 | 24013 | Planned | Planned | Mixed Asset Replacement
1126 |  | INCD-12681-K | Te Uku | Network | TEUCB11 | 26/03/2026 | 16:34 | 26/03/2026 | 22:49 | 0.3115 | 0.0011 | 110 | 31971 | Unplanned | Defective Equipment | Broken binder
1127 |  | INCD-885-K | Te Uku | Network | TEUCB11 | 04/04/2025 | 09:00 | 04/04/2025 | 09:37 | 0.0222 | 0.0006 | 61 | 2278 | Planned | Planned | Crossarm Replacement
1128 |  | INCD-10103-K | Te Uku | Network | TEUCB11 | 29/12/2025 | 15:32 | 30/12/2025 | 01:31 | 0.4524 | 0.0093 | 958 | 46433 | Unplanned | Adverse weather | Line clash high wind
1129 |  | INCD-10398-K | Te Uku | Network | TEUCB11 | 08/01/2026 | 09:01 | 08/01/2026 | 13:44 | 0.1585 | 0.0006 | 61 | 16268 | Planned | Planned | Mixed Asset Replacement
1130 |  | INCD-1701-L | Te Uku | Network | TEUCB11 | 13/01/2026 | 19:26 | 13/01/2026 | 22:16 | 0.0099 | 0.0001 | 6 | 1020 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
1131 |  | INCD-12873-K | Te Uku | Network | TEUCB11 | 27/03/2026 | 15:16 | 27/03/2026 | 15:27 | 0.0014 | 0.0001 | 13 | 143 | Unplanned | Unknown | All Ok - Fault cause not established
1132 |  | INCD-182-M | Te Uku | Network | TEUCB11 | 04/07/2025 | 08:02 | 04/07/2025 | 16:30 | 0.0068 | 0.0002 | 16 | 698 | Planned | Planned | Mixed Asset Replacement
1133 |  | INCD-8476-K | Te Uku | Network | TEUCB11 | 28/10/2025 | 07:50 | 28/10/2025 | 14:04 | 0.0146 | 0 | 4 | 1496 | Unplanned | Lightning | Lightning damage
1134 |  | INCD-12682-K | Te Uku | Network | TEUCB11 | 26/03/2026 | 16:37 | 27/03/2026 | 13:05 | 0.0645 | 0.0002 | 22 | 6616 | Unplanned | Defective Equipment | Faulty joint/connection
1135 |  | INCD-4185-K | Te Uku | Network | TEUCB11 | 04/07/2025 | 16:30 | 04/07/2025 | 16:35 | 0.0003 | 0.0001 | 7 | 34 | Planned | Planned | Mixed Asset Replacement
1136 |  | INCD-657-M | Te Uku | Network | TEUCB11 | 20/03/2026 | 09:49 | 20/03/2026 | 13:17 | 0.0081 | 0 | 4 | 832 | Planned | Planned | Crossarm Replacement
1137 |  | INCD-2801-K | Te Uku | Network | TEUCB11 | 23/05/2025 | 13:53 | 24/05/2025 | 02:22 | 0.1495 | 0.0028 | 284 | 15349 | Unplanned | Defective Equipment | Line break at twist joint
1138 |  | INCD-3849-K | Te Uku | Network | TEUCB11 | 19/06/2025 | 10:02 | 19/06/2025 | 15:15 | 0.2324 | 0.0008 | 81 | 23859 | Planned | Planned | Crossarm Replacement
1139 |  | INCD-10169-K | Te Uku | Network | TEUCB11 | 30/12/2025 | 06:25 | 31/12/2025 | 15:41 | 0.2154 | 0.0053 | 539 | 22110 | Unplanned | Unknown | All Ok - Fault cause not established
1140 |  | INCD-388-L | Te Uku | Network | TEUCB11 | 10/07/2025 | 08:57 | 10/07/2025 | 22:07 | 0.0136 | 0 | 2 | 1396 | Unplanned | Defective Equipment | Stay wire/ line clash
1141 |  | INCD-2788-K | Te Uku | Network | TEUCB11 | 23/05/2025 | 08:59 | 23/05/2025 | 12:49 | 0.1281 | 0.0006 | 61 | 13150 | Planned | Planned | Crossarm Replacement
1142 |  | INCD-2270-L | Te Uku | Network | TEUCB11 | 20/03/2026 | 15:13 | 20/03/2026 | 17:57 | 0.0016 | 0 | 1 | 164 | Unplanned | Unknown | All Ok - Fault cause not established
1143 |  | INCD-536-M | Te Uku | Network | TEUCB12 | 29/01/2026 | 09:03 | 29/01/2026 | 14:16 | 0.1098 | 0.0004 | 36 | 11268 | Planned | Planned | Crossarm Replacement
1144 |  | INCD-3999-K | Whatawhata | Network | TEUCB12 | 28/06/2025 | 00:00 | 28/06/2025 | 00:12 | 0.0316 | 0.0027 | 277 | 3241 | Planned | Planned | OTHER Maintenance
1145 |  | INCD-12334-K | Te Uku | Network | TEUCB12 | 12/03/2026 | 11:16 | 12/03/2026 | 11:30 | 0.0316 | 0.0021 | 220 | 3241 | Unplanned | Unknown | All Ok - Fault cause not established
1146 |  | INCD-4084-K | Te Uku Wind Farm | Network | TEUCB12 | 02/07/2025 | 00:34 | 02/07/2025 | 00:46 | 0.0339 | 0.0027 | 277 | 3481 | Planned | Planned | OTHER Maintenance
1147 |  | INCD-170-M | Te Uku | Network | TEUCB12 | 09/07/2025 | 08:39 | 09/07/2025 | 13:27 | 0.0113 | 0 | 4 | 1155 | Planned | Planned | Distribution Transformer Replacement
1148 |  | INCD-218-M | Te Uku | Network | TEUCB12 | 07/08/2025 | 10:09 | 07/08/2025 | 19:26 | 0.2765 | 0.0006 | 66 | 28380 | Planned | Planned | Distribution Transformer Replacement
1149 |  | INCD-16-M | Raglan | Network | TEUCB12 | 18/04/2025 | 14:51 | 18/04/2025 | 23:45 | 0.0874 | 0.0054 | 554 | 8970 | Planned | Planned | OTHER Maintenance
1150 |  | INCD-12691-K | Te Uku | Network | TEUCB12 | 26/03/2026 | 19:17 | 27/03/2026 | 03:07 | 0.0183 | 0 | 4 | 1880 | Unplanned | Defective Equipment | Intnl insulation failure
1151 |  | INCD-8310-K | Te Uku | Network | TEUCB12 | 19/10/2025 | 16:28 | 19/10/2025 | 23:03 | 0.1693 | 0.0004 | 44 | 17375 | Unplanned | Vegetation | Tree blown ovr on line (IN Zone)
1152 |  | INCD-12333-K | Te Uku | Network | TEUCB12 | 12/03/2026 | 11:15 | 12/03/2026 | 12:56 | 0.0568 | 0.0006 | 58 | 5833 | Unplanned | Unknown | Fire Risk Mitigation Patrol - Sucessfully reclosed
1153 |  | INCD-26-M | Te Uku | Network | TEUCB12 | 30/04/2025 | 10:06 | 30/04/2025 | 12:48 | 0.0032 | 0 | 2 | 324 | Planned | Planned | Distribution Transformer Replacement
1154 |  | INCD-642-M | Te Uku | Network | TEUCB12 | 13/03/2026 | 09:11 | 13/03/2026 | 10:04 | 0.0026 | 0 | 5 | 265 | Planned | Planned | OTHER Maintenance
1155 |  | INCD-10914-K | Te Uku | Network | TEUCB12 | 21/01/2026 | 14:08 | 21/01/2026 | 14:33 | 0.0142 | 0.0006 | 58 | 1456 | Unplanned | Defective Equipment | Loose connection
1156 |  | INCD-12280-K | Te Uku | Network | TEUCB13 | 09/03/2026 | 12:41 | 09/03/2026 | 12:50 | 0.0035 | 0.0004 | 41 | 364 | Unplanned | Human error | Tree felled into line (WEL)
1157 |  | INCD-586-M | Te Uku | Network | TEUCB13 | 10/02/2026 | 09:31 | 10/02/2026 | 15:43 | 0.145 | 0.0004 | 40 | 14886 | Planned | Planned | Crossarm Replacement
1158 |  | INCD-4084-K | Te Uku Wind Farm | Network | TEUCB13 | 02/07/2025 | 00:34 | 02/07/2025 | 00:46 | 0.005 | 0.0004 | 41 | 515 | Planned | Planned | OTHER Maintenance
1159 |  | INCD-364-L | Te Uku | Network | TEUCB13 | 05/07/2025 | 09:45 | 05/07/2025 | 19:49 | 0.0059 | 0 | 1 | 604 | Planned | Planned | Mixed Asset Replacement
1160 |  | INCD-8362-K | Te Uku | Network | TEUCB13 | 22/10/2025 | 07:21 | 22/10/2025 | 09:35 | 0.0357 | 0.0004 | 41 | 3667 | Unplanned | Unknown | All Ok - Fault cause not established
1161 |  | INCD-8147-K | Te Uku | Network | TEUCB13 | 11/10/2025 | 09:59 | 11/10/2025 | 17:18 | 0.0043 | 0 | 1 | 439 | Unplanned | Defective Equipment | Intnl insulation failure
1162 |  | INCD-8505-K | Te Uku | Network | TEUCB13 | 29/10/2025 | 09:10 | 29/10/2025 | 15:35 | 0.0259 | 0.0001 | 7 | 2660 | Planned | Planned | Mixed Asset Replacement
1163 |  | INCD-7166-K | Te Uku | Network | TEUCB13 | 15/09/2025 | 10:13 | 15/09/2025 | 10:14 | 0 | 0 | 1 | 1 | Planned | Planned | Mixed Asset Replacement
1164 |  | INCD-16-M | Raglan | Network | TEUCB13 | 18/04/2025 | 14:51 | 18/04/2025 | 23:45 | 0.0129 | 0.0008 | 82 | 1328 | Planned | Planned | OTHER Maintenance
1165 |  | INCD-2279-K | Te Uku | Network | TEUCB13 | 09/05/2025 | 14:17 | 09/05/2025 | 17:36 | 0.0019 | 0 | 1 | 199 | Unplanned | Lightning | Lightning damage
1166 |  | INCD-3999-K | Whatawhata | Network | TEUCB13 | 28/06/2025 | 00:00 | 28/06/2025 | 00:12 | 0.0047 | 0.0004 | 41 | 480 | Planned | Planned | OTHER Maintenance
1167 |  | INCD-2082-K | Te Uku | Network | TEUCB13 | 05/05/2025 | 15:42 | 05/05/2025 | 19:22 | 0.0129 | 0.0001 | 6 | 1320 | Unplanned | Unknown | All Ok - Fault cause not established
1168 |  | INCD-9889-K | Transpower Hamilton | Network | UNICB1 | 18/12/2025 | 16:55 | 18/12/2025 | 17:09 | 0.0001 | 0 | 1 | 14 | Planned | Planned | RMU Replacement
1169 |  | INCD-9889-K | Transpower Hamilton | Network | UNICB4 | 18/12/2025 | 16:55 | 18/12/2025 | 17:09 | 0.0001 | 0 | 1 | 14 | Planned | Planned | RMU Replacement
1170 |  | INCD-4521-K | Waikato University | Network | UNICB4 | 14/07/2025 | 08:11 | 14/07/2025 | 18:43 | 0.0062 | 0 | 1 | 632 | Planned | Planned | OTHER Maintenance
1171 |  | INCD-8468-K | Wallace Rd | Network | WALCB1 | 28/10/2025 | 08:34 | 28/10/2025 | 10:10 | 0.0065 | 0.0001 | 7 | 672 | Unplanned | Vegetation | Wind debris on line (OUT of Zone)
1172 |  | INCD-4780-K | Wallace | Network | WALCB1 | 20/07/2025 | 16:16 | 20/07/2025 | 17:40 | 0.0016 | 0 | 2 | 168 | Unplanned | Defective Equipment | Wear or shear of pins
1173 |  | INCD-10680-K | Wallace Rd | Network | WALCB1 | 15/01/2026 | 13:52 | 15/01/2026 | 15:55 | 0.0109 | 0.0002 | 16 | 1120 | Unplanned | Vegetation | Wind debris on line (OUT of Zone)
1174 |  | INCD-12067-K | Latham Court | Network | WALCB1 | 25/02/2026 | 18:48 | 25/02/2026 | 19:45 | 0.0104 | 0.0007 | 74 | 1063 | Unplanned | Defective Equipment | Cable fails unknown
1175 |  | INCD-12241-K | Wallace Rd | Network | WALCB1 | 06/03/2026 | 15:51 | 06/03/2026 | 15:51 | 0.0003 | 0.0007 | 74 | 31 | Unplanned | Human error | Unintentionally Disabled
1176 |  | INCD-12067-K | Latham Court | Network | WALCB2 | 25/02/2026 | 18:48 | 25/02/2026 | 19:45 | 0.2424 | 0.0117 | 1202 | 24881 | Unplanned | Defective Equipment | Cable fails unknown
1177 |  | INCD-12-M | Wallace | Network | WALCB2 | 11/04/2025 | 09:45 | 11/04/2025 | 14:10 | 0.2427 | 0.0009 | 94 | 24910 | Planned | Planned | Mixed Asset Replacement
1178 |  | INCD-12241-K | Wallace Rd | Network | WALCB2 | 06/03/2026 | 15:51 | 06/03/2026 | 15:51 | 0.0049 | 0.0117 | 1202 | 501 | Unplanned | Human error | Unintentionally Disabled
1179 |  | INCD-9812-K | Wallace Rd | Network | WALCB2 | 17/12/2025 | 09:30 | 17/12/2025 | 11:12 | 0.0821 | 0.0018 | 182 | 8423 | Planned | Planned | OTHER Maintenance
1180 |  | INCD-12067-K | Latham Court | Network | WALCB3 | 25/02/2026 | 18:48 | 25/02/2026 | 19:45 | 0.1345 | 0.0066 | 676 | 13802 | Unplanned | Defective Equipment | Cable fails unknown
1181 |  | INCD-1911-L | Wallace Rd | Network | WALCB3 | 26/02/2026 | 00:32 | 28/02/2026 | 10:53 | 0.1989 | 0.0032 | 328 | 20418 | Unplanned | Defective Equipment | Intnl insulation failure
1182 |  | INCD-12241-K | Wallace Rd | Network | WALCB3 | 06/03/2026 | 15:51 | 06/03/2026 | 15:51 | 0.0027 | 0.0066 | 676 | 282 | Unplanned | Human error | Unintentionally Disabled
1183 |  | INCD-6883-K | Kent St | Network | WALCB4 | 09/09/2025 | 09:15 | 09/09/2025 | 09:33 | 0.0002 | 0 | 1 | 18 | Unplanned | Defective Equipment | Cable joint fails
1184 |  | INCD-7017-K | Wallace | Network | WALCB4 | 12/09/2025 | 08:04 | 12/09/2025 | 10:10 | 0.0974 | 0.0012 | 126 | 9996 | Planned | Planned | Transformer Upgrade
1185 |  | INCD-5252-K | Wallace Rd | Network | WALCB4 | 31/07/2025 | 10:28 | 31/07/2025 | 15:58 | 0.3577 | 0.0012 | 120 | 36720 | Planned | Planned | ABS Replacement
1186 |  | INCD-12241-K | Wallace Rd | Network | WALCB4 | 06/03/2026 | 15:51 | 06/03/2026 | 15:51 | 0.0027 | 0.0064 | 658 | 274 | Unplanned | Human error | Unintentionally Disabled
1187 |  | INCD-309-M | Wallace | Network | WALCB4 | 19/09/2025 | 05:27 | 19/09/2025 | 19:59 | 0.0123 | 0.0004 | 40 | 1260 | Planned | Planned | Mixed Asset Replacement
1188 |  | INCD-6673-K | Wallace Rd | Network | WALCB4 | 04/09/2025 | 08:13 | 04/09/2025 | 10:04 | 0.0941 | 0.0012 | 126 | 9663 | Planned | Planned | Transformer Upgrade
1189 |  | INCD-12067-K | Latham Court | Network | WALCB4 | 25/02/2026 | 18:48 | 25/02/2026 | 19:45 | 0.1226 | 0.0064 | 658 | 12579 | Unplanned | Defective Equipment | Cable fails unknown
1190 |  | INCD-12067-K | Latham Court | Network | WALCB5 | 25/02/2026 | 18:48 | 25/02/2026 | 19:45 | 0.1382 | 0.0076 | 785 | 14182 | Unplanned | Defective Equipment | Cable fails unknown
1191 |  | INCD-5252-K | Wallace Rd | Network | WALCB5 | 31/07/2025 | 10:28 | 31/07/2025 | 15:58 | 0.1833 | 0.0006 | 57 | 18810 | Planned | Planned | ABS Replacement
1192 |  | INCD-8127-K | Wallace | Network | WALCB5 | 10/10/2025 | 09:04 | 10/10/2025 | 10:21 | 0.057 | 0.0007 | 76 | 5852 | Planned | Planned | Transformer Upgrade
1193 |  | INCD-12241-K | Wallace Rd | Network | WALCB5 | 06/03/2026 | 15:51 | 06/03/2026 | 15:51 | 0.0032 | 0.0076 | 785 | 327 | Unplanned | Human error | Unintentionally Disabled
1194 |  | INCD-9319-K | Wallace Rd | Network | WALCB5 | 01/12/2025 | 05:43 | 01/12/2025 | 08:47 | 0.0771 | 0.0004 | 43 | 7912 | Unplanned | Unknown | All Ok - Fault cause not established
1195 |  | INCD-252-N | Wallace Rd | Network | WALCB5 | 01/12/2025 | 14:17 | 01/12/2025 | 14:38 | 0.0088 | 0.0004 | 43 | 903 | Unplanned | Unknown | All Ok - Fault cause not established
1196 |  | INCD-471-M | Wallace | Network | WALCB5 | 15/12/2025 | 09:21 | 15/12/2025 | 13:04 | 0.0956 | 0.0004 | 44 | 9812 | Planned | Planned | OTHER Maintenance
1197 |  | INCD-7984-K | Wallace Rd | Network | WALCB5 | 06/10/2025 | 09:03 | 06/10/2025 | 15:50 | 0.3014 | 0.0007 | 76 | 30932 | Planned | Planned | Transformer Upgrade
1198 |  | INCD-2535-K | Wallace Rd | Network | WALCB6 | 16/05/2025 | 08:42 | 16/05/2025 | 13:39 | 0.026 | 0.0001 | 9 | 2673 | Planned | Planned | OTHER Maintenance
1199 |  | INCD-56-L | Wallace Rd | Network | WALCB6 | 06/05/2025 | 14:19 | 06/05/2025 | 18:28 | 0.0049 | 0 | 2 | 498 | Unplanned | Defective Equipment | Corroded pin splits insul
1200 |  | INCD-12241-K | Wallace Rd | Network | WALCB6 | 06/03/2026 | 15:51 | 06/03/2026 | 15:51 | 0.0052 | 0.0124 | 1272 | 530 | Unplanned | Human error | Unintentionally Disabled
1201 |  | INCD-774-K | Wallace Rd | Network | WALCB6 | 01/04/2025 | 10:06 | 01/04/2025 | 12:15 | 0.0176 | 0.0001 | 14 | 1806 | Unplanned | Defective Equipment | Rotten crossarm
1202 |  | INCD-3098-E | Wallace | Private | WALCB6 | 14/04/2025 | 08:31 | 14/04/2025 | 15:24 | 0.0282 | 0.0001 | 7 | 2891 | Planned | Unknown | Mixed Asset Replacement
1203 |  | INCD-4748-K | Wallace Rd | Network | WALCB6 | 19/07/2025 | 07:10 | 19/07/2025 | 09:17 | 0.0099 | 0.0001 | 8 | 1015 | Unplanned | Unknown | All Ok - Fault cause not established
1204 |  | INCD-2022-K | Wallace Rd | Network | WALCB6 | 02/05/2025 | 15:06 | 02/05/2025 | 17:52 | 0.0032 | 0 | 2 | 332 | Unplanned | Unknown | All Ok - Fault cause not established
1205 |  | INCD-375-M | Wallace | Network | WALCB6 | 22/10/2025 | 09:25 | 22/10/2025 | 14:34 | 0.2811 | 0.0009 | 96 | 28856 | Planned | Planned | Crossarm Replacement
1206 |  | INCD-12293-K | Wallace | Network | WALCB6 | 10/03/2026 | 10:16 | 10/03/2026 | 12:03 | 0.001 | 0 | 1 | 107 | Unplanned | Unknown | All Ok - Fault cause not established
1207 |  | INCD-231-N | Wallace | Network | WALCB6 | 23/01/2026 | 09:15 | 23/01/2026 | 16:43 | 0.1682 | 0.0004 | 39 | 17264 | Planned | Planned | Crossarm Replacement
1208 |  | INCD-4219-K | Whatawhata | Network | WALCB6 | 06/07/2025 | 13:34 | 06/07/2025 | 20:34 | 0.0246 | 0.0001 | 6 | 2520 | Unplanned | Third_party | Car in contact with pole
1209 |  | INCD-511-M | Wallace | Network | WALCB6 | 22/12/2025 | 09:13 | 22/12/2025 | 13:59 | 0.0111 | 0 | 4 | 1144 | Planned | Planned | Distribution Transformer Replacement
1210 |  | INCD-12067-K | Latham Court | Network | WALCB6 | 25/02/2026 | 18:48 | 25/02/2026 | 19:45 | 0.1915 | 0.0124 | 1271 | 19658 | Unplanned | Defective Equipment | Cable fails unknown
1211 |  | INCD-3088-K | Wallace | Network | WALCB6 | 30/05/2025 | 08:21 | 30/05/2025 | 10:21 | 0.0082 | 0.0001 | 7 | 840 | Unplanned | Unknown | All Ok - Fault cause not established
1212 |  | INCD-560-M | Wallace Rd | Network | WALCB6 | 27/01/2026 | 09:01 | 27/01/2026 | 16:16 | 0.112 | 0.0003 | 33 | 11493 | Planned | Planned | Crossarm Replacement
1213 |  | INCD-601-M | Wallace | Network | WALCB6 | 18/02/2026 | 09:19 | 18/02/2026 | 15:28 | 0.235 | 0.0007 | 71 | 24119 | Planned | Planned | Crossarm Replacement
1214 |  | INCD-134-M | Wallace | Network | WALCB6 | 24/06/2025 | 09:14 | 24/06/2025 | 17:02 | 1.0113 | 0.0022 | 222 | 103807 | Planned | Planned | Mixed Asset Replacement
1215 |  | INCD-3661-K | Wallace Rd | Network | WALCB6 | 14/06/2025 | 19:25 | 14/06/2025 | 20:55 | 0.0035 | 0 | 4 | 360 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
1216 |  | INCD-64-L | Wallace Rd | Private | WALCB6 | 12/05/2025 | 13:06 | 12/05/2025 | 13:32 | 0.001 | 0 | 4 | 104 | Unplanned | Defective Equipment | LVC - WEL & Customer
1217 |  | INCD-674-M | Wallace | Network | WALCB6 | 24/03/2026 | 09:30 | 24/03/2026 | 12:26 | 0.0117 | 0.0001 | 7 | 1206 | Planned | Planned | OTHER Maintenance
1218 |  | INCD-6433-K | Wallace | Network | WALCB6 | 31/08/2025 | 17:56 | 31/08/2025 | 20:08 | 0.009 | 0.0001 | 7 | 924 | Unplanned | Vegetation | Wind debris on line (OUT of Zone)
1219 |  | INCD-2351-K | Wallace Rd | Network | WALCB6 | 09/05/2025 | 22:57 | 09/05/2025 | 22:58 | 0.0076 | 0.0048 | 496 | 777 | Unplanned | Defective Equipment | Wear or shear of pins
1220 |  | INCD-596-M | Wallace | Network | WALCB6 | 17/02/2026 | 09:15 | 17/02/2026 | 18:39 | 0.033 | 0.0001 | 6 | 3384 | Planned | Planned | Pole Replacement
1221 |  | INCD-665-M | Wallace | Network | WALCB6 | 17/03/2026 | 15:37 | 17/03/2026 | 17:24 | 0.0094 | 0.0001 | 9 | 963 | Planned | Planned | OTHER Maintenance
1222 |  | INCD-1383-K | Weavers | Network | WEACB2 | 17/04/2025 | 09:31 | 17/04/2025 | 16:15 | 0.4736 | 0.0013 | 134 | 48610 | Unplanned | Vegetation | Tree blown ovr on line (OUT of Zone)
1223 |  | INCD-12766-K | Weavers | Network | WEACB2 | 29/03/2026 | 05:32 | 29/03/2026 | 13:15 | 0.1233 | 0.0008 | 78 | 12654 | Unplanned | Defective Equipment | Line break at twist joint
1224 |  | INCD-5192-K | Weavers | Network | WEACB2 | 29/07/2025 | 13:58 | 29/07/2025 | 16:53 | 0.0017 | 0 | 1 | 175 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
1225 |  | INCD-10329-K | Weavers | Network | WEACB2 | 06/01/2026 | 09:14 | 06/01/2026 | 15:24 | 0.2804 | 0.0008 | 78 | 28784 | Planned | Planned | Mixed Asset Replacement
1226 |  | INCD-1477-K | Weavers | Network | WEACB2 | 17/04/2025 | 15:01 | 17/04/2025 | 15:11 | 0.0394 | 0.0038 | 387 | 4044 | Unplanned | Defective Equipment | Connect/jumper loose
1227 |  | INCD-3430-K | Weavers | Network | WEACB2 | 09/06/2025 | 17:32 | 09/06/2025 | 20:36 | 0.0072 | 0 | 4 | 736 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
1228 |  | INCD-5705-K | Weavers | Network | WEACB2 | 13/08/2025 | 09:41 | 13/08/2025 | 15:24 | 0.1677 | 0.0005 | 54 | 17211 | Planned | Planned | ABS Replacement
1229 |  | INCD-11124-K | Weavers | Network | WEACB2 | 24/01/2026 | 18:06 | 24/01/2026 | 21:58 | 0.009 | 0 | 4 | 928 | Unplanned | Defective Equipment | Intnl insulation failure
1230 |  | INCD-9288-K | Weavers | Network | WEACB2 | 28/11/2025 | 12:30 | 28/11/2025 | 14:37 | 0.0336 | 0.0003 | 27 | 3447 | Unplanned | Defective Equipment | Faulty joint/connection
1231 |  | INCD-5-L | Weavers | Network | WEACB2 | 03/04/2025 | 14:36 | 03/04/2025 | 16:58 | 0.0014 | 0 | 1 | 142 | Unplanned | Unknown | All Ok - Fault cause not established
1232 |  | INCD-316-M | Weavers | Network | WEACB2 | 11/09/2025 | 09:38 | 11/09/2025 | 11:50 | 0.2296 | 0.0018 | 189 | 23565 | Planned | Planned | Crossarm Replacement
1233 |  | INCD-4614-K | Weavers | Network | WEACB2 | 16/07/2025 | 02:28 | 16/07/2025 | 03:44 | 0.3792 | 0.0106 | 1091 | 38924 | Unplanned | Vegetation | Wind debris on line (IN Zone)
1234 |  | INCD-12066-K | Weavers | Network | WEACB2 | 25/02/2026 | 18:17 | 25/02/2026 | 21:27 | 0.0167 | 0.0001 | 9 | 1710 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
1235 |  | INCD-6369-K | Weavers | Network | WEACB2 | 31/08/2025 | 13:59 | 31/08/2025 | 15:53 | 0.0553 | 0.0006 | 58 | 5675 | Unplanned | Vegetation | Wind debris on line (OUT of Zone)
1236 |  | INCD-208-M | Weavers | Network | WEACB2 | 29/08/2025 | 11:05 | 29/08/2025 | 14:47 | 0.1461 | 0.0009 | 90 | 14993 | Planned | Planned | Transformer Upgrade
1237 |  | INCD-1397-K | Weavers | Network | WEACB2 | 17/04/2025 | 09:32 | 17/04/2025 | 10:44 | 0.1219 | 0.0017 | 173 | 12514 | Unplanned | Adverse weather | High wind lne break
1238 |  | INCD-690-L | Weavers | Network | WEACB2 | 07/10/2025 | 11:37 | 07/10/2025 | 14:41 | 0.0179 | 0.0001 | 10 | 1840 | Unplanned | Defective Equipment | Mechanism seized
1239 |  | INCD-10293-K | Weavers | Network | WEACB2 | 29/12/2025 | 00:27 | 29/12/2025 | 00:45 | 0.0139 | 0.0008 | 78 | 1422 | Unplanned | Third_party | Car in contact with pole
1240 |  | INCD-591-L | Weavers | Network | WEACB2 | 10/09/2025 | 09:36 | 10/09/2025 | 11:41 | 0.0012 | 0 | 1 | 125 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
1241 |  | INCD-273-N | Weavers | Network | WEACB2 | 13/02/2026 | 08:38 | 13/02/2026 | 10:50 | 0.0013 | 0 | 1 | 132 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
1242 |  | INCD-8041-K | Weavers | Network | WEACB2 | 07/10/2025 | 09:49 | 07/10/2025 | 19:27 | 0.0507 | 0.0001 | 9 | 5199 | Unplanned | Defective Equipment | Faulty joint/connection
1243 |  | INCD-5148-K | Weavers | Private | WEACB2 | 28/07/2025 | 19:32 | 28/07/2025 | 20:08 | 0.0011 | 0 | 3 | 108 | Unplanned | Defective Equipment | LVC - WEL & Customer
1244 |  | INCD-10587-K | Weavers | Network | WEACB2 | 14/01/2026 | 04:11 | 14/01/2026 | 10:49 | 0.1356 | 0.0008 | 78 | 13917 | Unplanned | Wildlife | Bird lne clash/break
1245 |  | INCD-5951-K | Weavers | Network | WEACB2 | 19/08/2025 | 10:10 | 19/08/2025 | 11:56 | 0.001 | 0 | 1 | 106 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
1246 |  | INCD-32-L | Weavers | Network | WEACB2 | 17/04/2025 | 16:37 | 17/04/2025 | 16:39 | 0.0004 | 0.0002 | 21 | 37 | Unplanned | Vegetation | Tree blown ovr on line (OUT of Zone)
1247 |  | INCD-44-M | Weavers | Network | WEACB2 | 07/05/2025 | 09:08 | 07/05/2025 | 14:36 | 0.0499 | 0.0002 | 16 | 5118 | Planned | Planned | Mixed Asset Replacement
1248 |  | INCD-93-L | Weavers | Network | WEACB2 | 13/06/2025 | 09:53 | 13/06/2025 | 12:18 | 0.0014 | 0 | 1 | 145 | Unplanned | Unknown | All Ok - Fault cause not established
1249 |  | INCD-1115-K | Weavers | Network | WEACB2 | 09/04/2025 | 18:02 | 09/04/2025 | 21:05 | 0.016 | 0.0001 | 9 | 1647 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
1250 |  | INCD-9576-K | Weavers | Network | WEACB2 | 10/12/2025 | 05:18 | 10/12/2025 | 07:07 | 0.0117 | 0.0001 | 11 | 1199 | Unplanned | Unknown | All Ok - Fault cause not established
1251 |  | INCD-1394-K | Weavers | Network | WEACB2 | 17/04/2025 | 09:45 | 17/04/2025 | 10:10 | 0.0594 | 0.0028 | 292 | 6093 | Unplanned | Adverse weather | High wind lne break
1252 |  | INCD-10685-K | Weavers | Network | WEACB2 | 15/01/2026 | 10:28 | 15/01/2026 | 19:07 | 0.0051 | 0 | 1 | 519 | Unplanned | Unknown | All Ok - Fault cause not established
1253 |  | INCD-231-M | Weavers | Network | WEACB3 | 11/08/2025 | 09:08 | 11/08/2025 | 11:24 | 0.0229 | 0.0002 | 20 | 2349 | Planned | Planned | OTHER Maintenance
1254 |  | INCD-6566-K | Weavers | Network | WEACB3 | 02/09/2025 | 14:11 | 02/09/2025 | 14:26 | 0.0003 | 0 | 2 | 30 | Unplanned | Lightning | Lightning damage
1255 |  | INCD-1116-K | Weavers | Private | WEACB3 | 09/04/2025 | 21:55 | 09/04/2025 | 22:09 | 0.0005 | 0 | 4 | 56 | Unplanned | Defective Equipment | LVC - WEL & Customer
1256 |  | INCD-4628-K | Weavers | Network | WEACB3 | 16/07/2025 | 09:33 | 16/07/2025 | 15:56 | 0.0273 | 0.0001 | 10 | 2806 | Unplanned | Defective Equipment | Intnl insulation failure
1257 |  | INCD-534-M | Weavers | Network | WEACB3 | 19/01/2026 | 09:35 | 19/01/2026 | 15:39 | 0.1551 | 0.0005 | 47 | 15920 | Planned | Planned | Pole Replacement
1258 |  | INCD-7937-K | Weavers | Network | WEACB3 | 04/10/2025 | 09:26 | 04/10/2025 | 12:30 | 0.0054 | 0 | 3 | 552 | Unplanned | Defective Equipment | Wear or shear of pins
1259 |  | INCD-442-M | Weavers | Network | WEACB3 | 02/12/2025 | 09:09 | 02/12/2025 | 15:15 | 0.0434 | 0.0002 | 18 | 4453 | Planned | Planned | Mixed Asset Replacement
1260 |  | INCD-10355-K | Weavers | Network | WEACB3 | 07/01/2026 | 07:37 | 07/01/2026 | 09:32 | 0.0022 | 0 | 2 | 230 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
1261 |  | INCD-32-L | Weavers | Network | WEACB3 | 17/04/2025 | 16:37 | 17/04/2025 | 16:39 | 0.0024 | 0.0013 | 137 | 245 | Unplanned | Vegetation | Tree blown ovr on line (OUT of Zone)
1262 |  | INCD-140-N | Weavers | Network | WEACB3 | 13/11/2025 | 09:37 | 13/11/2025 | 13:39 | 0.1484 | 0.0007 | 71 | 15232 | Planned | Planned | New Connections
1263 |  | INCD-689-M | Weavers | Network | WEACB3 | 23/03/2026 | 07:26 | 23/03/2026 | 15:18 | 0.0482 | 0.0002 | 18 | 4951 | Planned | Planned | ABS Replacement
1264 |  | INCD-7966-K | Weavers | Network | WEACB3 | 05/10/2025 | 12:53 | 05/10/2025 | 14:26 | 0.0027 | 0 | 3 | 279 | Unplanned | Defective Equipment | Intnl insulation failure
1265 |  | INCD-1161-K | Weavers | Network | WEACB3 | 10/04/2025 | 17:13 | 10/04/2025 | 20:26 | 0.0075 | 0 | 4 | 772 | Unplanned | Defective Equipment | Intnl insulation failure
1266 |  | INCD-4756-K | Weavers | Network | WEACB3 | 19/07/2025 | 14:49 | 19/07/2025 | 16:25 | 0.0187 | 0.0002 | 20 | 1916 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
1267 |  | INCD-9403-K | Weavers | Network | WEACB3 | 04/12/2025 | 12:57 | 04/12/2025 | 22:11 | 0.2607 | 0.0077 | 789 | 26764 | Unplanned | Vegetation | Tree blown ovr on line (OUT of Zone)
1268 |  | INCD-80-M | Weavers | Network | WEACB3 | 10/06/2025 | 09:03 | 10/06/2025 | 13:02 | 0.1614 | 0.0007 | 71 | 16567 | Planned | Planned | Distribution Transformer Replacement
1269 |  | INCD-33-L | Weavers | Network | WEACB3 | 17/04/2025 | 14:06 | 17/04/2025 | 21:30 | 0.0043 | 0 | 1 | 444 | Unplanned | Defective Equipment | Intnl insulation failure
1270 |  | INCD-5956-K | Weavers | Network | WEACB3 | 19/08/2025 | 09:38 | 19/08/2025 | 14:28 | 0.0028 | 0 | 1 | 290 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
1271 |  | INCD-568-M | Weavers | Network | WEACB3 | 28/01/2026 | 09:44 | 28/01/2026 | 14:43 | 0.0744 | 0.0003 | 26 | 7638 | Planned | Planned | Mixed Asset Replacement
1272 |  | INCD-98-M | Weavers | Network | WEACB3 | 03/06/2025 | 09:32 | 03/06/2025 | 14:18 | 0.1209 | 0.0005 | 47 | 12411 | Planned | Planned | Mixed Asset Replacement
1273 |  | INCD-160-M | Weavers | Network | WEACB3 | 09/07/2025 | 09:56 | 09/07/2025 | 14:22 | 0.0363 | 0.0001 | 14 | 3724 | Planned | Planned | Crossarm Replacement
1274 |  | INCD-7228-K | Weavers | Network | WEACB3 | 16/09/2025 | 12:47 | 16/09/2025 | 18:40 | 0.2293 | 0.0045 | 458 | 23540 | Unplanned | Defective Equipment | Pins fulls out
1275 |  | INCD-10782-K | Weavers | Network | WEACB3 | 18/01/2026 | 22:09 | 19/01/2026 | 03:28 | 0.2109 | 0.0022 | 222 | 21650 | Unplanned | Defective Equipment | Line break at twist joint
1276 |  | INCD-131-N | Weavers | Network | WEACB3 | 04/11/2025 | 10:07 | 04/11/2025 | 14:54 | 0.0555 | 0.0002 | 20 | 5695 | Planned | Planned | Crossarm Replacement
1277 |  | INCD-144-M | Weavers | Network | WEACB3 | 24/06/2025 | 09:43 | 24/06/2025 | 14:29 | 0.122 | 0.0004 | 44 | 12518 | Planned | Planned | Mixed Asset Replacement
1278 |  | INCD-1504-K | Weavers | Network | WEACB3 | 17/04/2025 | 13:55 | 17/04/2025 | 17:36 | 0.2712 | 0.0069 | 704 | 27840 | Unplanned | Vegetation | Tree blown ovr on line (OUT of Zone)
1279 |  | INCD-6821-K | Weavers | Network | WEACB3 | 08/09/2025 | 09:15 | 08/09/2025 | 14:27 | 0.0152 | 0 | 5 | 1560 | Planned | Planned | OTHER Maintenance
1280 |  | INCD-11525-K | Weavers | Network | WEACB3 | 07/02/2026 | 03:02 | 07/02/2026 | 04:26 | 0.0025 | 0 | 3 | 252 | Unplanned | Unknown | All Ok - Fault cause not established
1281 |  | INCD-1383-K | Weavers | Network | WEACB3 | 17/04/2025 | 09:31 | 17/04/2025 | 16:15 | 0.8339 | 0.0077 | 788 | 85598 | Unplanned | Vegetation | Tree blown ovr on line (OUT of Zone)
1282 |  | INCD-4484-K | Weavers | Network | WEACB3 | 11/07/2025 | 13:39 | 11/07/2025 | 21:19 | 0.0045 | 0 | 1 | 460 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
1283 |  | INCD-176-M | Weavers | Network | WEACB3 | 14/07/2025 | 10:01 | 14/07/2025 | 11:49 | 0.041 | 0.0004 | 39 | 4212 | Planned | Planned | OTHER Maintenance
1284 |  | INCD-3652-K | Weavers | Network | WEACB3 | 14/06/2025 | 12:38 | 14/06/2025 | 13:50 | 0.0007 | 0 | 1 | 72 | Unplanned | Unknown | All Ok - Fault cause not established
1285 |  | INCD-5851-K | Weavers | Network | WEACB3 | 17/08/2025 | 22:43 | 18/08/2025 | 01:07 | 0.0056 | 0 | 4 | 576 | Unplanned | Unknown | All Ok - Fault cause not established
1286 |  | INCD-9453-K | Weavers | Network | WEACB3 | 06/12/2025 | 05:31 | 06/12/2025 | 16:52 | 0.6728 | 0.0103 | 1058 | 69063 | Unplanned | Third_party | Car in contact with pole
1287 |  | INCD-178-M | Weavers | Network | WEACB3 | 18/07/2025 | 10:12 | 18/07/2025 | 16:55 | 0.3033 | 0.0008 | 78 | 31135 | Planned | Planned | ABS Replacement
1288 |  | INCD-1201-K | Weavers | Network | WEACB3 | 12/04/2025 | 08:22 | 12/04/2025 | 14:34 | 0.4349 | 0.0045 | 459 | 44642 | Unplanned | Third_party | Car in contact with pole
1289 |  | INCD-2145-K | Weavers | Network | WEACB3 | 06/05/2025 | 19:20 | 06/05/2025 | 22:11 | 0.0067 | 0 | 4 | 684 | Unplanned | Defective Equipment | Mechanism seized
1290 |  | INCD-69-L | Weavers | Network | WEACB3 | 13/05/2025 | 11:16 | 13/05/2025 | 15:29 | 0.0049 | 0 | 2 | 506 | Unplanned | Unknown | All Ok - Fault cause not established
1291 |  | INCD-11019-K | Weavers | Network | WEACB3 | 22/01/2026 | 13:32 | 22/01/2026 | 14:09 | 0.0014 | 0 | 4 | 148 | Unplanned | Defective Equipment | Pins fulls out
1292 |  | INCD-30-N | Weavers | Network | WEACB4 | 07/07/2025 | 21:07 | 07/07/2025 | 22:13 | 0.0135 | 0.0002 | 21 | 1386 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
1293 |  | INCD-12499-K | Weavers | Network | WEACB4 | 20/03/2026 | 01:06 | 20/03/2026 | 02:17 | 0.0048 | 0.0001 | 7 | 497 | Unplanned | Unknown | All Ok - Fault cause not established
1294 |  | INCD-530-M | Weavers | Network | WEACB4 | 23/01/2026 | 08:33 | 23/01/2026 | 16:22 | 0.043 | 0.0001 | 10 | 4411 | Planned | Planned | Mixed Asset Replacement
1295 |  | INCD-1401-K | Weavers | Network | WEACB4 | 17/04/2025 | 10:10 | 17/04/2025 | 19:27 | 0.1565 | 0.0006 | 63 | 16066 | Unplanned | Defective Equipment | Connect/jumper loose
1296 |  | INCD-2583-K | Weavers | Network | WEACB4 | 18/05/2025 | 21:26 | 18/05/2025 | 22:36 | 0.0143 | 0.0002 | 21 | 1470 | Unplanned | Unknown | All Ok - Fault cause not established
1297 |  | INCD-524-M | Weavers | Network | WEACB4 | 18/12/2025 | 09:33 | 18/12/2025 | 16:03 | 0.2333 | 0.0006 | 64 | 23947 | Planned | Planned | Mixed Asset Replacement
1298 |  | INCD-1477-K | Weavers | Network | WEACB4 | 17/04/2025 | 15:01 | 17/04/2025 | 15:11 | 0.0196 | 0.0021 | 212 | 2010 | Unplanned | Defective Equipment | Connect/jumper loose
1299 |  | INCD-354-M | Weavers | Network | WEACB4 | 22/10/2025 | 09:13 | 22/10/2025 | 11:43 | 0.0172 | 0.0001 | 12 | 1764 | Planned | Planned | Mixed Asset Replacement
1300 |  | INCD-1214-K | Weavers | Network | WEACB4 | 13/04/2025 | 04:09 | 13/04/2025 | 05:56 | 0.0031 | 0 | 3 | 321 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
1301 |  | INCD-6794-K | Weavers | Network | WEACB4 | 06/09/2025 | 20:30 | 06/09/2025 | 22:15 | 0.0215 | 0.0002 | 21 | 2205 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
1302 |  | INCD-3141-K | Weavers | Network | WEACB4 | 31/05/2025 | 20:38 | 01/06/2025 | 00:29 | 0.0293 | 0.0001 | 13 | 3003 | Unplanned | Unknown | All Ok - Fault cause not established
1303 |  | INCD-6546-K | Weavers | Network | WEACB4 | 02/09/2025 | 09:30 | 02/09/2025 | 11:24 | 0.0033 | 0 | 3 | 342 | Unplanned | Unknown | All Ok - Fault cause not established
1304 |  | INCD-88-M | Weavers | Network | WEACB4 | 12/06/2025 | 09:45 | 12/06/2025 | 15:34 | 0.042 | 0.0001 | 13 | 4306 | Planned | Planned | Pole Replacement
1305 |  | INCD-10453-K | Weavers | Network | WEACB4 | 11/01/2026 | 02:07 | 11/01/2026 | 16:22 | 0.0893 | 0.0023 | 233 | 9163 | Unplanned | Defective Equipment | Line break at twist joint
1306 |  | INCD-9-M | Weavers | Network | WEACB4 | 09/04/2025 | 09:02 | 09/04/2025 | 14:01 | 0.032 | 0.0001 | 11 | 3289 | Planned | Planned | Conductor Replacement
1307 |  | INCD-1693-L | Weavers | Network | WEACB4 | 11/01/2026 | 11:41 | 11/01/2026 | 16:58 | 0.0124 | 0 | 4 | 1268 | Unplanned | Defective Equipment | Faulty joint/connection
1308 |  | INCD-1375-K | Weavers | Network | WEACB4 | 17/04/2025 | 08:37 | 17/04/2025 | 14:23 | 0.0067 | 0 | 2 | 692 | Unplanned | Vegetation | Tree known grows in line (IN Zone)
1309 |  | INCD-34-L | Weavers | Network | WEACB4 | 22/04/2025 | 08:25 | 22/04/2025 | 11:16 | 0.0017 | 0 | 1 | 171 | Unplanned | Lightning | Lightning damage
1310 |  | INCD-234-M | Weavers | Network | WEACB5 | 12/08/2025 | 09:34 | 12/08/2025 | 15:26 | 0.1783 | 0.0005 | 52 | 18304 | Planned | Planned | ABS Replacement
1311 |  | INCD-269-N | Weavers | Network | WEACB5 | 09/03/2026 | 08:39 | 09/03/2026 | 14:54 | 0.0215 | 0.0001 | 6 | 2202 | Planned | Planned | Transformer Upgrade
1312 |  | INCD-7501-K | Weavers | Network | WEACB5 | 23/09/2025 | 07:18 | 23/09/2025 | 15:57 | 0.2889 | 0.0043 | 438 | 29655 | Unplanned | Third_party | Car in contact with pole
1313 |  | INCD-7641-K | Horotiu | Network | WEACB5 | 26/09/2025 | 09:25 | 26/09/2025 | 11:03 | 0.0019 | 0 | 2 | 196 | Unplanned | Third_party | Car in contact with pole
1314 |  | INCD-1036-K | Weavers | Network | WEACB5 | 08/04/2025 | 13:43 | 08/04/2025 | 15:06 | 0.0008 | 0 | 1 | 83 | Unplanned | Unknown | All Ok - Fault cause not established
1315 |  | INCD-8282-K | Weavers | Network | WEACB5 | 17/10/2025 | 17:00 | 17/10/2025 | 19:30 | 0.0768 | 0.0007 | 76 | 7879 | Unplanned | Defective Equipment | Insulator split
1316 |  | INCD-1745-K | Weavers | Network | WEACB5 | 26/04/2025 | 16:02 | 27/04/2025 | 02:20 | 0.4967 | 0.0086 | 879 | 50986 | Unplanned | Third_party | Car in contact with pole
1317 |  | INCD-5779-K | Weavers | Network | WEACB5 | 14/08/2025 | 16:11 | 14/08/2025 | 19:13 | 0.0053 | 0 | 3 | 546 | Unplanned | Defective Equipment | Pins fulls out
1318 |  | INCD-25-M | Weavers | Network | WEACB5 | 30/04/2025 | 10:08 | 30/04/2025 | 13:15 | 0.0146 | 0.0001 | 8 | 1496 | Planned | Planned | Mixed Asset Replacement
1319 |  | INCD-633-M | Weavers | Network | WEACB6 | 12/03/2026 | 10:17 | 12/03/2026 | 13:11 | 0.0271 | 0.0002 | 16 | 2784 | Planned | Planned | Mixed Asset Replacement
1320 |  | INCD-9949-K | Weavers | Network | WEACB6 | 19/12/2025 | 23:29 | 20/12/2025 | 13:54 | 1.7815 | 0.0046 | 470 | 182856 | Unplanned | Defective Equipment | Insulator split
1321 |  | INCD-1586-K | Weavers | Network | WEACB6 | 19/04/2025 | 03:16 | 19/04/2025 | 10:16 | 0.0123 | 0 | 3 | 1260 | Unplanned | Lightning | Lightning damage
1322 |  | INCD-2208-K | Weavers | Network | WEACB6 | 08/05/2025 | 09:08 | 08/05/2025 | 13:11 | 0.0095 | 0 | 4 | 972 | Planned | Planned | OTHER Maintenance
1323 |  | INCD-2489-K | Weavers | Network | WEACB6 | 15/05/2025 | 09:06 | 15/05/2025 | 17:39 | 0.624 | 0.0012 | 125 | 64050 | Planned | Planned | Mixed Asset Replacement
1324 |  | INCD-10067-K | Weavers | Network | WEACB6 | 26/12/2025 | 13:03 | 26/12/2025 | 20:41 | 0.122 | 0.001 | 99 | 12525 | Unplanned | Defective Equipment | Contact problem
1325 |  | INCD-1582-K | Weavers | Network | WEACB6 | 19/04/2025 | 08:05 | 19/04/2025 | 09:55 | 0.0128 | 0.0001 | 12 | 1317 | Unplanned | Lightning | Lightning damage
1326 |  | INCD-1775-L | Weavers | Network | WEACB6 | 05/02/2026 | 11:42 | 05/02/2026 | 17:38 | 0.0069 | 0 | 2 | 712 | Unplanned | Unknown | All Ok - Fault cause not established
1327 |  | INCD-637-M | Weaver | Network | WEACB6 | 26/02/2026 | 09:16 | 26/02/2026 | 09:16 | 0.0088 | 0 | 2 | 908 | Planned | Planned | Mixed Asset Replacement
1328 |  | INCD-8313-K | Weavers | Network | WEACB6 | 20/10/2025 | 06:21 | 20/10/2025 | 09:31 | 0.0443 | 0.0002 | 24 | 4543 | Unplanned | Unknown | All Ok - Fault cause not established
1329 |  | INCD-9346-K | Weavers | Network | WEACB6 | 02/12/2025 | 18:21 | 02/12/2025 | 20:49 | 0.0029 | 0 | 2 | 296 | Unplanned | Defective Equipment | Line break at twist joint
1330 |  | INCD-1490-K | Weavers | Network | WEACB6 | 17/04/2025 | 12:03 | 17/04/2025 | 16:05 | 0.0424 | 0.0002 | 18 | 4356 | Unplanned | Adverse weather | Line clash high wind
1331 |  | INCD-399-L | Weavers | Network | WEACB6 | 11/07/2025 | 16:48 | 12/07/2025 | 12:22 | 0.1571 | 0.0011 | 114 | 16124 | Unplanned | Defective Equipment | Connect/jumper loose
1332 |  | INCD-99-M | Weavers | Network | WEACB6 | 06/06/2025 | 10:20 | 06/06/2025 | 14:55 | 0.0134 | 0 | 5 | 1375 | Planned | Planned | Mixed Asset Replacement
1333 |  | INCD-10730-K | Weavers | Network | WEACB6 | 16/01/2026 | 11:49 | 16/01/2026 | 15:19 | 0.0041 | 0 | 2 | 420 | Unplanned | Lightning | Lightning damage
1334 |  | INCD-11069-K | Weavers | Network | WEACB6 | 23/01/2026 | 11:22 | 23/01/2026 | 13:01 | 0.0068 | 0.0001 | 7 | 693 | Unplanned | Unknown | All Ok - Fault cause not established
1335 |  | INCD-12577-K | Weavers | Network | WEACB6 | 21/03/2026 | 11:40 | 21/03/2026 | 13:40 | 0.0035 | 0 | 3 | 360 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
1336 |  | INCD-1577-K | Weavers | Network | WEACB6 | 19/04/2025 | 02:18 | 19/04/2025 | 02:35 | 0.0188 | 0.0012 | 125 | 1926 | Unplanned | Unknown | All Ok - Fault cause not established
1337 |  | INCD-6517-K | Weavers | Network | WEACB6 | 01/09/2025 | 09:20 | 01/09/2025 | 16:59 | 0.0089 | 0 | 2 | 918 | Unplanned | Unknown | All Ok - Fault cause not established
1338 |  | INCD-122-M | Weavers | Network | WEACB6 | 12/06/2025 | 09:02 | 12/06/2025 | 14:55 | 0.0204 | 0.0001 | 6 | 2095 | Planned | Planned | Pole Replacement
1339 |  | INCD-4929-K | Weavers | Network | WEACB6 | 24/07/2025 | 07:17 | 24/07/2025 | 16:50 | 0.0926 | 0.0057 | 586 | 9502 | Unplanned | Third_party | Car in contact with pole
1340 |  | INCD-1487-L | Weavers | Network | WEACB6 | 26/11/2025 | 10:09 | 26/11/2025 | 18:33 | 0.0377 | 0.0001 | 8 | 3867 | Planned | Planned | Mixed Asset Replacement
1341 |  | INCD-8264-K | Weavers | Network | WEACB6 | 17/10/2025 | 06:34 | 17/10/2025 | 11:22 | 0.0673 | 0.0002 | 24 | 6909 | Unplanned | Unknown | All Ok - Fault cause not established
1342 |  | INCD-12487-K | Weavers | Network | WEACB6 | 19/03/2026 | 09:30 | 19/03/2026 | 15:07 | 0.2056 | 0.0006 | 63 | 21102 | Planned | Planned | Mixed Asset Replacement
1343 |  | INCD-1609-L | Weavers | Network | WEACB6 | 04/12/2025 | 09:20 | 04/12/2025 | 15:06 | 0.0067 | 0 | 2 | 692 | Unplanned | Unknown | All Ok - Fault cause not established
1344 |  | INCD-4957-K | Ngaruawahia | Network | WEACB6 | 24/07/2025 | 07:32 | 24/07/2025 | 14:19 | 1.9781 | 0.0105 | 1075 | 203040 | Unplanned | Defective Equipment | Line break at twist joint
1345 |  | INCD-631-M | Weavers | Network | WEACB6 | 24/02/2026 | 08:18 | 24/02/2026 | 11:15 | 0.0172 | 0.0001 | 10 | 1770 | Planned | Planned | Mixed Asset Replacement
1346 |  | INCD-2376-L | Weavers | Network | WEACB6 | 25/03/2026 | 11:49 | 25/03/2026 | 14:09 | 0.0144 | 0.0001 | 12 | 1473 | Unplanned | Defective Equipment | Nut or bolt loose
1347 |  | INCD-10204-K | Weavers | Network | WEACB6 | 29/12/2025 | 18:20 | 30/12/2025 | 22:41 | 0.0331 | 0 | 2 | 3402 | Unplanned | Unknown | All Ok - Fault cause not established
1348 |  | INCD-10205-K | Weavers | Network | WEACB6 | 30/12/2025 | 23:48 | 31/12/2025 | 02:16 | 0.0274 | 0.0002 | 19 | 2812 | Unplanned | Defective Equipment | Split crossarm
1349 |  | INCD-10640-K | Weavers | Network | WEACB6 | 14/01/2026 | 17:08 | 14/01/2026 | 19:19 | 0.4201 | 0.0057 | 585 | 43116 | Unplanned | Vegetation | Wind debris on line (OUT of Zone)
1350 |  | INCD-12596-K | Weavers | Network | WEACB6 | 22/03/2026 | 08:57 | 22/03/2026 | 10:53 | 0.0683 | 0.004 | 412 | 7010 | Planned | Planned | Mixed Asset Replacement
1351 |  | INCD-8687-K | Weavers | Network | WEACB6 | 05/11/2025 | 20:17 | 05/11/2025 | 22:34 | 0.008 | 0.0001 | 6 | 822 | Unplanned | Defective Equipment | Loss or failure of oil
1352 |  | INCD-4316-K | Weavers | Network | WEACB6 | 08/07/2025 | 10:11 | 08/07/2025 | 11:59 | 0.0053 | 0 | 5 | 540 | Unplanned | Defective Equipment | Intnl insulation failure
1353 |  | INCD-3835-K | Weavers | Network | WEACB6 | 18/06/2025 | 19:07 | 18/06/2025 | 21:32 | 0.0622 | 0.0004 | 44 | 6380 | Unplanned | Defective Equipment | Cable short to fuse fram
1354 |  | INCD-1502-L | Weavers | Network | WEACB6 | 26/11/2025 | 21:04 | 26/11/2025 | 22:58 | 0.0011 | 0 | 1 | 114 | Unplanned | Human error | Incorr fuse rating
1355 |  | INCD-8359-K | Weavers | Network | WEACB6 | 21/10/2025 | 18:55 | 21/10/2025 | 19:52 | 0.0011 | 0 | 2 | 114 | Unplanned | Adverse weather | Line clash high wind
1356 |  | INCD-2486-K | Weavers | Network | WEACB6 | 15/05/2025 | 08:51 | 15/05/2025 | 18:44 | 1.4798 | 0.0029 | 293 | 151894 | Planned | Planned | Mixed Asset Replacement
1357 |  | INCD-11423-K | Weavers | Network | WEACB6 | 03/02/2026 | 09:32 | 03/02/2026 | 16:56 | 0.5533 | 0.0013 | 137 | 56794 | Planned | Planned | Mixed Asset Replacement
1358 |  | INCD-1766-L | Weavers | Network | WEACB6 | 16/01/2026 | 11:49 | 16/01/2026 | 16:20 | 0.0053 | 0 | 2 | 542 | Unplanned | Lightning | Lightning damage
1359 |  | INCD-3063-E | Weavers | Network | WEACB6 | 29/09/2025 | 08:39 | 29/09/2025 | 10:49 | 0.0101 | 0.0001 | 8 | 1040 | Planned | Planned | OTHER Maintenance
1360 |  | INCD-4630-K | Weavers | Network | WEACB6 | 16/07/2025 | 10:01 | 16/07/2025 | 14:27 | 0.1133 | 0.0004 | 46 | 11632 | Planned | Planned | Mixed Asset Replacement
1361 |  | INCD-8407-K | Weavers | Network | WEACB6 | 24/10/2025 | 13:49 | 24/10/2025 | 16:42 | 0.0327 | 0.0003 | 29 | 3363 | Unplanned | Third_party | Vehicle hits lines
1362 |  | INCD-9787-K | Weavers | Network | WEACB6 | 16/12/2025 | 18:31 | 16/12/2025 | 19:52 | 0.1634 | 0.0025 | 261 | 16773 | Unplanned | Unknown | All Ok - Fault cause not established
1363 |  | INCD-12239-K | Weavers | Network | WEACB6 | 06/03/2026 | 14:47 | 06/03/2026 | 16:01 | 0.0594 | 0.0025 | 252 | 6097 | Unplanned | Wildlife | Bird betw line & pole
1364 |  | INCD-1515-K | Weavers | Network | WEACB6 | 17/04/2025 | 11:14 | 17/04/2025 | 19:40 | 0.0592 | 0.0001 | 12 | 6072 | Unplanned | Adverse weather | Line clash high wind
1365 |  | INCD-11483-K | Weavers | Network | WEACB6 | 05/02/2026 | 09:30 | 05/02/2026 | 15:12 | 0.0908 | 0.0003 | 29 | 9324 | Planned | Planned | Mixed Asset Replacement
1366 |  | INCD-654-M | Weavers | Network | WEACB6 | 18/03/2026 | 09:44 | 18/03/2026 | 13:38 | 0.0114 | 0 | 5 | 1170 | Planned | Planned | Pole Replacement
1367 |  | INCD-7996-K | Weavers | Network | WEACB6 | 06/10/2025 | 07:59 | 06/10/2025 | 12:12 | 0.0049 | 0 | 2 | 506 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
1368 |  | INCD-11988-K | Weavers | Network | WEACB6 | 22/02/2026 | 14:07 | 22/02/2026 | 15:55 | 0.0074 | 0.0001 | 7 | 756 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
1369 |  | INCD-423-M | Weavers | Network | WEACB6 | 18/11/2025 | 09:37 | 18/11/2025 | 15:29 | 0.0069 | 0 | 2 | 704 | Planned | Planned | Crossarm Replacement
1370 |  | INCD-9944-K | Weavers | Network | WEACB6 | 19/12/2025 | 22:26 | 19/12/2025 | 22:50 | 0.0569 | 0.0025 | 261 | 5842 | Unplanned | Defective Equipment | Insulator split
1371 |  | INCD-12032-K | Weavers | Network | WEACB6 | 24/02/2026 | 08:00 | 24/02/2026 | 14:20 | 0.1631 | 0.0004 | 46 | 16737 | Planned | Planned | Mixed Asset Replacement
1372 |  | INCD-632-M | Weavers | Network | WEACB6 | 24/02/2026 | 08:09 | 24/02/2026 | 14:55 | 0.3477 | 0.0009 | 89 | 35694 | Planned | Planned | Mixed Asset Replacement
1373 |  | INCD-2748-K | Whatawhata | Network | WHACB2 | 22/05/2025 | 11:45 | 22/05/2025 | 13:38 | 0.0033 | 0 | 3 | 339 | Unplanned | Unknown | All Ok - Fault cause not established
1374 |  | INCD-11013-K | Whatawhata | Network | WHACB2 | 22/01/2026 | 10:18 | 22/01/2026 | 12:42 | 0.0042 | 0 | 3 | 432 | Unplanned | Adverse weather | Line clash high wind
1375 |  | INCD-145-M | Whatawhata | Network | WHACB2 | 23/06/2025 | 08:00 | 23/06/2025 | 08:24 | 0.0026 | 0.0001 | 11 | 264 | Planned | Planned | OTHER Maintenance
1376 |  | INCD-4021-K | Whatawhata | Network | WHACB2 | 29/06/2025 | 08:00 | 29/06/2025 | 12:16 | 1.1477 | 0.0046 | 476 | 117806 | Planned | Planned | OTHER Maintenance
1377 |  | INCD-10129-K | Whatawhata | Network | WHACB2 | 29/12/2025 | 17:05 | 30/12/2025 | 00:25 | 0.5483 | 0.0046 | 474 | 56280 | Unplanned | Adverse weather | High wind lne break
1378 |  | INCD-9283-K | Whatawhata | Network | WHACB2 | 28/11/2025 | 09:49 | 28/11/2025 | 15:47 | 0.2336 | 0.0007 | 71 | 23975 | Planned | Planned | ABS Replacement
1379 |  | INCD-4067-K | Whatawhata | Network | WHACB2 | 01/07/2025 | 13:11 | 01/07/2025 | 16:58 | 1.0108 | 0.0046 | 476 | 103752 | Planned | Planned | OTHER Maintenance
1380 |  | INCD-5563-K | Whatawhata | Network | WHACB2 | 10/08/2025 | 07:32 | 10/08/2025 | 09:24 | 0.0065 | 0.0001 | 6 | 672 | Unplanned | Unknown | All Ok - Fault cause not established
1381 |  | INCD-5783-K | Whatawhata | Network | WHACB2 | 14/08/2025 | 18:04 | 14/08/2025 | 18:19 | 0.0187 | 0.0046 | 475 | 1921 | Unplanned | Unknown | All Ok - Fault cause not established
1382 |  | INCD-5286-K | Whatawhata | Private | WHACB2 | 01/08/2025 | 11:40 | 01/08/2025 | 11:51 | 0.0001 | 0 | 1 | 11 | Unplanned | Defective Equipment | LVC - WEL & Customer
1383 |  | INCD-11851-K | Whatawhata | Network | WHACB2 | 18/02/2026 | 09:00 | 18/02/2026 | 14:12 | 0.3078 | 0.0011 | 112 | 31595 | Planned | Planned | Mixed Asset Replacement
1384 |  | INCD-5934-K | Whatawhata | Network | WHACB3 | 19/08/2025 | 06:21 | 19/08/2025 | 12:39 | 0.0287 | 0.0001 | 9 | 2942 | Planned | Planned | Mixed Asset Replacement
1385 |  | INCD-497-M | Whatawhata | Network | WHACB3 | 16/12/2025 | 09:35 | 16/12/2025 | 16:37 | 0.036 | 0.0001 | 9 | 3694 | Planned | Planned | ABS Replacement
1386 |  | INCD-11460-K | Whatawhata | Private | WHACB3 | 04/02/2026 | 11:43 | 04/02/2026 | 11:52 | 0.0008 | 0.0001 | 9 | 81 | Unplanned | Defective Equipment | LVC - WEL & Customer
1387 |  | INCD-1051-K | Whatawhata | Network | WHACB3 | 08/04/2025 | 16:15 | 08/04/2025 | 22:28 | 0.0109 | 0 | 3 | 1119 | Unplanned | Unknown | All Ok - Fault cause not established
1388 |  | INCD-8397-K | Whatawhata | Network | WHACB3 | 23/10/2025 | 22:30 | 24/10/2025 | 17:03 | 0.1566 | 0.0008 | 81 | 16079 | Unplanned | Third_party | Car in contact with pole
1389 |  | INCD-2622-K | Whatawhata | Network | WHACB3 | 20/05/2025 | 01:04 | 20/05/2025 | 05:24 | 0.0127 | 0 | 5 | 1300 | Unplanned | Defective Equipment | Loss or failure of oil
1390 |  | INCD-517-M | Whatawhata | Network | WHACB3 | 25/02/2026 | 09:21 | 25/02/2026 | 15:18 | 0.2688 | 0.0008 | 83 | 27591 | Planned | Planned | Mixed Asset Replacement
1391 |  | INCD-669-M | Whatawhata | Network | WHACB3 | 24/03/2026 | 09:41 | 24/03/2026 | 15:21 | 0.0199 | 0.0001 | 6 | 2040 | Planned | Planned | Mixed Asset Replacement
1392 |  | INCD-377-M | Whatawhata | Network | WHACB4 | 24/10/2025 | 09:16 | 24/10/2025 | 13:02 | 0.0154 | 0.0001 | 7 | 1582 | Planned | Planned | Crossarm Replacement
1393 |  | INCD-12545-K | Whatawhata | Network | WHACB4 | 20/03/2026 | 20:10 | 20/03/2026 | 23:11 | 0.0302 | 0.0005 | 54 | 3096 | Unplanned | Third_party | Car in contact with pole
1394 |  | INCD-11730-K | Whatawhata | Network | WHACB4 | 13/02/2026 | 17:14 | 13/02/2026 | 23:22 | 0.0221 | 0.0001 | 10 | 2267 | Unplanned | Lightning | Lightning damage
1395 |  | INCD-12456-K | Wallace Rd | Network | WHACB4 | 17/03/2026 | 09:30 | 17/03/2026 | 12:15 | 0.1011 | 0.0006 | 63 | 10375 | Planned | Planned | Crossarm Replacement
1396 |  | INCD-2337-L | Whatawhata | Network | WHACB4 | 24/03/2026 | 09:13 | 24/03/2026 | 11:18 | 0.0012 | 0 | 1 | 125 | Unplanned | Unknown | All Ok - Fault cause not established
1397 |  | INCD-1377-K | Whatawhata | Private | WHACB4 | 17/04/2025 | 08:35 | 17/04/2025 | 08:45 | 0.0015 | 0.0001 | 15 | 150 | Unplanned | Third_party | Temp Disconnect / safety isolation
1398 |  | INCD-10332-K | Whatawhata | Network | WHACB4 | 06/01/2026 | 09:34 | 06/01/2026 | 11:47 | 0.0661 | 0.0005 | 54 | 6788 | Planned | Planned | Crossarm Replacement
1399 |  | INCD-256-M | Whatawhata | Network | WHACB4 | 19/08/2025 | 09:37 | 19/08/2025 | 14:32 | 0.0553 | 0.0002 | 20 | 5672 | Planned | Planned | Mixed Asset Replacement
1400 |  | INCD-5168-K | Whatawhata | Network | WHACB4 | 29/07/2025 | 06:37 | 29/07/2025 | 10:19 | 0.013 | 0.0001 | 6 | 1332 | Unplanned | Unknown | All Ok - Fault cause not established
1401 |  | INCD-3246-K | Whatawhata | Network | WHACB4 | 04/06/2025 | 15:44 | 04/06/2025 | 21:58 | 0.0219 | 0.0001 | 6 | 2244 | Unplanned | Lightning | Lightning damage
1402 |  | INCD-6755-K | Whatawhata | Network | WHACB4 | 05/09/2025 | 15:09 | 05/09/2025 | 17:14 | 0.0073 | 0.0001 | 6 | 750 | Unplanned | Vegetation | Wind debris on line (OUT of Zone)
1403 |  | INCD-8442-K | Whatawhata | Network | WHACB4 | 27/10/2025 | 16:24 | 27/10/2025 | 21:43 | 0.1262 | 0.0004 | 46 | 12954 | Unplanned | Third_party | Car in contact with pole
1404 |  | INCD-56-M | Whatawhata | Network | WHACB4 | 14/05/2025 | 09:10 | 14/05/2025 | 11:37 | 0.0544 | 0.0004 | 38 | 5586 | Planned | Planned | OTHER Maintenance
1405 |  | INCD-2143-K | Whatawhata | Network | WHACB4 | 06/05/2025 | 18:16 | 08/05/2025 | 17:03 | 0.0547 | 0 | 2 | 5614 | Unplanned | Third_party | Tree felled into line (Third Party)
1406 |  | INCD-4067-K | Whatawhata | Network | WHACB4 | 01/07/2025 | 13:11 | 01/07/2025 | 16:58 | 0.236 | 0.001 | 107 | 24227 | Planned | Planned | OTHER Maintenance
1407 |  | INCD-9383-K | Whatawhata | Network | WHACB4 | 03/12/2025 | 18:24 | 04/12/2025 | 12:10 | 0.0312 | 0 | 3 | 3198 | Unplanned | Lightning | Lightning damage
1408 |  | INCD-230-N | Whatawhata | Network | WHACB4 | 12/01/2026 | 09:21 | 12/01/2026 | 14:05 | 0.0138 | 0 | 5 | 1420 | Planned | Planned | Mixed Asset Replacement
1409 |  | INCD-7194-K | Whatawhata | Network | WHACB4 | 16/09/2025 | 03:26 | 16/09/2025 | 04:43 | 0.0688 | 0.0018 | 188 | 7066 | Unplanned | Vegetation | Wind debris on line (IN Zone)
1410 |  | INCD-10333-K | Whatawhata | Network | WHACB4 | 04/02/2026 | 08:35 | 04/02/2026 | 14:30 | 0.0484 | 0.0001 | 14 | 4970 | Planned | Planned | Mixed Asset Replacement
1411 |  | INCD-5633-K | Whatawhata | Network | WHACB4 | 11/08/2025 | 10:03 | 11/08/2025 | 14:30 | 0.0234 | 0.0001 | 9 | 2403 | Unplanned | Unknown | All Ok - Fault cause not established
1412 |  | INCD-678-M | Whatawhata | Network | WHACB4 | 17/03/2026 | 08:31 | 17/03/2026 | 13:39 | 0.4626 | 0.0015 | 154 | 47481 | Planned | Planned | ABS Replacement
1413 |  | INCD-8892-K | Whatawhata | Network | WHACB4 | 14/11/2025 | 06:49 | 14/11/2025 | 08:03 | 0.0143 | 0.0002 | 20 | 1467 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
1414 |  | INCD-1288-K | Whatawhata | Network | WHACB4 | 15/04/2025 | 07:12 | 15/04/2025 | 09:11 | 0.007 | 0.0001 | 6 | 714 | Unplanned | Defective Equipment | Mechanism seized
1415 |  | INCD-4021-K | Whatawhata | Network | WHACB4 | 29/06/2025 | 08:00 | 29/06/2025 | 12:16 | 0.2671 | 0.001 | 107 | 27413 | Planned | Planned | OTHER Maintenance
1416 |  | INCD-9475-K | Whatawhata | Network | WHACB4 | 07/12/2025 | 08:43 | 07/12/2025 | 10:32 | 0.0032 | 0 | 3 | 327 | Unplanned | Defective Equipment | Intnl insulation failure
1417 |  | INCD-2123-L | Whatawhata | Private | WHACB5 | 13/03/2026 | 16:56 | 13/03/2026 | 17:32 | 0.0035 | 0.0001 | 10 | 360 | Unplanned | Defective Equipment | LVC - WEL & Customer
1418 |  | INCD-10878-K | Whatawhata | Network | WHACB5 | 21/01/2026 | 04:22 | 21/01/2026 | 13:14 | 0.5574 | 0.0076 | 784 | 57212 | Unplanned | Defective Equipment | Insulator split
1419 |  | INCD-2269-L | Whatawhata | Network | WHACB5 | 20/03/2026 | 16:21 | 20/03/2026 | 17:32 | 0.0184 | 0.0003 | 30 | 1888 | Unplanned | Wildlife | Foreign Objt obstruct /Animal contact
1420 |  | INCD-6066-K | Whatawhata | Network | WHACB5 | 21/08/2025 | 19:12 | 21/08/2025 | 22:54 | 0.0743 | 0.0004 | 37 | 7622 | Unplanned | Defective Equipment | Nut or bolt loose
1421 |  | INCD-276-M | Whatawhata | Network | WHACB5 | 02/09/2025 | 09:08 | 02/09/2025 | 16:41 | 0.485 | 0.0011 | 114 | 49785 | Planned | Planned | Mixed Asset Replacement
1422 |  | INCD-1864-K | Whatawhata | Network | WHACB5 | 29/04/2025 | 19:18 | 30/04/2025 | 01:14 | 0.2345 | 0.0007 | 73 | 24065 | Unplanned | Third_party | Car in contact with pole
1423 |  | INCD-8099-K | Whatawhata | Network | WHACB5 | 09/10/2025 | 09:04 | 09/10/2025 | 14:42 | 0.0165 | 0 | 5 | 1690 | Planned | Planned | OTHER Maintenance
1424 |  | INCD-696-M | Whatawhata | Network | WHACB5 | 17/03/2026 | 09:10 | 17/03/2026 | 11:50 | 0.0117 | 0.0001 | 8 | 1202 | Planned | Planned | Mixed Asset Replacement
1425 |  | INCD-9922-K | Whatawhata | Private | WHACB5 | 19/12/2025 | 09:42 | 19/12/2025 | 09:53 | 0.0009 | 0.0001 | 8 | 88 | Unplanned | Defective Equipment | LVC - WEL & Customer
1426 |  | INCD-5412-K | Whatawhata | Network | WHACB5 | 06/08/2025 | 04:57 | 06/08/2025 | 06:46 | 0.0328 | 0.0003 | 31 | 3367 | Unplanned | Unknown | All Ok - Fault cause not established
1427 |  | INCD-497-M | Whatawhata | Network | WHACB6 | 16/12/2025 | 09:35 | 16/12/2025 | 16:37 | 0.0414 | 0.0001 | 11 | 4246 | Planned | Planned | ABS Replacement
1428 |  | INCD-8353-K | Whatawhata | Network | WHACB6 | 21/10/2025 | 15:43 | 21/10/2025 | 21:25 | 0.2062 | 0.0006 | 62 | 21169 | Unplanned | Vegetation | Tree blown ovr on line (OUT of Zone)
1429 |  | INCD-7108-K | Whatawhata | Network | WHACB6 | 13/09/2025 | 15:23 | 14/09/2025 | 02:05 | 0.2712 | 0.0006 | 62 | 27834 | Unplanned | Vegetation | Tree blown ovr on line (IN Zone)
1430 |  | INCD-579-M | Whatawhata | Network | WHACB6 | 02/02/2026 | 09:18 | 02/02/2026 | 12:09 | 0.0383 | 0.0002 | 23 | 3933 | Planned | Planned | Crossarm Replacement
1431 |  | INCD-1169-L | Whatawhata | Network | WHACB6 | 28/10/2025 | 15:22 | 28/10/2025 | 16:51 | 0.0385 | 0.0006 | 62 | 3950 | Unplanned | Defective Equipment | Faulty joint/connection
1432 |  | INCD-539-M | Whatawhata | Network | WHACB6 | 23/01/2026 | 09:05 | 23/01/2026 | 15:33 | 0.1173 | 0.0005 | 51 | 12040 | Planned | Planned | Crossarm Replacement
1433 |  | INCD-5934-K | Whatawhata | Network | WHACB6 | 19/08/2025 | 06:21 | 19/08/2025 | 12:39 | 0.0151 | 0.0001 | 11 | 1551 | Planned | Planned | Mixed Asset Replacement
1434 |  | INCD-11807-K | Whitiora School | Network | WHICB4 | 17/02/2026 | 08:31 | 17/02/2026 | 15:38 | 0.7738 | 0.0018 | 186 | 79422 | Planned | Planned | Mixed Asset Replacement
1435 |  | INCD-12753-K | Civic Car Park | Network | WHICB4 | 28/03/2026 | 08:00 | 28/03/2026 | 14:01 | 0.0597 | 0.0002 | 17 | 6123 | Planned | Planned | Mixed Asset Replacement
1436 |  | INCD-12709-K | Civic Car Park | Network | WHICB4 | 27/03/2026 | 08:00 | 27/03/2026 | 08:07 | 0.0101 | 0.0014 | 147 | 1041 | Planned | Planned | Mixed Asset Replacement
1437 |  | INCD-4392-K | Whitiora School | Network | WHICB7 | 10/07/2025 | 06:47 | 10/07/2025 | 06:52 | 0 | 0 | 1 | 5 | Planned | Planned | OTHER Maintenance
1438 |  | INCD-4081-K | Whitiora School | Private | WHICB7 | 01/07/2025 | 20:05 | 01/07/2025 | 20:11 | 0.0001 | 0 | 1 | 6 | Planned | Planned | External Customer
¹ Extend table as necessary to disclose information for all individual interruptions